COMMONWEALTH OF MASSACHUSETTS

SUFFOLK, ss. 				                BUILDING CODE APPEALS BOARD								    DOCKET NO.: 11-993

______________________________

)

James Jensen,				)

Appellant 		                        )

)

v.					)

)

City of Boston,            		)

Appellees		                        )

______________________________)

BOARD’S RULING ON APPEAL

Introduction

This matter came before the State Building Code Appeals Board (“Board”) on appellant’s appeal filed pursuant to G.L. c.143, §100 and 780 CMR 122.1.  In accordance with 780 CMR 122.3 the appellant petitioned the Board to grant a variance from Section 1021 and 1021.1 of the Eighth Edition of the Massachusetts State Building Code (“Code”) requiring that each story have access to the minimum number of approved exits. For the following reasons, the Board grants appellant a variance from the Code’s requirements.

Procedural History

The Board convened a public hearing on May 17, 2011, in accordance with G.L. c. 30A, §§10 & 11; G.L. c. 143, §100; 801 CMR 1.02; and 780 CMR 122.3. All interested parties were provided an opportunity to testify and present evidence to the Board. Kevin Hastings of R.W. Sullivan and James Jensen of Boston Opera House Ventures appeared on behalf of the appellant. Though notified, no representative from the City of Boston Inspectional Services Department appeared on behalf of the appellee. All witnesses were duly sworn.

The Board previously granted appellant an identical variance using identical renovation plans, but appellant subsequently decided not to complete the project and the variance expired after two years. State Building Code Appeals Board Docket No. 05-282 (2006).

Findings of Fact

The Board bases the following findings upon the testimony presented at the hearing.  There is substantial evidence to support the following findings:

- The property at issue is located at 537-539 Washington Street, Boston, MA.

- The Appellant would like to renovate an area of the opera house into office space (“proposed office space”). This area is the last remaining area of the opera house to be renovated.

- The proposed office space has a single means of egress which leads to an area behind the balcony seating area which is one floor up from grade level.

- The maximum occupant load for the proposed office space is 20 people. The actual travel distance from the most remote corner of the proposed office space to the bottom of the egress stair is 132 feet.

- The proposed office space will house fifteen work stations.

- 780 CMR Table 1017.2 and 780 CMR 1011.2.1 allows for the proposed office space to have a single means of egress with a common path of travel of not greater than 100 feet.

- The opera house has a full sprinkler system and fire alarm system, including smoke detection.

Discussion

- Jurisdiction of the Board

There is no question that the Board has jurisdiction to hear this case. The governing statute provides that:

Whoever is aggrieved by an interpretation, order, requirement, direction or failure to act by any state or local agency or any person or state or local agency charged with the administration or enforcement of the state building code or any of its rules and regulations, except any specialized codes as described in section ninety-six, may within forty-five days after the service of notice thereof appeal from such interpretation, order, requirement, direction, or failure to act to the appeals board.      G.L. c.143, §100.

The issues giving rise to this matter directly implicate provisions of the Code.  As such, this Board has jurisdiction to decide this case pursuant to G.L. c. 143, §100.

- State Building Code requirements

The issue in this case is whether the Board shall grant appellant a variance from the minimum number of approved exits. Section 1021.1 of 780 CMR provides in pertinent part that “[a]ll spaces within each story shall have access to the minimum number of approved independent exit as specified in Table 1021.1 based on the occupant level of the story.” Appellant testified that the proposed office space meets the requirements for a single egress but for the common path of travel exceeding the Code by 32 feet. Furthermore, the space includes a sprinkler system and fire alarm system complete with smoke detection.

Conclusion

Jacob Nunnemacher motioned to grant a variance from 780 CMR 1021 and 1021.1 to the approved exits requirement provided that smoke detection exists throughout the proposed office space and egress. Alexander MacLeod seconded his motion. The motion passed unanimously. Appellant’s request for variance is hereby granted.

_______________________ 	  _______________________   __________________

Jacob Nunnemacher                  Alexander MacLeod		Doug Semple

Any person aggrieved by a decision of the State Building Code Appeals Board may appeal to Superior Court in accordance with G.L. c.30A, §14 within 30 days of receipt of this decision.

DATED:  June 6, 2011