The Commonwealth of Massachusetts

Department of Environmental Quality Engineering

Status Report on Tetrachloroethylene Contamination

Of Public Drinking Water Supplies caused by

Vinyl-lined Asbestos Cement Pipe

June 1982

Department of Environmental Quality Engineering

Division of Water Supply

Edward J. King

Governor

John Bewick

Secretary, Executive Office of Environmental Affairs

Anthony D. Cortese, Sc.D.

Commissioner

Department of Environmental Quality Engineering

M. Ilyas Bhatti

Director, Division of Water Supply

CONTENTS

I		Problem Statement

II	Health Effects

III	Testing Program

IV	Studies and Solutions

V		Conclusions and Recommendations

VI	Program Status, April 1982

Attachment A

Graph Showing Relationship between PERC Level and Age of Pipe

Attachment B

Provisionally Approved Pressure Type Vacuum Breakers and Test Procedure

INTRODUCTION AND SUMMARY

Since January 1980, the Division of Water Supply has been assisting communities in coping with contamination of their water-supplies with the organic chemical tetrachloroethylene. The source of the contamination proved to be vinyl-lined asbestos cement water mains. The tetrachloroethylene had been used by the pipe manufacturer as a solvent for the vinyl resin liner. In the coating process, the solution had been sprayed onto the interior walls of the pipe and allowed to dry. In some cases traces of the solvent remained in the resin lining or in the pores of the pipe walls up to the time the pipes were installed as water mains.

An extensive survey revealed that 660 miles of the pipe were used as water mains in the State with 91 different communities-involved. It is significant that the larger cities in the Commonwealth had not installed any of the pipe. The area of the State most seriously impacted falls under the jurisdiction of the southeast Department of Environmental Quality Engineering (DEQE) office in Lakeville. Cities and towns within that area accounted for approximately 500 miles of the pipe, with 44 different communities contributing to the figure. Falmouth and Sandwich were each using about 50 miles of the pipe. No other communities had installed such a large amount.

Health studies discussed in the body of the report implicate tetrachloroethylene as a toxic material and a likely human carcinogen. Extensive testing of water quality where drinking water flows through the vinyl-lined asbestos cement pipe has shown that the level of tetrachloroethylene found in the water will naturally decrease with time. The Department anticipates the problem will be substantially absent after about five years. After considering the health studies, the Environmental Protection Agency (EPA) set a level of 40 micrograms per liter as a maximum level of the solvent which should be allowed in the water. Efforts of the DEQE in assisting communities have been directed toward establishing control procedures and schedules which assure compliance with that limit.

While the most obvious solution would appear to be replacement of the pipe, the cost of this would be so high that communities are not prepared to cope with it except where very short lengths were used. The cost of statewide replacement is estimated to be $157 million for pipe replacement alone, without including

associated costs such as street repairs.

The most practical method to control levels of the impurity is to run some water to waste constantly. A flow of about 4 gallons per minute bled from the distribution system at appropriately chosen points will maintain the required water quality.

Three communities with only short lengths of pipe replaced the pipe. One, the Town of Hatfield, used its own labor force to replace 2700 feet of the pipe at a cost of $25,000, excluding about 166 man hours of labor costs.

1.

Of the 91'communities involved, 33 met standards without corrective measures, 48 chose to control levels of the contaminant by continuous bleeding of water from the pipe, three replaced the pipe, one lined the pipe, and one controls the contaminant levels by flushing the pipe routinely. Five communities have not yet fully controlled the problem.

It is roughly estimated that the monitoring required of communities, the installation of equipment and devices necessary to control the contamination, and the wasting of water will cost the communities involved a total of some $6 to $8 million. Cost of the problem to DEQE to date has been at least $175,000.

In spite of dry weather conditions prevailing since discovery of the problem, most of the water supplies have had enough water available for distribution system bleeding necessary to maintain safe levels of the contaminant. Should the water shortage increase to the point where system bleeding is not possible, the communities would have to choose another alternative such as re-placement or lining of the pipe, use of bottled water for drinking or use of activated carbon filters.

In September 1980 DEQE released a report covering the facts then known relating to contamination of drinking water from vinyl-lined asbestos cement pipes. This April 1982 revision updates the earlier report. Major new components are sections on health effects and giving the status of the problem in each of the 91 communities of concern.

I  	- Problem Statement

In January 1980 Massachusetts and the other five New England States discovered a problem with the chemical tetrachloroethylene leaching into some of their drinking water because of the type of pipe used in some parts of the water distribution system.

Tetrachloroethylene is an organic chemical slightly soluble in water used in a variety of ways including the dry cleaning process as a degreasing solvent and heat transfer medium. The chemical has also been used in the manufacture of vinyl-lined asbestos cement pipes as a solvent or vehicle for the resin.

Asbestos cement (AC) pipes have been in use since the 1930's. The lined variety has been in use for approximately twelve years in New England. The vinyl lining reportedly was developed as a response to customer complaints about the taste and odor of water coming into contact with the asphaltic coating used on water supply pipes, especially in dead end situations.

In July 1976 tetrachloroethylene was discovered in a distribution system in Newport, Rhode Island. An investigation to determine its source was in-conclusive and the significance of the problem not fully understood.

In 1978 and 1979 correspondence about Newport's problem was exchanged between Johns-Manville and Rhode Island officials. Rhode Island periodically updated the other New England states but information was meager and inconclusive. During this time, feeling grew that the problem had something to do with the manufacture of the pipe as opposed to installation practices.

By December 1979 circumstantial evidence showed that lined AC pipes were leaching tetrachloroethylene. A piece of four inch lined AC pipe was shipped in December 1979 from Newport to EPA's Municipal Environmental Research Laboratory in Cincinnati for testing. The experiment run twice in January 1980 verified that tetrachloroethylene came from the lined pipe. At the end of January this information went to each state in EPA Region I.

Discovery of the problem in Massachusetts came about in late January 1980 as a result of DEQE testing in Westford to determine the parameters of a water supply contamination problem. This was in connection with the discovery of a storage area containing barrels of chemical waste. Private wells in the vicinity of the storage area were sampled and a tap on the public supply was also sampled. The sample taken from the public supply showed over 1100 parts per billion (ppb) of tetrachloroethylene. A second sample from the same tap showed over 1000 ppb. Other samples in town showed no amounts of the chemical.

Investigation in 1977 showed the town had installed 8500 feet of 12 inch vinyl-lined asbestos cement pipe in the area in which the tap at the end of the line was sampled by DEQE. Detention time in this segment was calculated to be eleven days. Samples were collected upstream of the line, midway, and at the

end and showed concentrations of 0 ppb, 40 ppb, and 1000 ppb, respectively. This led to the conclusion that tetrachloroethylene was leaching out of the pipe.

DEQE regional offices were instructed to immediately identify and sample

several installations in their region where:

3.

- Lined AC pipe was in use.

- The pipe was installed in a dead-end or low flow location.

This first testing was conducted to determine quickly the extent and severity of the problem.

Results of this first sampling showed that the problem likely existed to some extent among all installations of lined AC pipe.

DEQE mailed a questionnaire to all water department superintendents throughout the state to determine the number of miles of this pipe in use and approximately how many "dead end" situations existed. It was deemed unlikely that this kind of pipe would have been installed by owners of property served by private wells.

Data gathered from the questionnaire indicated that parts of at least 83 public water supplies with a total length of over.. 700 miles of pipe were involved.

Massachusetts requested a meeting with officials of Johns-Mansville from the factory at Manville, New Jersey to get factual and first hand information on the manufacturing process. At this meeting in March 1980 officials learned about the chemicals used, the mixing procedure and the application technique.

Massachusetts also identified two other manufacturers, Certain-Teed and Capco which used this type of lining, whose sales in the area were limited and identifiable.

Another meeting was held between Johns-Mansville officials from Denver, Colorado and Massachusetts officials on April 1, 1980 to obtain more information on the extent of the problem and to discuss possible solutions. Representatives of EPA and the other New England states were invited to this meeting. It is important to note that at all times during this process, there was a dialogue and exchange of information and experience going on not only within each state but between the states and EPA.

At a previously scheduled meeting between EPA and the New England states held in Boston April 2 and 3, this problem was the main topic of discussion. Massachusetts made plans to alert the affected water supply agencies, local officials and legislators and a question and answer package on tetrachloroethylene was developed for the media and the public at this time.

From the time that the problem was first identified, DEQE regional field staff have spent considerable time working with each affected water supplier in an effort to:

- Pinpoint areas of concern.

- Provide advice and some laboratory testing support to lower the levels of tetrachloroethylene and to monitor the effects of control efforts.

In addition, DEQE has initiated or participated in a number of studies de-signed to find short term and long term solutions to this problem.

4.

EPA has undertaken several studies, provided guidance in the area of health risk associated with the problem and provided information on the effectiveness of carbon as a removal agent.

II - Health Effects

Tetrachloroethylene is rapidly absorbed through the lungs and skin. Al-though no studies have been done on its absorption through the gastrointestinal tract, chemical properties of tetrachloroethylene indicate it should be rapidly and completely absorbed as well. The majority of absorbed tetrachloroethylene is rapidly eliminated from the body. Only a minor portion of the total (less than 2%) is retained in tissues.

Because of the nature of the tetrachloroethylene problem associated with vinyl-lined pipes -- long term exposure to relatively low levels of the chemical - we are primarily concerned with chronic toxicity and potential carcinogenicity of tetrachloroethylene.

Tetrachloroethylene affects liver and kidneys as well as the central nervous system, manifested by dizziness, headaches and fatigue. These effects are mild and in most cases reversible if the exposure is stopped. Experimental daily doses required to produce first signs of toxicity in animals were at least a.thousand times higher than that consumed from drinking water containing 40 ppb of tetrachloroethylene.

The results of several studies conducted to assess the carcinogenic potential of tetrachloroethylene are conflicting; the chemical gave positive response in some and negative in others. The most comprehensive study was completed in 1977 by the National Cancer Institute (NCI). In that work massive doses of tetrachloroethylene were given to laboratory mice and rats. The lack of carcinogenic response in rats should be interpreted with caution since the survival of experimental rats was very poor due to the toxic effects of tetrachloroethylene at the doses applied.

NCI is currently conducting two more animal studies on the carcinogenic and teratogenic potential of tetrachloroethylene. The carcinogen bioassay results will become available by late 1982 and the teratogenicity study has recently begun.

Three epidemiological studies are in progress on dry cleaning workers who are exposed occupationally to tetrachloroethylene. The study conducted by the National Institute for Occupational Safety. and Health (NIOSH) will be completed the end of 1982. Preliminary results indicate no increased incidence of cancer, but this may change when the work is completed. Preliminary results of a second study by the NCI on workers in St. Louis indicate an increased risk of cancer, (Blair, Am J Public Health 69,508 (1979). This study will be completed in 1982. A third study conducted by Dr. Nabin Asal of Oklahoma University on dry cleaning workers in Oklahoma indicated increased death rates for kidney cancer in males. A case control study is ongoing. Preliminary results show a number of the 200 cases of kidney cancer were of persons who were dry cleaners

5.

by profession. Statistical analysis has not yet been completed, but final results should become available by March 1982. It should be stressed that tetrachloroethylene is only one of the solvents to which dry cleaning workers would be occupationally exposed. Therefore, even if excess cancer incidence was found in these studies it could not be conclusively linked to tetrachloroethylene.

In summary, positive evidence provided by the NCI mouse study, suggested evidence of the NCI epidemiological study and the similarity of tetrachloroethylene to the known chemical carcinogens vinyl chloride (human) and vinylidene chloride (animal) provide substantial evidence that tetrachloroethylene is likely to be a human carcinogen. (Roy Albert, Carcinogen Assessment Group, EPA, July 25, 1980.)

Statistical probability of developing cancer in man due to exposure to tetrachloroethylene has been calculated by the Committee on Safe Drinking Water with the NCI study with mice, which showed a higher incidence of liver cancer than other animals, to man. The method involved a complex mathematical handling of the laboratory data using a computer program based on a mathematical model of cancer formation. A level of 40 ppb resulted from these calculations. It means that drinking 2 liters of water containing 40 ppb of tetrachloroethylene per day for 70 years will contribute to no more than one additional cancer in 100,000 people exposed.

Suggested No Adverse Response Level (SNARL) which is based on toxic, not carcinogenic response, was established for tetrachloroethylene. A published study was chosen as a basis of the calculations, where inhalation of large doses of tetrachloroethylene had a detectable effect on the liver and kidneys of experimental rabbits. The animal data were extrapolated to man, taking into consideration: 1. route of exposure (ingestion versus inhalation); 2. body weight (20 lb. child to be protected); 3. daily intake (1 liter of water per day per child); 4. absorption rate by the digestive system (to protect the public, 100% is assumed). The number arrived at, 17,000 ppb, was divided by 1000 to provide a wide safety margin. The resulting number 17 was rounded up to 20 ppb. The SNARL of 20 ppb applies to chronic exposure. Using similar procedures to that described for the chronic exposure SNARL, a one day SNARL of 2300 ppb and a ten day SNARL of 175 ppb was established by EPA.

,It should be stressed that all assumptions and generalizations made in

the process of SNARL setting are made in such a way as to protect public health. This is the essence of the conservative approach of the government agencies in determining safe levels of tetrachloroethylene and other chemicals.

In light of the widespread contamination of the Massachusetts water sup-plies which became apparent in 1980, the EPA Office of Drinking Water, responsible for setting the SNARL of 20 ppb for chronic exposure, re-evaluated all the health effects of the compound and recommended a temporary Suggested Action Guide (SAG) of 40 ppb. The choice was justified by the facts that tetrachloroethylene is not an overtly toxic chemical, that the problem was not a long term one and because the SNARL of 20 ppb had a very conservation safety margin of 1000 built into it.

6.

III - Testing Program

The testing program conducted by DEQE has been undertaken in essentially 4 phases. The first was to quickly determine the extent of the problem, the second to further identify areas where the problem might be most serious, the third to support efforts and experiments to find solutions or determine effectiveness of control measures, and the fourth to monitor to verify that control measures continued to be effective and provide direct assistance to communities.

PHASE I:

Original testing was performed in Westford on one section of the AC pipe with vinyl lining in late January 1980. The analysis of samples collected showed levels of tetrachloroethylene exceeding 1,000 parts per billion of water (ppb). These few samples led to further testing in 23 communities.

Testing in these 23 communities was done on:

- unlined AC pipe

- lined AC pipe under normal flow conditions

- lined AC pipe under low flow conditions Both ground and surface supplies were tested.

The analyses of samples collected showed that:

- unlined AC pipe gave no tetrachloroethylene

- lined AC pipe under normal flow conditions generally gave low or intermediate levels.

- dead end or low flow conditions gave concentrations of tetrachloroethylene in the high hundreds to several thousands of parts per billion.

7.

PHASE II:

Because of the concentrations of tetrachloroethylene discovered in phase one, each water supply system was contacted, and samples were collected where vinyl-lined AC pipe was present in water distribution systems. DEQE requested a distribution map from each water department in the affected communities to determine the location of the pipe, its age, and number of customers served. Communities were ranked by DEQE for priority of assistance based upon mileage of pipe and general response to the questionnaire sent in April. DEQE met with local water suppliers on the basis of this priority list and established a limited sampling program based on analytical resources available to the Department.

Samples were also collected and analyzed to determine the effects of pipe age, detention time, or other conditions affecting tetrachloroethylene concentration. This phase of sampling eliminated many areas from future consideration because of the low level detected. It also showed some areas where the concentrations were above guidelines and indicated the need for looping, flushing, installation of bleeders or some other control measure. During this testing phase 75 water supply systems were sampled and 574 samples analyzed.

PHASE III:

Many samples were collected and analyzed to determine the effects of flushing, bleeding, use of faucet aerators, pH control, chlorination, cement lining, etc., on tetrachloroethylene concentrations. This phase will continue as required. Approximately 248 samples from 13 systems were analyzed during the first eight months of the program. Since then, these special studies have accounted for about 160 additional tests.

PHASE IV:

The original testing procedure used at the Lawrence Experiment Station involved the gas chromatograph. About 50 minutes were required for each sample. In addition, known standards had to be run for quality control and time had to be devoted to machine maintenance.

The Experiment Station developed an acceptable variation in the procedure and reduced the time needed to process a sample for tetrachloroethylene. When down time, quality assurance, machine maintenance and other requirements are factored in, about 50 tetrachloroethylene samples per week can be performed on

a sustained basis. Initially, with one laboratory machine and a trained chemist devoted exclusively to the tetrachloroethylene problem, the laboratory ran tests of that rate. Because of the success of control measures, the need to monitor gradually decreased. Very close to 2000 individual tests have been run by the laboratory in the twenty-four months since the problem was discovered.

IV - Studies and Solutions:

During the course of this problem, there have been many suggestions and re-commendations about avenues which should be pursued in looking for a solution.

8.

The following summarizes various investigations. Faucet Aeration

An attempt was made to determine the effect of faucet aerators on the tetrachloroethylene content of affected homes.

From this very limited study, it can be concluded that household aerators have no significant effect on tetrachloroethylene content.

Since the problem lies in the distribution system and not the source, the only reasonable place to consider aeration would be at the point-of-use.

Dilution

Dilution is an effective method of reducing the concentration of material in a water supply by mixing that water supply with another cleaner source of water, but there is no practical way of providing dilution to solve this particular problem.

Cleaning and/or Lining

In 1980 a research program was conducted by Haley and Ward, Inc., to find a cost-effective method of treating asbestos-cement vinyl-lined (A.C. - V.L.) pipe to reduce the leaching rate of tetrachloroethylene thus reducing the concentrations.

That program has been summarized in a report titled: "Tetrachloroethylene (TCE) Concentration Reduction in Vinyl-Lined Asbestos Cement Water Mains Through The Application Of Cement Mortar Linings". The Boston office of the Department has four copies of the report which may be examined on the premises during normal working hours. Individuals desiring their own copy should communicate directly with Haley and Ward Inc., Engineers, Waltham, Mass.

A test site was constructed in Ashland, Mass., consisting of 156 linear feet (L.F.) of A.C. - V.L. pipe installed within an earthen berm, in four separate sections.

. Section "A" consisted of 52 L.F. of pipe, with the vinyl liner removed by wire brushing and a cement liner installed.

- Section "B" consisted of 52 L.F. in which the cement liner was installed directly over the vinyl liner.

- Section "C" and "D",26 L.F. each, were left in the original condition.

All sections were chlorinated, flushed and refilled with clean water, and samples were taken approximately every 7 days for a period of 60 days, with analyses done by the DEQE laboratory at Lawrence. For this particular installation, a con-

9.

sistent 97-99% reduction in TCE concentration was realized for Section 'A" and "B", compared to Sections "C" and "D". It should be understood that this was a short term test (60 days), for pipe 6-months old prior to installation and under static (no flow, no pressure) conditions. Results to date indicate this method of treatment shows promise, and could be utilized at approximately 1/3 the cost of complete pipe replacement,

The method of placing a cement lining over the vinyl lining has been estimated to cost $10 per foot. To remove the vinyl lining from the pipe and then apply the cement lining could be done for approximately $15 per foot.

Additional testing was also attempted by. Haley and Ward, at this site, on similar asbestos-cement vinyl-lined pipe.' The first test consisted of directing a high temperature (200'F), high pressure water jet from a machinery cleaning apparatus on a specific location on the vinyl-liner for 5 minutes. There was no measurable reduction in thickness. An attempt was made to remove the liner with sandblasting equipment. Within one second of operation, the liner was re-moved but there was so much damage to the pipe itself that this method was judged impracticable and the test suspended.

Flushing and/or Bleeding

Extensive sampling of vinyl--lined pipes by DEQE revealed a definite and direct relationship between residence time (length of time the water is in contact with the pipe) and the tetrachloroethylene level observed. It was logical to assume that reducing residence time by flushing and/or bleeding would result in a reduction of the tetrachloroethylene level.

Almost from the outset, DEQE was aware that flushing would lower tetrachloroethylene levels but the level would recover when flushing was terminated. Recognizing the need to be able to predict the rate, duration, and frequency of flushing required to maintain acceptable levels; DEQE has participated in studies designed to provide such information. Data gathered to date relative to high velocity flushing (1 turnover per hour or greater) indicates that 2 complete turnovers will reduce the tetrachloroethylene level to less than 1% of the original level and the maximum rate at which tetrachloroethylene recovers to the initial level is approximately 10% per day.

Continuous bleeding at the terminus of dead ends at a rate of 1 turnover per day appears to be even more effective than high velocity flushing in that there is less fluctuation in the tetrachloroethylene level. Sampling results from approximately 10 locations show that continuous bleeding has consistently lowered the level to below 40 ppb which in most cases represents less than 10% of the original level.

This information on the effectiveness of installing a bleeder on the system is consistent with work done by Johns-Manville (J-M) in Simsbury, Connecticut. There it was found that maintaining flow rates as low as 2 to 3 gallons per minute was adequate to maintain low TCE levels. The tests were all conducted on.8 inch lines but the J-M report indicates similar results could be expected for 10 and 12 inch lines. Pipes used in the J-M experiment were installed in 1977, 1978 and 1979.

10.

Flushing and/or bleeding is reported to be the method employed in con-trolling this problem in the other New England States. This solution or control measure is not without its drawbacks. Water conservation is a stated goal and program of the Commonwealth. Continuous wasting of water is inconsistent with the program. Many communities are water short and cannot afford to waste water. The question has also been raised about a bleeder being left running in winter causing a safety hazard by forming ice in the street.

The Department has determined that a bleeder line may be discharged into

a catch basin or similar receiving area without constituting a cross-connection if:

- The supplier provides the Department with a listing giving the location of each installation.

- A pressure type vacuum breaker is installed on the line.

- The water supplier periodically (at least biweekly) inspects the vacuum breaker to see that it is in operating condition.

- The supplier agrees to shut off and physically remove all piping associated with the bleeder when the problem is solved.

Attachment "B" to this report lists the provisionally approved types of vacuum breakers and outlines a simple testing procedure which requires no special equipment.

Question was raised about the effect a flushing or bleeding program might have on other parts of the environment. DEQE does not believe adverse effects will be caused by the discharge of this water to waste because of the low levels and the probable dilution in the ground.

Since vinyl-lined pipe contains a finite amount of tetrachloroethylene, even normal water flow in the distribution system will eventually remove all the chemical originally present. Evaluation of the results of 230 samples collected in Southeastern Massachusetts shows that the tetrachloroethylene level decreases as the age of the pipe increases. The mean (average) level has been found to be less than 40 ppb in pipe which is 5 years or older. (See Attachment "A") Similar information compiled on 82 samples in the State of Maine supports this finding.

Carbon Filtration

Most state and federal agencies maintain that drinking water delivered to the ultimate consumer should be safe and the consumer should not have to in-stall and/or operate any type of device at point-of-use to insure this safety. If treatment of a public water supply is necessary, it should be accomplished at a central plant where it is under the control of a trained operator.

11.

This philosophy is still valid except that in the present situation, the contamination is occurring at diverse locations in the distribution system and not at the source.

The problem will eventually disappear through use and ingestion of the water is the only real concern about its use. By making some assumptions and using laboratory test data supplied by the EPA one way the concerned individual home owner could address the problem is by installing a filter.

EPA's Office of Drinking Water published a (July 1980) Fact Sheet/Update on their testing of Home Water Treatment Units. Under a contract some 30 commercially available activated carbon units were tested to determine their effectiveness in removing certain organics, bacteria and endotoxins. Of particular interest for this report is the fact that the removal efficiency for tetrachloroethylene should be of the same order of magnitude as that for trihalomethanes, one of the organics actually studied.

If a home owner chose to install a unit with a reported efficiency of 95% for example for trihalomethane (THM) removal, that unit should reduce water with a tetrachloroethylene level of 800 ppb down to 40 ppb for the indicated test life of the filter cartridge.

Assuming a family of four, the amount of water used for drinking and cooking purposes amounts to no more than five gallons per day. If a carbon filter were installed just ahead of a faucet used only to obtain water for these purposes and the filter had an indicated test life of 500 gallons, the carbon cartridge would have to be replaced at approximately 3 month intervals. Use of this tap for other purposes such as dishwashing would reduce the useful life of the filter.

A copy of pertinent parts of this report is available from the DEQE or EPA on request.

Boiling

EPA laboratories in Cincinnati and Lexington have experimented to determine the effectiveness of boiling water as a means of removing chemical contamination. The two compounds chosen for the experiment were trichloroethylene and .tetrachloroethylene but it is reasonable to assume other chlorinated hydro-carbons would follow the same trend.

Results show that after five minutes of a vigorous boil less than. 1% of the tetrachloroethylene remained.

A number of cautions should be observed in using this solution to the problem:

- The person should not stand over the pot of boiling water .where the vapors can be breathed.

2. A range hood should be used.

12.

- A timer is a must. An accurate time of boiling is difficult to judge.

- The inorganic quality of the water should be considered. If the water is heavy with iron for example, boiling will tend to concentrate the iron.

For maximum effectiveness, the depth of water should be no greater than 2 inches. Either glass or metal pans are suitable.

The Department feels that boiling can be an effective method of reducing the concentration of tetrachloroethylene in drinking water, but because of the variabilities with respect to original concentration and other cautions, it may not be a practical long term solution.

pH Adjustment

At the same time the presence of tetrachloroethylene in vinyl-lined asbestos cement pipe was confirmed, a town in Central Massachusetts was about to add potassium hydroxide to the towns water supply for the purpose of corrosion control. It was recognized that this afforded an excellent opportunity to study the effect of pH on the concentration of tetrachloroethylene.

The town has one vinyl lined asbestos cement pipe in a low flow location. This line,1500 feet long, 10" diameter, serves 5 houses.-	The calculated residence time is 4.9 days. Several samples were collected from a hydrant at the end of this line before the KOH was added, with results as follows:

March 18	123 ppb

April 24	38 ppb (after flushing)

The addition of potassium hydroxide was begun on May 9, 1980 and the pH raised to 8.2. The line was flushed to waste for a period of two weeks to draw the high pH water through the line. At the end of that time samples were collected weekly, with results as follows:

May 9	150.4 ppb

May 16	Less than 5 ppb	(while flushing)

June 3	3.3 ppb

June 10	91.8 ppb

June 17	144 ppb

June 25	137 ppb

July 9	285 ppb

July 16	180 ppb

July 23	140 ppb

At the time of the latest sampling, the pH was 8.2 at the station and 8.9 at the hydrant.

It. can be seen that within a short time, the level of tetrachloroethylene reverted to its original level and increasing the p1-i has no effect on reducing the tetrachloroethylene concentration.

13.

Superchlorination

Dufresne-Henry, consulting engineers for the town in Southeastern Massachusetts, recently designed a water transmission main using vinyl-lined AC pipe. After installation, samples of water taken from the transmission line showed concentration levels of tetrachloroethylene above the recommended level of 40 ppb.

To determine the effectiveness of super chlorination in reducing the tetrachloroethylene concentrations, the pipe line was chlorinated at a level, of 50 ppm and the chlorinated water allowed to flow through the pipe at 20 gallons per minute (gpm) for 16 days then allowed to stand in the pipe for 5 days, Chlorinated water was flushed out of the pipeline and the pipeline periodically re-sampled.

Periodic sampling showed that tetrachloroethylene concentrations returned to their original levels after chlorination and flushing.

The EPA has also done bench studies on the effect of chlorination on vinyl-lined asbestos cement pipe and observed generally similar results.

Replacement

Asbestos cement, vinyl-lined pipe is located in areas across the Common-wealth, from Clarksburg in the Berkshires to Provincetown on Cape Cod, including the offshore islands. Sizes vary from 6 inches up to 16 inches with the majority being 6 inches and 8 inches in size. Several lines are short spur lines that dead end, many less than 2400 feet in length. To dig up and replace this pipe would create a costly problem for the communities. Our best estimate of quantity is 660 miles or 3,484,800 feet of pipe in the ground.

Replacement of the pipe would entail more than just digging it up and re-laying. Any house service on the existing line would have to be reconnected;, this would also mean hydrant connections; plans and specifications would have to be prepared for bidding; and engineering inspection for the contract would be another cost.

Currently, contractor bids for laying 6" mains are $35 per foot; 8" mains are $40 per foot; and 10" mains are $45 per foot. Using the 10 inch cost per foot as an average, the raw replacement of the mains would be:

Total Replacement 	660 miles	156,816,000

75% Replacement	495 miles	117,612,000

5O% Replacement	330 miles	78,408,000

25% Replacement	165 miles	39,204,000

To these costs must be added the costs of:

- Plans and specifications

- Bidding

- House service connections

- Hydrant connections

- Construction inspection

- Repair of streets, sidewalks and driveways affected.

14.

No specific state or federal programs exist for problems of this type for cost sharing, so the entire cost of replacement must be borne by the water supplier.

Bottled Water - Alternate Water Supply

Bottled water as an alternate supply is usually available in either one gallon plastic jugs at the supermarket or five gallon carboys from a company which will deliver to the home. Testing of bottled water is not as comprehensive a program as the testing of public water supplies.

In many communities there is no-problem with tetrachloroethylene in any part of the water system and even in the affected communities not all parts of the system are affected. This raises the possibility of taps in public buildings (libraries, fire stations, the well or treatment plant) being made available to people who wish to draw water for drinking and culinary purposes.

V - Conclusions and Recommendations

The problems are:

- This contaminant is in the distribution pipe and not the source.

- It is not amenable to treatment with another waterworks chemical, i.e., chlorination, corrosion control chemicals, etc.

- There is no Maximum Contaminant Level yet established by the federal EPA. However, the Department has adopted the EPA guideline of 40 ppb which was established to protect the public health with a margin of safety.

- Since the lining was applied by hand rather than an automated process, the amount of vinyl lining can vary. In at least one case it is reported that the local water department was dissatisfied with the amount of material on some pipe they bought and it was sent back to the factory to be lined. This, coupled with the varying age of pipe in the systems tested, lack of knowledge about how old the pipe was before it was laid and the difference in flow patterns that the pipe is subject to in the system, make it impossible to draw more than broad and general conclusions from the data. Significantly more amounts of testing probably will not allow us to be any more precise with general conclusions. The degree of the problem is to a large extent site specific and must now be dealt with on that basis.

Possible solutions to the problem are several and selection of the most advantageous one (or combination of several) must depend on decisions made at the local level.

Possibilities to be considered include:

- Providing a program of bleeding and/or flushing.

- Providing an alternate water supply.

15.

- Providing for carbon filtration.

- Looping dead end situations or making other structural changes to provide for a better flow of water.

- Boiling water used for consumption.

- Scraping and/or relining pipe in place.

- Replacing the pipe.

The eventual goal is to provide water in all locations where samples or water in the pipes under normal use conditions is consistently less than 40 ppb. The sampling program could then be discontinued. Further use and aging of the pipe will eventually lower this level to 0 ppb, well within the 70 year time span on which the SNARL is based.

To solve the problem of tetrachloroethylene in water pipes, each supplier must submit a written action plan to the Department indicating how he proposes to address his problem.

The Department will assign one water supply engineer in each region whose prime responsibility will be to work with the water suppliers on this problem, collect such additional samples as necessary to assess the success of the efforts and keep a current record on each affected supplier's efforts and the results of those efforts so that as areas of concern fall below the 40 ppb level, they can be eliminated from further testing. Samples collected by these engineers will be analyzed by the Department. However, neither the Commonwealth nor the EPA have the laboratory capability to do all of the monitoring work that will be required. Suppliers should contract with private laboratories to do the routine analytical work, keeping a record of all expenses incurred.

It is the responsibility of the water supplier to provide the best possible quality of water to the consumers. If, despite best efforts there is still a problem, the ultimate consumer must be made aware of the quality of the supply by the water supplier. The consumer will then be aware of the problem and the factors which have gone into any decision and can make informed judgments about using or not using the water for various purposes.

Strategy for Dealing with the Problem

The following strategy is suggested as a possible plan for action.

- Water suppliers identify all areas where vinyl-lined AC pipes have been installed.

- Areas where the pipe is in a constant flow situation and areas where the pipe is five years old or older be tested and eliminated from future testing if the concentration is 40 ppb or less.

- Areas where previous sampling has shown the concentration to be 40 ppb or less under normal use conditions be eliminated from future testing.

16.

- Areas where previous sampling or new sampling shows the concentration to be between 40 ppb and 100 ppb under normal flow conditions be immediately flushed and equipped with a bleeder. The bleeder should be protected with a backflow device such as a pressure type vacuum breaker if necessary. One sample should be collected from these locations every six months to confirm that the level is being maintained below 40 ppb..

- Areas where the concentrations are above 100 ppb under normal use conditions to be identified; and

- Flushes and bleeders installed where appropriate.

- Sampled monthly by the water supplier. Frequency of this sampling can be reduced to once every 6 months provided that 3 consecutive months' samples show tetrachloroethylene levels below 40 ppb.

If steps (a) and (b) show the concentration is not kept below an average of 40 ppb over a six month average, or if any monthly sample exceeds 175 ppb which is the 10 day SNARL, then the supplier must initiate a program for the affected area whereby:

- Consumers in the affected area are formally notified of the problem and the water supplier's intended further actions to correct it.

- Affected consumers are advised of possible alternatives such as:

- Obtaining water from another nearby source which is not affected.

- Installation of an appropriate carbon filtration unit.

- Boiling water used for consumption.

As an indication of their concern and awareness of this problem, it is suggested that the supplier, as a matter of policy, keep consumers affected by this problem informed about its prevalence within the system, efforts being made to solve the problem, outcome of these efforts, results of testing, etc., as this in-formation becomes known.

The essence of the program should be that the average level of tetrachloroethylene is maintained at, or below, 40 ppb even though the short-term (less than

a month) levels may be higher than that. The Department believes that despite these short-term variations in excess of 40 ppb, the long-term effects of tetrachloroethylene at these levels present no danger to the health of the exposed population, based on two liters of water ingested per day for 70 years.

17.

VI - Program Status, April 1982

Of the 91. communities using vinyl-lined asbestos cement pipe as water mains, 33 were shown by testing to meet standards without corrective measures, 48 chose to control levels of the contaminant tetrachloroethylene by continuous bleeding of water from the pipes, three replaced the pipe, one lined the pipe, and one controls the contaminant levels by routinely flushing the pipe. Five communities have not fully controlled the problem.

Table I which follows identifies the 91 communities which used the pipe under discussion and gives the lengths of the lined pipe used in those communities.

Table II identifies the 33 communities where levels of tetrachloroethylene were below 40 micrograms per liter so that corrective action was not necessary.

Table III identifies 48 communities which maintain the level of the contaminant at or below 40 micrograms per liter by bleeding water from the vinyl-lined mains.

Table IV identifies the five communities which have controlled the contaminant level at or below 40 micrograms per liter by one of the following procedures.

- replacement of the pipe; or

- lining the pipe; or

- routine flushing of the pipe.

The five communities which have not fully controlled the problem are Clarks-burg, East Bridgewater, Ipswich, Sandwich, and Whitman. Testing in these towns has shown the following ranges of contaminant levels.

COMMUNITY	RANGE OF PERC LEVELS FOUND

Clarksburg	62-72 Parts per billion

East Bridgewater	0-179

Ipswich	0-250	„	„

Sandwich	1-167

Whitman	0-254	"	„	"

Clarksburg is a small community which does not have enough water available to control the situation by system bleeding and does not have sufficient funds for other possible control measures. The community provides bottled water at the schools and notified its citizens who must make their own arrangements about obtaining suitable drinking water.

East Bridgewater submitted a plan indicating intent to control the contaminant levels by installing bleeding devices in problem areas. The Department directed Bridgewater to proceed with its plan in November 1981.

18.

Ipswich has three areas with high results and informed DEQE that customers in these areas have been notified of the problem. The town had testing done and advised DEQE that system bleeding devices will be installed.

Sandwich installed devices for system bleeding to control the problem. Test results show the problem is not yet entirely solved and more devices are necessary.

Whitman obtains water from the Brockton water supply system. Because of the extreme water shortage experienced by City of Brockton, bleeding of the distribution system within Whitman has not been possible. Although about 80% of the areas with the vinyl lined pipe meet standards, there are still areas with high test results.

State funds are not available to assist the communities with this problem. However, as some of the communities have been eliminated from the list of towns where monitoring is necessary, DEQE will be able to provide increased assistance to the problem areas in the form of testing service and advice. It may become necessary in some cases to take strong enforcement action.

19.

PART VI

TABLE I

WATER SUPPLIES WITH ASBESTOS CEMENT VINYL LINED PIPE

NO	TOWN	WATER SUPPLY		MILES OF PIPE

1	Acushnet	Town Supply	' 2.0

2	Amherst	1.0

3	Arlington	0.1

4	Ashland	4.0

5	Ayer	4.5

6	Barnstable	Barnstable Water Company	16.0

7	Bourne	Bourne Water District	15.0

8	Bourne	Buzzards Bay Water District	0.05

9	Bourne	North Sagamore Water District	5.0

10	Bourne	South Sagamore Water District	2.0

11	Brewster	Town Supply	6..0

12	Bridgewater	"	16.0

13	Brookfield	"	"	1.25

14	Burlington	"	"	15.50

15	Chatham	“	7.5

16	Chicopee	Municipal Supply	0.75

17	Clarksburg	Red Miles Water Supply	1.10

18	Cohasset	Town Supply	12.0

19	Dartmouth	"	"	12.0

20	Deerfield	Deerfield Fire District	0.2

21	Deerfield	.South Deerfield Water District	0.45

22	Douglas	Town Supply		2.0

23	Duxbury	"	„	15.0

24	East Bridgewater	"	"	20.0

25	East Brookfield	"	"	0.25

26	Easthampton	"	"	0.1

27	Edgartown	Edgartown Water Company	15.0

28	Essex	Town Supply	 0.5

29	Fairhaven	10.0

30	Falmouth	"		50.0

31	Franklin	5.0

32	Gosnold	Gosnold Water Company	0.05

33	Halifax	Town Supply	4.0

34	Hamilton	"	„	7.75

35	Hanover	"	'	12.0

36	Hanson	18.0

37	Harwich	"	"	0.2

38 	Hatfield	"	0.5

39	Haverhill	Municipal Supply	0.05

40	Holden	Town Supply	8.0

41	Holliston	"	"	2.0

42	Ipswich	"	"	12.8

43	Kingston	0.2

44	Lincoln	"	1.0

45	Littleton	"	1.0

46	Longmeadow	"	"	5.0

47	Lunenburg	"	1.0

48	Marion	4.0

49	Marshfield	15.0

(Continued)	PART V1

TABLE I

WATER SUPPLIES WITH ASBESTOS CFM NF VINYL LINED PIPE

NO	TOWN	WATER SUPPLY	MILES OF PIPE

50	Mashpee	Highwood Water Company	1.0

51	Mattapoisett	Town Supply	4.0

52	Milford	Milford Water Company	42.0

53	Nantucket	Wannacomet Water Company	0.2

54	Norfolk	Town Supply	8.7

55	North Brookfield	"	"	3.0

56	Northborough	T'	"	7.0

57	Northfield	Northfield Water District	0.75

58	Norwell	Town Supply	2.0

59	Oak Bluffs	10.0

60	Paxton	"	„	1.0

61	Pembroke	TT	TT	5.0

62	Plymouth	35.0

63	Provincetown	6.0

64	Raynham	Raynham Center Water District	2.0

65	Raynham	North Raynham Water District	2.0

66	Rowley	Town Supply	3.8

67	Rutland	1.0

68	Salisbury	"	3.3

69	Sandwich 	"	50.0

70	Scituate	T'	3.0

71	Sharon	''	''	1.0

72	Shirley	Mass Correction Institution	1.0

73	Shrewsbury	Town Supply	8.0

74	Southborough	"	7.0

75	Southampton	"	0.05

76	Sterling	15.0

77	Sunderland	"	"	0.5

78	Taunton	Municipal Supply	20.0

79	Tisbury	Town Supply	10.0

80	Wareham	Wareham Fire District	20.0

81	Wareham	Onset Fire District	20.0

82	West Boylston	West Boylston Water District,	0.5

83	 West Bridgewater	Town Supply	5.0

84	West Brookfield	"	0.1

85	Westford	TT	IT	7.0

86	Westminster	3.0

87	West Newbury	"	TT	0.3

88	Whitman	IF	It	8.0

89	Winchester	'T	IT	4.5

90	Woburn	Municipal Supply	0.60

91	Wrentham	Town Supply	_	4.0

21.

PART VI

TABLE II

COMMUNITIES MEETING STANDARDS WITHOUT CORRECTIVE ACTION

TOWN	SUPPLY	MILES OF PIPE

Acushnet	Town Supply	2.0

Arlington	“	0.1

Ayer	4.5

Barnstable	Barnstable Water Company	16.

Bourne	Buzzards Bay Water District	0.05

Brookfield	Town Supply	1.24

Chatham	"	7.5

Cohasset	"	12.

Deerfield	Deerfield Fire District	0.2

Duxbury	Town Supply	15.

Franklin	"	It	5.

Hanover	12.

Harwich	it	0.2

Haverhill	Municipal Supply	0.05

Holden	Town Supply	8.

Holliston	“	2. Lunenburg	"	1.

Milford	Milford Water Company	42.

Nantucket	Wannacomet Water Company	0.2

North Brookfield.	Town Supply	3.

Paxton	"	"	1.

Provincetown	"	6.

Raynham	North Raynham Water District	2.

Rutland	Town Supply	1.

Salisbury	' 	3.3

Sharon	“	1.

Shirley	Mass. Correctional Institution	1.

Southborough	Town Supply.	7.'

Sunderland	"	“	0.5

Wareham	Wareham Fire District	20.

Westminster	Town Supply	3.

West Newbury	"	it	.3

Woburn	Municipal Supply	.60

22.

PART .VI

TABLE III

COMMUNITIES MEETING STANDARDS BY SYSTEM BLEEDING

TOWN  	SUPPLY	MILES OF PIPE

Amherst	Town Supply	1

Ashland	"	"	4.

Bourne	Bourne Water District	15.

Bourne	North Sagamore Water District	5.

Brewster	Town Supply	6.

Bridgewater	16.

Chicopee	Municipal Supply	0.75

Dartmouth	Town Supply	12.

Deerfield	South Deerfield 'Water District	0.45

Douglas	Town Supply	2.

East Brookfield	0.25

Easthampton	"	0.1

Edgartown	Edgartown Water Company	15.

Fairhaven	Town Supply	10.

Falmouth	50.

Gosnold	Gosnold Water Company	0.05

Halifax	Town Supply	4.

Hamilton	,'	''	7.75

Hanson	',	"	18.

Kingston	"	0.2

Lincoln	1.

Littleton	"	"	1.

Longmeadow	,'	5.

Marion	4.

Marshfield	15.

Mashpee	"	"	1.

Mattapoisett	"	"	4.

Norfolk	8.7

Northborough	7.

Northfield	,'	0.75

Norwell	''	2.

Oak Bluffs	"	"	10.

Pembroke	5.

Plymouth	"	35.

Raynham	"	2.

Rowley	',	3.8

Scituate	"	"	3.

Shrewsbury	"	8.

Sterling	"	"	15.

Taunton	Municipal Supply	20.

Tisbury	Town Supply	10.

Wareham .	Onset Fire District	20.

West Boylston	West Boylston Water District	0.5

West Bridgewater	Town Supply	5.

Westford	7.

Winchester	4.5

Wrentham	"	4.

.	23.

PART VI

TABLE IV

COMMUNITIES MEETING STANDARDS BY MISCELLANEOUS METHODS

TOWN	WATER SUPPLY	MILES OF PIPE	CONTROL METHOD

Hatfield	Town Supply	0.5	Replaced Pipe

Southampton	“	“	0.05

West Brookfield	"	0.1	“	“

Burlington	“	15.50	Lined Pipe

Essex	“	0.50	Flush System

PART VI

TABLE V

COMMUNITIES WHERE PROBLEM IS NOT COMPLETELY UNDER CONTROL

TOWN	WATER SUPPLY	MILLS OF PIPE	LEV].IS FOUND

Clarksburg	Red Mills Supply	1.1	62-72 Parts Per Billion

East Bridgewater Town Supply	20.	0-179	"	"

Ipswich	“	“	12.8	0-250	"	"	"

Sandwich	"	50.	1-167	"

Whitman	"	8.	0-254	"

Attachment B PRESSURE = TYPE . VACUUM BREAKERS

The model and size of pressure type-vacuum breakers listed below are not yet fully approved by the Department. In accordance with our policy of requiring evaluation under field conditions before full approval is given they will be allowed to be used on bleeder lines from public water supply distribution systems to lower the tetrachloroethylene levels. The water supplies must make application to the Department for each installation although no formal permit will be issued or fee charged.

Company	Model	Sizes

FEBCO	765	1/2",3/4",l",1-1/4",1-1/2" and 2"

WATTS	No. 8000 series	3/4",1",1-1/4",1-1/2" and 2"

RAINBIRD	PVB 075	3/4"

PVB 100	1"

PVB 125	1-1/4"

PVB 150	1-1/2"

PVB 200	2"

NEPTUNE		720	1/2',3/4",l",1-1/4",1-1/2" and 2"

TEST PROCEDURE FOR PRESSURE VACUUM BRED

- Remove canopy from top of vacuum to expose air inlet tube.

- Close shutoff valve No. 2 on discharge side of vacuum breaker.

- Close shutoff valve No. 1 on inlet side of vacuum breaker.

- Slowly open test cock No. 2, watching guide in air inlet tube.

Valve must be fully open by the time the water stops running from

test cock No. 2. If it is not open, then air inlet is sticking and

valve must be repaired.

- Close test cock No. 2.

- Open inlet shutoff valve No. 1 very slightly and allow water to fill to the top of the air chamber. Then close shutoff valve No. 1 tightly.

- Open test cock No. 1.

- The water level in the air inlet tube will drop initially due to. the seating of the diaphragm. After the initial drop, the level of the water should remain fixed in the air inlet. If it continues to drop, then check valve is leaking and should be replaced.

- If both 3 and 7 test satisfactorily, restore all shutoff valves and test cocks to initial positions.

NOTES: Open shutoff valve No. 2 on the discharge side of the vacuum breaker before opening the shutoff valve No. 1. This eliminates any shock that might cause the diaphragm to blew due to the compressed air and resultant shock wave.

26.