## EXHIBIT PG-1
PHYSICAL COLLOCATION
VERIZON MASSACHUSETTS
COST SUMMARY
| (A) | (B) | (C)
LINE |  |  | MONTHLY
NO | ITEM | SOURCE | RECURRING
1 | PER DC AMP | WP 1.0, PG 1, LINE 77 | 13.9064
2 | AC AMP PER DC AMP | WP 2.0, PG 1 LINE 29 | 4.8261

## WP 1.0 PG-1 DC POWER PER AMP
PHYSICAL COLLOCATION
VERIZON MASSACHUSETTS
DC POWER CONSUMPTION
| (A) | (B) | (C) | (D) | (E) | (F)
LINE NO. | ITEM | SOURCE | METRO | URBAN | SUBURBAN | RURAL
MICROPROCESSOR PLANT
1 | AMPs | ENGINEERING | 6000 | 2600 | 2600 | 1200
2 | TOTAL MATERIAL INVESTMENT | ENGINEERING | 19829 | 16905 | 16905 | 13710
3 | UNIT INVESTMENT PER AMP | LINE 2 / LINE 1 | 3.3048 | 6.5019 | 6.5019 | 11.425
RECTIFIERS
4 | QUANTITY | ENGINEERING | 9 | 8 | 8 | 3
5 | AMPS PER UNIT | ENGINEERING | 400 | 200 | 200 | 200
6 | TOTAL AMPS | LINE 4 X LINE 5 | 3600 | 1600 | 1600 | 600
7 | UTILIZATION | (LINE 4 -1) / LINE 4 | 88.89% | 87.5% | 87.5% | 66.67%
8 | MATERIAL INVESTMENT | ENGINEERING | 79497 | 54512 | 54512 | 20442
9 | TOTAL MATERIAL INVESTMENT | LINE 8 / LINE 7 | 89434.125 | 62299.4286 | 62299.4286 | 30663
10 | UNIT INVESTMENT PER AMP | LINE 9 / LINE 6 | 24.8428 | 38.9371 | 38.9371 | 51.105
BATTERIES
11 | STRINGS | ENGINEERING | 4 | 4 | 4 | 2
12 | AMPs PER STRING | ENGINEERING | 688 | 310 | 310 | 310
13 | TOTAL AMPS | LINE 11 X LINE 12 | 2752 | 1240 | 1240 | 620
14 | TOTAL MATERIAL INVESTMENT | ENGINEERING | 105824 | 43856 | 43856 | 21928
15 | UNIT INVESTMENT PER AMP | LINE 14 / LINE 13 | 38.4535 | 35.3677 | 35.3677 | 35.3677
AUTOMATIC BREAKER
16 | AMPs PER BREAKER | ENGINEERING | 1600 | 800 | 800 | 400
17 | TOTAL MATERIAL INVESTMENT | ENGINEERING | 50000 | 35000 | 35000 | 20000
18 | UNIT INVESTMENT PER AMP | LINE 17 / LINE 16 | 31.25 | 43.75 | 43.75 | 50
POWER DISTRIBUTION SERVICE CABINET
19 | AMPs | ENGINEERING | 1200 | 800 | 800 | 400
20 | TOTAL MATERIAL INVESTMENT | ENGINEERING | 5672 | 5303 | 5303 | 3857
21 | UNIT INVESTMENT PER AMP | LINE 20 / LINE 19 | 4.7267 | 6.6288 | 6.6288 | 9.6425
EMERGENCY ENGINE
22 | DC AMP CAPACITY | WP 3.0, PG 1, LINE 4 | 6000 | 2600 | 2600 | 1200
23 | UTILIZATION | ENGINEERING | 70% | 70% | 70% | 70%
24 | UTILIZED DC AMPs | LINE 22 X LINE 23 | 4200 | 1820 | 1820 | 840
25 | EMERGENCY ENGINE INVESTMENT | ENGINEERING | 86700 | 55800 | 45600 | 28000 | 121700 | 85800 | 70600 | 48000 | Verizon's Material Investment
26 | CONDUIT / EMERGENCY LIGHTS | ENGINEERING | 35000 | 30000 | 25000 | 20000
27 | UNIT INVESTMENT PER AMP | LINE 25 / LINE 24) + (LINE 26 / LINE 22) | 26.4762 | 42.1978 | 34.6703 | 50 | 329253.7874 | 142676.6412 | 142676.6412 | 65850.7575 | Material Investment
27A | PERCENT UTILIZED FOR DC POWER | WP 3.0, PG 1, LINE 6 | 28.8% | 35.66% | 62.4% | 72%
27B | UTILIZED DC POWER INVESTMENT | LINE 27 X LINE 27A | 7.6251 | 15.0465 | 21.6343 | 36 | 170.5% | 66.29% | 102.1% | 37.19% | Over-Recovery Percentage
28 | TOTAL UNIT INVESTMENT PER AMP (> THAN 60 AMPS) | SUM (3+10+15+18+21+27) | 110.2029 | 146.2321 | 152.8198 | 193.5402
29 | POWER INSTALLATION FACTOR - 377C | WP 6.0, PG 1, LINE 10 | 2.7852 | 2.7852 | 2.7852 | 2.7852
30 | TOTAL INSTALLED INVESTMENT | LINE 28 X LINE 29 | 306.9372 | 407.2856 | 425.6338 | 539.0483 | 917037.6488 | 397382.9811 | 397382.9811 | 183407.5298 | Total Investment
31 | LAND INVESTMENT FACTOR | WP 6.0, PG 1, LINE 7 | 0.003 | 0.003 | 0.003 | 0.003
32 | BUILDING INVESTMENT FACTOR | WP 6.0, PG 1, LINE 8 | 0.0749 | 0.0749 | 0.0749 | 0.0749
33 | LAND INVESTMENT | LINE 30 X LINE 31 | 0.92081 | 1.2219 | 1.2769 | 1.6171
34 | BUILDING INVESTMENT | LINE 30 X LINE 32 | 22.9896 | 30.5057 | 31.88 | 40.3747
35 | LAND - ANNUAL COST FACTOR | WP 6.0, PG 1, LINE 1 | 0.28108 | 0.28108 | 0.28108 | 0.28108
36 | LAND - ANNUAL COST | LINE 33 X LINE 35 | 0.25882 | 0.34344 | 0.35892 | 0.45455
37 | BUILDING - ANNUAL COST FACTOR (10C) | WP 6.0, PG 1, LINE 3 | 0.40981 | 0.40981 | 0.40981 | 0.40981
38 | BUILDING - ANNUAL COST | LINE 34 X LINE 37 | 9.4213 | 12.5014 | 13.0646 | 16.5458
39 | DIGITAL SWITCH - ANNUAL COST FACTOR | WP 6.0, PG 1, LINE 4 | 0.31826 | 0.31826 | 0.31826 | 0.31826
40 | DIGITAL SWITCH - ANNUAL COST | LINE 30 X LINE 39 | 97.6871 | 129.6243 | 135.4639 | 171.5597
41 | TOTAL ANNUAL COST PER DC AMP | LINE 36 + LINE 38 + LINE 40 | 107.3672 | 142.4692 | 148.8875 | 188.5601 | 320781.4141 | 139005.2794 | 139005.2794 | 64156.2828 | Annual Cost
42 | MONTHLY RECURRING COST PER AMP | LINE 41 / 12 | 8.9473 | 11.8724 | 12.4073 | 15.7133
43 | STATEWIDE WEIGHTING FACTOR | WP 6.0, PG 1, LINES 14 THRU 17 | 0.072287 | 0.39208 | 0.48867 | 0.046967
44 | WEIGHTED COST PER AMP | LINE 42 X LINE 43 | 0.64677 | 4.6549 | 6.0631 | 0.73801
45 | STATEWIDE COST PER AMP | SUM OF LINE 44 | 12.1027 |  |  |  | 26731.7845 | 11583.7733 | 11583.7733 | 5346.3569 | Monthly Less Common Overhead Factor
46 | COMMON OVERHEAD FACTOR | WP 6.0, PG 1, LINE 11 | 1.0803
47 | MONTHLY COST PER AMP | LINE 45 X LINE 46 | 13.0746 |  |  |  | 28878.3468 | 12513.9503 | 12513.9503 | 5775.6694 | Monthly Less Gross Revenue Loading
48 | GROSS REVENUE LOADING | WP 6.0, PG 1, LINE 13 | 1.0027
49 | TOTAL STATEWIDE MONTHLY COST PER AMP - GREATER THAN 60 AMPS | LINE 47 X LINE 48 | 13.11 |  |  |  | 28956.5205 | 12547.8255 | 12547.8255 | 5791.3041 | Monthly Recurring Revenue for Backup Generator Capacity
50 | GREATER THAN 60 AMPS WEIGHTING | LINE 49 X 0.05 | 0.6555
BATTERY DISTRIBUTION FUSE BAY
51 | AMP CAPACITY | ENGINEERING | 800 | 800 | 800 | 800
52 | TOTAL MATERIAL INVESTMENT | ENGINEERING | 7626 | 7626 | 7626 | 7626
53 | UNIT INVESTMENT PER DC AMP | LINE 51 / LINE 52 | 9.5325 | 9.5325 | 9.5325 | 9.5325
54 | DIGITAL SWITCH POWER INSTALLATION FACTOR | WP 6.0, PG 1, LINE 10 | 2.7852 | 2.7852 | 2.7852 | 2.7852
55 | TOTAL INSTALLED INVESTMENT | LINE 53 X LINE 54 | 26.5499 | 26.5499 | 26.5499 | 26.5499
56 | LAND INVESTMENT FACTOR | WP 6.0, PG 1, LINE 7 | 0.003 | 0.003 | 0.003 | 0.003
57 | BUILDING INVESTMENT FACTOR | WP 6.0, PG 1, LINE 8 | 0.0749 | 0.0749 | 0.0749 | 0.0749
58 | LAND INVESTMENT | LINE 55 X LINE 56 | 0.07965 | 0.07965 | 0.07965 | 0.07965
59 | BUILDING INVESTMENT | LINE 55 X LINE 57 | 1.9886 | 1.9886 | 1.9886 | 1.9886
60 | LAND - ANNUAL COST FACTOR | WP 6.0, PG 1, LINE 1 | 0.28108 | 0.28108 | 0.28108 | 0.28108
61 | LAND - ANNUAL COST | LINE 58 X LINE 60 | 0.022388 | 0.022388 | 0.022388 | 0.022388
62 | BUILDING - ANNUAL COST FACTOR | WP 6.0, PG 1, LINE 3 | 0.40981 | 0.40981 | 0.40981 | 0.40981
63 | BUILDING - ANNUAL COST | LINE 59 X LINE 62 | 0.81494 | 0.81494 | 0.81494 | 0.81494
64 | DIGITAL SWITCH - ANNUAL COST FACTOR | WP 6.0, PG 1, LINE 4 | 0.31826 | 0.31826 | 0.31826 | 0.31826
65 | DIGITAL SWITCH - ANNUAL COST | LINE 54 X LINE 64 | 8.4499 | 8.4499 | 8.4499 | 8.4499
66 | TOTAL ANNUAL COST PER DC AMP | LINE 61 + LINE 63 + LINE 65 | 9.2872 | 9.2872 | 9.2872 | 9.2872
67 | MONTHLY RECURRING COST PER AMP | LINE 66 / 12 | 0.77393 | 0.77393 | 0.77393 | 0.77393
68 | STATEWIDE WEIGHTING FACTOR | WP 6.0, PG 1, LINE 14 THRU 17 | 0.072287 | 0.39208 | 0.48867 | 0.046967
69 | WEIGHTED COST PER AMP | LINE 67 X LINE 68 | 0.055946 | 0.30344 | 0.3782 | 0.03635
70 | STATEWIDE COST PER AMP | SUM OF LINE 69 | 0.77393
71 | COMMON OVERHEAD FACTOR | WP 6.0, PG 1, LINE 11 | 1.0803
72 | MONTHLY COST PER AMP | LINE 70 X LINE 71 | 0.83608
73 | GROSS REVENUE LOADING | WP 6.0, PG 1, LINE 13 | 1.0027
74 | BATTERY DISTRIBUTION FUSE BAY COST PER AMP | LINE 72 X LINE 73 | 0.83834
75 | TOTAL STATEWIDE MONTHLY COST PER AMP - < THAN OR = TO 60 AMPS | LINE 49 + LINE 74 | 13.9483
76 | LESS THAN OR EQUAL TO 60 AMPS WEIGHTING | LINE 75 X 0.95 | 13.2509
77 | TOTAL STATEWIDE MONTHLY COST PER DC AMP | LINE 50 + LINE 76 | 13.9064

## WP 2.0 PG-1 AC PER DC AMP
PHYSICAL COLLOCATION
VERIZON MASSACHUSETTS
AC AMPS PER DC AMPS
| (A) | (B) | (C) | (D) | (E) | (F)
LINE NO. | ITEM | SOURCE | METRO | URBAN | SUBURBAN | RURAL
EMERGENCY ENGINE
1 | AC AMP CAPACITY | WP 5.0, PG 1, LINES 6,12,18,24 | 1505.2987 | 1215.8181 | 694.7532 | 277.9013
2 | UTILIZATION | ENGINEERING | 70% | 70% | 70% | 70%
3 | UTILIZED AC AMPs | LINE 1 X LINE 2 | 1053.7091 | 851.0727 | 486.3273 | 194.5309
4 | EMERGENCY ENGINE INVESTMENT | ENGINEERING | 86700 | 55800 | 45600 | 28000
5 | CONDUIT / EMERGENCY LIGHTS | ENGINEERING | 35000 | 30000 | 25000 | 20000
6 | UNIT INVESTMENT PER AMP | (LINE 4 / LINE 4) + (LINE 5 / LINE 1) | 105.532 | 90.2391 | 129.748 | 215.904
7 | AC % OF ENGINE CAPACITY | WP 3.0, PG 1, LINE 10 | 71.2% | 64.34% | 37.6% | 28%
8 | AC INVESTMENT FOR ANCILLARY EQUIPMENT | LINE 6 X LINE 7 | 75.1388 | 58.0624 | 48.7853 | 60.4531
9 | POWER INSTALLATION FACTOR - 377C | WP 6.0, PG 1, LINE 10 | 2.7852 | 2.7852 | 2.7852 | 2.7852
10 | TOTAL INSTALLED INVESTMENT | LINE 8 X LINE 9 | 209.2765 | 161.7154 | 135.8767 | 168.374
11 | LAND INVESTMENT FACTOR | WP 6.0, PG 1, LINE 7 | 0.003 | 0.003 | 0.003 | 0.003
12 | BUILDING INVESTMENT FACTOR | WP 6.0, PG 1, LINE 8 | 0.0749 | 0.0749 | 0.0749 | 0.0749
13 | LAND INVESTMENT | LINE 10 X LINE 11 | 0.62783 | 0.48515 | 0.40763 | 0.50512
14 | BUILDING INVESTMENT | LINE 10 X LINE 12 | 15.6748 | 12.1125 | 10.1772 | 12.6112
15 | LAND - ANNUAL COST FACTOR | WP 6.0, PG 1, LINE 1 | 0.28108 | 0.28108 | 0.28108 | 0.28108
16 | LAND - ANNUAL COST | LINE 13 X LINE 15 | 0.17647 | 0.13637 | 0.11458 | 0.14198
17 | BUILDING - ANNUAL COST FACTOR (10C) | WP 6.0, PG 1, LINE 3 | 0.40981 | 0.40981 | 0.40981 | 0.40981
18 | BUILDING - ANNUAL COST | LINE 14 X LINE 17 | 6.4236 | 4.9638 | 4.1707 | 5.1682
19 | DIGITAL SWITCH - ANNUAL COST FACTOR | WP 6.0, PG 1, LINE 4 | 0.31826 | 0.31826 | 0.31826 | 0.31826
20 | DIGITAL SWITCH - ANNUAL COST | LINE 10 X LINE 19 | 66.6052 | 51.4682 | 43.2447 | 53.5874
21 | TOTAL ANNUAL COST PER DC AMP | LINE 16 + LINE 18 + LINE 20 | 73.2053 | 56.5683 | 47.5299 | 58.8975
22 | MONTHLY RECURRING COST PER AMP | LINE 21 / 12 | 6.1004 | 4.714 | 3.9608 | 4.9081
23 | STATEWIDE WEIGHTING FACTOR | WP 6.0, PG 1, LINE 14 THRU 17 | 0.072287 | 0.39208 | 0.48867 | 0.046967
24 | WEIGHTED COST PER AMP | LINE 22 X LINE 23 | 0.44098 | 1.8483 | 1.9355 | 0.23052
25 | STATEWIDE COST PER AMP | SUM OF LINE 24 | 4.4553
26 | COMMON OVERHEAD FACTOR | WP 6.0, PG 1, LINE 11 | 1.0803
27 | MONTHLY COST PER AMP | LINE 25 X LINE 26 | 4.8131
28 | GROSS REVENUE LOADING | WP 6.0, PG 1, LINE 13 | 1.0027
29 | TOTAL STATEWIDE MONTHLY COST PER AC AMP | LINE 27 X LINE 28 | 4.8261

## WP 3.0 PG-1 DC-AC RATIO
PHYSICAL COLLOCATION
VERIZON MASSACHUSETTS
DC AMP TO AC AMP RATIO
| (A) | (B) | (C) | (D) | (E) | (F)
LINE NO. | ITEM | SOURCE | METRO | URBAN | SUBURBAN | RURAL
MICROPROCESSOR PLANT
1 | DC AMPS | WP 1.0, PG 1, LINE 1 | 6000 | 2600 | 2600 | 1200
DC EMERGENCY ENGINE
2 | SIZE RATED IN KW | WP 4.0, PG 1, LNS 2,7,12,17 | 1000KW | 350KW | 200KW | 80KW
3 | KW TO DC AMP CONVERSION | WP 4.0, PG 1, LNS 5,10,15,20 | 20833.3333 | 7291.6667 | 4166.6667 | 1666.6667
4 | DC AMPS - POWER PLANT CAPACITY | LINE 1 | 6000 | 2600 | 2600 | 1200
5 | DC AMPS AVAIL FOR ANCIL EQUIP | LINE 3 - LINE 4 | 14833.3333 | 4691.6667 | 1566.6667 | 466.6667
6 | DC % OF ENGINE CAPACITY | LINE 1 / LINE 3 | 28.8% | 35.66% | 62.4% | 72%
7 | AC % OF ENGINE CAPACITY | LINE 5 / LINE 3 | 71.2% | 64.34% | 37.6% | 28%

## WP 4.0 PG-1 KW TO DC
PHYSICAL COLLOCATION
VERIZON MASSACHUSETTS
KW TO DC AMPS
| (A) | (B) | (C)
LINE NO. | ITEM | SOURCE | DENSITY ZONE
| KW TO DC AMP CONVERSION |  | METRO
1 | FORMULA | ATTACHMENT #2 | DC AMPS=KW X 1000 / VOLTS
2 | METRO ENGINE SIZE - KW | ENGINEERING | 1000KW
3 | DC VOLTAGE | ENGINEERING | 48
4 | METRO FORMULA (KW TO DC AMPS) | LINE 1 | DC AMPS=1000 X 1000 / 48
5 | METRO ENGINE - DC AMPS | LINE 4 | 20833.3333
| KW TO AC AMP CONVERSION |  | URBAN
6 | FORMULA | ATTACHMENT #2 | DC AMPS=KW X 1000 / VOLTS
7 | URBAN ENGINE SIZE - KW | ENGINEERING | 350KW
8 | VOLTAGE OF CENTRAL OFFICE | ENGINEERING | 48
9 | URBAN FORMULA (KW TO DC AMPS) | LINE 6 | DC AMPS=350 X 1000 / 48
10 | URBAN ENGINE - DC AMPS | LINE 9 | 7291.6667
| KW TO AC AMP CONVERSION |  | SUBURBAN
11 | FORMULA | ATTACHMENT #2 | DC AMPS=KW X 1000 / VOLTS
12 | SUBURBAN ENGINE SIZE - KW | ENGINEERING | 200KW
13 | VOLTAGE OF CENTRAL OFFICE | ENGINEERING | 48
14 | SUBURBAN FORMULA (KW TO DC AMPS) | LINE 11 | DC AMPS=200 X 1000 / 48
15 | SUBURBAN ENGINE - DC AMPS | LINE 14 | 4166.6667
| KW TO AC AMP CONVERSION |  | RURAL
16 | FORMULA | ATTACHMENT #2 | DC AMPS=KW X 1000 / VOLTS
17 | RURAL ENGINE SIZE - KW | ENGINEERING | 80KW
18 | VOLTAGE OF CENTRAL OFFICE | ENGINEERING | 48
19 | RURAL FORMULA (KW TO DC AMPS) | LINE 16 | DC AMPS=80 X 1000 / 48
20 | RURAL ENGINE - DC AMPS | LINE 19 | 1666.6667

## WP 5.0 PG-1 KW TO AC
PHYSICAL COLLOCATION
VERIZON MASSACHUSETTS
KW TO AC CONVERSION
| (A) | (B) | (C)
LINE NO. | ITEM | SOURCE | DENSITY ZONE
| KW TO AC AMP CONVERSION |  | METRO
1 | FORMULA | ATTACHMENT #2 | AC AMPS=KW X 1000 / (1.73 X VOLTS X PF)
2 | METRO ENGINE SIZE - KW | ENGINEERING | 1000KW
3 | VOLTAGE OF CENTRAL OFFICE | ENGINEERING | 480 VOLTS
4 | POWER FACTOR (PF) | ATTACHMENT #3 | 0.8
5 | METRO FORMULA (KW TO AC AMPS) | LINE 1 | AC AMPS=1000 X 1000 / (1.73 X 480 X .8)
6 | METRO ENGINE - AC AMPS | LINE 5 | 1505.2987
| KW TO AC AMP CONVERSION |  | URBAN
7 | FORMULA | ATTACHMENT #2 | AC AMPS=KW X 1000 / (1.73 X VOLTS X PF)
8 | URBAN ENGINE SIZE - KW | ENGINEERING | 350KW
9 | VOLTAGE OF CENTRAL OFFICE | ENGINEERING | 208 VOLTS
10 | POWER FACTOR (PF) | ATTACHMENT #3 | 0.8
11 | URBAN FORMULA (KW TO AC AMPS) | LINE 7 | AC AMPS=350 X 1000 / (1.73 X 208 X .8)
12 | URBAN ENGINE - AC AMPS | LINE 11 | 1215.8181
| KW TO AC AMP CONVERSION |  | SUBURBAN
13 | FORMULA | ATTACHMENT #2 | AC AMPS=KW X 1000 / (1.73 X VOLTS X PF)
14 | SUBURBAN ENGINE SIZE - KW | ENGINEERING | 200KW
15 | VOLTAGE OF CENTRAL OFFICE | ENGINEERING | 208 VOLTS
16 | POWER FACTOR (PF) | ATTACHMENT #3 | 0.8
17 | SUBURBAN FORMULA (KW TO AC AMPS) | LINE 13 | AC AMPS=200 X 1000 / (1.73 X 208 X .8)
18 | SUBURBAN ENGINE - AC AMPS | LINE 17 | 694.7532
| KW TO AC AMP CONVERSION |  | RURAL
19 | FORMULA | ATTACHMENT #2 | AC AMPS=KW X 1000 / (1.73 X VOLTS X PF)
20 | RURAL ENGINE SIZE - KW | ENGINEERING | 80KW
21 | VOLTAGE OF CENTRAL OFFICE | ENGINEERING | 208 VOLTS
22 | POWER FACTOR (PF) | ATTACHMENT #3 | 0.8
23 | RURAL FORMULA (KW TO AC AMPS) | LINE 13 | AC AMPS=80 X 1000 / (1.73 X 208 X .8)
24 | RURAL ENGINE - AC AMPS | LINE 17 | 277.9013

## WP 6.0 PG-1 FACTORS
PHYSICAL COLLOCATION
VERIZON MASSACHUSETTS
FACTORS
| (A) | (B) | (C)
LINE NO. | ITEM | SOURCE | DATA
ANNUAL COST FACTORS
1 | LAND - ACCOUNT 2111 - FRC 20C | VCOST | 0.28108
2 | BUILDING - ACCOUNT 2121 - FRC 10C | VCOST | 0.41075
3 | BUILDING - ACCOUNT 2121 - FRC 13C | VCOST | 0.40981
4 | DIGITAL SWITCH - ACCOUNT 2212 - FRC 377C | VCOST | 0.31826
5 | DIGITAL CIRCUIT OTHER - FRC 357C (EXPENSE ONLY) | VCOST | 0.10815
6 | CONDUIT - ACCOUNT 2441 - FRC 4C | VCOST | 0.28285
OTHER FACTORS
7 | LAND INVESTMENT FACTOR | VCOST | 0.003
8 | BUILDING INVESTMENT FACTOR | VCOST | 0.0749
9 | DIGITAL CIRCUIT OTHER INSTALLATION FACTOR - 357C | VCOST | 1.532
10 | DIGITAL SWITCH POWER INSTALLATION FACTOR - 377C | VCOST | 2.7852
11 | COMMON OVERHEAD FACTOR | VCOST | 1.0803
12 | COMMON OVERHEAD FACTOR - LABOR ONLY | VCOST | 1.0892
13 | GROSS REVENUE LOADING | VCOST | 1.0027
14 | METRO STATEWIDE WEIGHTING FACTOR | SERVICE COSTS | 0.072287
15 | URBAN STATEWIDE WEIGHTING FACTOR | SERVICE COSTS | 0.39208
16 | SUBURBAN STATEWIDE WEIGHTING FACTOR | SERVICE COSTS | 0.48867
17 | RURAL STATEWIDE WEIGHTING FACTOR | SERVICE COSTS | 0.046967