|  |  | Massachusetts Department of Environmental Protection RTCR-2 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 5.0 | Atmospheric Storage Tanks Complete one form for each atmospheric storage tank. |  |  |  |  |  |  |
|  | Storage Tank Name: |  |  |  |  |  |  |
|  | Date of last complete storage tank inspection. |  |  | Interior Exterior Cleaned |  |  |  |
|  | List any unaddressed recommendations or noted deficiencies from that inspection: |  |  |  |  |  |  |
|  | As part of this Level 2 Assessment, identify what was evaluated for this storage tank: Exterior (ground level) Top Interior Other |  |  |  |  |  |  |
|  | Assessment Elements For any shaded box checked, it should be considered an issue and a description must be included. |  | Issue and/or Description *If any element has not been reviewed, you must include an explanation. |  |  |  |  |
|  |  |  |  |  | Yes | No | Not Reviewed* |
| 5.1 | Were any concerns or deficiencies noted in the monthly (last 12 months) or annual tank inspection report? If yes, have they been addressed? |  |  |  |  |  |  |
| 5.2 | Is the facility secured to prevent unauthorized access? |  |  |  |  |  |  |
| 5.4 | Is there any evidence of intentional contamination and/or unauthorized access at the storage tank? IMMEDIATELY Contact MA State Police and MassDEP |  |  |  |  |  |  |
| 5.5 | Does the drain/overflow line terminate at a minimum of 12" air gap? |  |  |  |  |  |  |
| 5.6 | Are the overflow and vents properly screened (24-mesh non-corrodible)? |  |  |  |  |  |  |
| 5.7 | Is the vent turned down and does it maintain an approved air gap at the termination point? |  |  |  |  |  |  |
| 5.8 | Were there any observed leaks? |  |  |  |  |  |  |
| 5.9 | Are there any unsealed openings in the storage facility, such as access doors, vents or joints? Does the access have the appropriate gasket? |  |  |  |  |  |  |
| 5.10 | Was there any observed physical deterioration of the tank? Could the physical condition of the tank be a source of contamination? |  |  |  |  |  |  |
| 5.11 | Has there been any recent tank maintenance (i.e. painting/coating)? If yes, when? If yes, was disinfection performed? |  |  |  |  |  |  |
| 5.12 | Is there a mixer? If yes, is it being used continuously? |  |  |  |  |  |  |
| 5.13 | Is lack of mixing or turnover an issue in the tank? Does excessive storage or variable demand contribute to turnover issues? |  |  |  |  |  |  |
| 5.14 | What was the measured chlorine residual (total/free) of the water exiting the storage tank on the date of the assessment? |  |  |  |  |  |  |
| 5.15 | Where is the sample tap located? If it is a location representative of the tank, how far away is it from the tank? |  |  |  |  |  |  |
| 5.16 | Was the sample collected when the water was exiting the tank? Does the PWS have procedures to ensure that samples are collected when the tank is emptying? |  |  |  |  |  |  |
| 5.17 | Other comments on the storage tank? |  |  |  |  |  |  |
| List all storage tank corrective actions taken (including date). Include assessment element number. |  |  |  |  |  |  |  |