This file incorporates comment from numerous stakeholders and building officials, staff, two BBRS advisory committees (SAC and C34AC), and others into the original redline code proposal approved by the BBRS in 2012.

780 CMR:	MASSACHUSETTS AMENDMENTS TO THE INTERNATIONAL EXISTING BUILDING CODE 2009

CHAPTER 34: EXISTING BUILDINGS AND STRUCTURES

CHAPTER 34: Delete in its entirety and replace with the International Existing Building Code 2009 (IEBC 2009) including its appendices, and as modified with Massachusetts Amendments as follows:

101.1 Replace as follows:

101.1 Title.  These regulations shall be known as the Existing Building Code of Massachusetts, hereinafter referred to as “this code.”

101.2 Replace as follows:

101.2 Scope.  The provisions of this code shall apply to the repair, alteration, change of occupancy, addition, and relocation of existing buildings.  See Table 101.2 below which includes, but is not limited to, applicable laws and specific use of other regulations.

TABLE 101.2 APPLICABLE LAWS AND REGULATIONS

| Unless directed otherwise in this code, reference to: | Shall mean to use the requirements found in: |
| --- | --- |
| International Plumbing Code | 248 CMR Board of Plumbers and Gas Fitters Regulations |
| International Property Maintenance Code | 780 CMR 1 |
| International Fire Code (IFC) Table 101.2: The IFC reference was synched with proposed language in Chapter 1. | Reference to the IFC for fire prevention issues shall be considered reference to 527 CMR Board of Fire Prevention Regulations. 527 CMR is enforced by the fire official. IFC provisions for prospective building code issues not otherwise addressed in 780 CMR are adopted. Retroactive building code provisions of the IFC are not adopted by 780 CMR. 780 CMR is enforced by the building official. |
| International Electrical Code | 527 CMR 12 Massachusetts Electrical Code |
| International Energy Conservation Code (IECC) | 780 CMR 13 and 51 (IECC with MA amendments) |
| International Mechanical Code (IMC) | Reference to the IMC for sheet metal work only shall be considered reference to 271 CMR Board of Examiners of Sheet Metal Workers, otherwise the IMC shall be used. |
| International Fuel Gas Code | 248 CMR Board of Plumbers and Gas Fitters Regulations |
| International Residential Code (IRC) | 780 CMR 51 Residential Volume (IRC with MA amendments). |
| International Building Code (IBC) or 780 CMR | 780 CMR Base Volume a.k.a. IBC with MA amendments. |
| Construction in flood areas | 780 CMR Appendix G |
| Accessibility | 521 CMR Architectural Access Board Regulations |
| Elevators and lifts | 524 CMR Board of Elevator Regulations |
| Sprinkler Systems | This code (780 CMR 34) or if applicable M.G.L. c. 148, § 26A, 26A1/2, 26G, 26G1/2, 26H or 26I, or M.G.L. c. 272 §§ 86 through 86d |
| Other requirements | Refer to: |
| for Carbon Monoxide Protection in all R-Uses | 780 CMR 9 |
| for A-2 Nightclubs Use | 780 CMR 1, 3, 9 and 10 |

Table 101.2: CO and nightclub requirements were moved from elsewhere in the document to this table.

101.5.0 Add subsections:

Section 101.5.0: After SAC review, structural compliance alternatives were allowed. The original proposal precluded this but earlier code editions did not.

101.5.0 Compliance Alternatives. Where compliance with the provisions of the code for new construction, required by this code, is impractical because of construction difficulties or regulatory conflicts, compliance alternatives may be accepted by the building official.  The building official may accept these compliance alternatives, archaic materials and assemblies in Resource A of this code, or others proposed.  If the compliance alternative involves fire protection systems the building official shall consult with the fire official.

101.5.0.1 Submittals.  The application for a permit shall be in accordance with 780 CMR 1 and identify all items of non- or partial compliance with the requirements of this code, and compliance alternatives, if any are proposed, for approval by the building official.  The building official shall respond to the acceptability of any proposed compliance alternatives within 30 days of the filing of the permit application.  Where proposed compliance alternatives are, in the opinion of the building official, unacceptable, or where issues of non-compliance remain, the permit applicant shall have the remedies prescribed by 780 CMR 113.

101.5.1 Replace as follows:

101.5.1 Prescriptive compliance method. Repairs, alterations, additions, and changes of occupancy complying with Chapter 3 of this code in buildings complying with these sections of the International Fire Code:

- 803 Interior Wall and Ceiling Finish and Trim in Existing Buildings

- 804 Interior Wall and Ceiling Trim in New and Existing Buildings

- 4603 Fire Safety Requirements for Existing Buildings

- 4604 Means of Egress for Existing Buildings

shall be considered in compliance with the provisions of this code. In International Fire Code Section 4603 any reference to ‘fire code official’ shall mean ‘building official and fire official’ and in International Fire Code Section 4604 any reference to ‘fire code official’ shall mean ‘building official’. In addition to these requirements,

The investigation and evaluation report (Section 101.5.4.0) shall indicate how the building will comply with Sections 803, 804, 4603 and 4604 of the International Fire Code.

Note: This compliance method shall not apply to Group R occupancies unless the Group R occupancy is in compliance with the fire suppression provisions of the 6th or later edition of 780 CMR 9.

Section 101.5.1: The sprinkler requirement for R-Use found in the note was moved from its original location in Section 301.1.2. It is suggested that the 7th edition be used instead of the 6th edition. The Chapter 34 Advisory Committee (C34AC) agreed to retain this requirement for the Prescriptive Method.

101.5.4.0 Add subsection:

101.5.4.0 Investigation and Evaluation.  For any proposed work regulated by this code and subject to 780 CMR 107, as a condition of the issuance of a permit the building owner shall cause the existing building (or portion thereof) to be investigated and evaluated in accordance with the provisions of this code

The investigation and evaluation shall be in sufficient detail to ascertain the effects of the proposed work on at least these systems: structural, means of egress, fire protection, energy conservation, lighting, and ventilation for the space under consideration and, where necessary, the entire building or structure and its foundation if impacted by the proposed work.

The results of the investigation and evaluation, along with any proposed compliance alternatives, shall be submitted to the building official in written report form.

Section 101.5.4.0 was clarified to include the review of several key building systems in the I&E report.

101.5.4.1 Item 1.  Replace this Item as follows:

1.   780 CMR using 100% of the prescribed forces.  For existing buildings with seismic force resisting systems found in Table 101.5.4.1.0, the values of R, Ω0, and Cd from this table shall be used in the analysis.  For seismic force resisting systems not found in Table 101.5.4.1.0, the values of R, Ω0, and Cd used for analysis in accordance with 780 CMR 16 shall be those specified for structural systems classified as “Ordinary” in accordance with Table 12.2-1 of ASCE 7, unless it can be demonstrated that the structural system satisfies the proportioning and detailing requirements for systems classified as “Intermediate” or “Special”.

101.5.4.1.0 Insert Table 101.5.4.1.0

The formatting of this Table and Table A106.2 went awry during various revisions of this file. The original format, text, and data values will be retained in the final version.

TABLE 101.5.4.1.0

| BASIC SEISMIC-FORCE-RESISTING SYSTEM | R | Ω0 | Cd |
| --- | --- | --- | --- |
| Bearing Wall Systems |  |  |  |
| Steel concentrically braced frame (CBF) with diagonal 3 or X-bracing |  |  |  |
| CBF per 6th Edition SBC2 except for Section 9.5 of 1992 AISC Seismic Provisions | 3.5 | 2 | 3.5 |
| Otherwise4 | 3 | 3 | 3 |
| Steel CBF with V, Inverted V or K bracing |  |  |  |
| V or Inverted V bracing per 6th Edition SBC2 | 3 | 3 | 3 |
| V or Inverted V bracing, otherwise4 | 3 | 3 | 3 |
| K bracing | 1.25 | 1.25 | 1.25 |
| Reinforced concrete shear walls with boundary elements and without coupling beams, in accordance with 780 CMR 1113.5.1.4a, 5th Edition | 5 | 2.5 | 5 |
| Reinforced concrete shear walls with reinforcing steel less than required by, or with spacing greater than permitted by Section 11.9.9 of ACI 318-08 | 1.5 | 1.5 | 1.5 |
| Unreinforced concrete shear walls | 1.25 | 1.25 | 1.25 |
| Reinforced masonry shear walls |  |  |  |
| Class A5 | 4.5 | 2.5 | 3.5 |
| Class B6 | 2.25 | 2.25 | 2.25 |
| Class C7 | 1.25 | 1.25 | 1.25 |
| Unreinforced masonry shear walls | 1.25 | 1.25 | 1.25 |
| Light-framed walls sheathed with wood structural panels or diagonal sheathing | 4 | 2.5 | 3 |
| Other light-framed walls10 | 2 | 2 | 2 |
| Building Frame Systems |  |  |  |
| Steel concentrically braced frame (CBF) with diagonal 3 or X-bracing |  |  |  |
| CBF per 6th Edition SBC2 except for Section 9.5 of 1992 AISC Seismic Provisions | 4 | 2 | 3.5 |
| Otherwise4 | 3 | 3 | 3 |
| Steel CBF with V, Inverted V or K bracing |  |  |  |
| V or Inverted V bracing per 6th Edition SBC2 | 3 | 3 | 3 |
| V or Inverted V bracing, otherwise4 | 3 | 3 | 3 |
| K bracing | 1.5 | 1.5 | 1.5 |
| Reinforced concrete shear walls with boundary elements and without coupling beams, in accordance with 780 CMR 1113.5.1.4a, 5th Edition | 6 | 2.5 | 5 |
| Reinforced concrete shear walls with reinforcing steel less than required by, or with spacing greater than permitted by Section 11.9.9 of ACI 318-08 | 1.5 | 1.5 | 1.5 |
| Unreinforced concrete shear walls | 1.5 | 1.5 | 1.5 |

| 34.00: continued Table 101.5.4.1.0 - continued |  |  |  |
| --- | --- | --- | --- |
| Reinforced masonry shear walls |  |  |  |
| Class A5 | 5 | 2.5 | 4 |
| Class B6 | 2.25 | 2.25 | 2.25 |
| Class C7 | 1.5 | 1.5 | 1.5 |
| Unreinforced masonry shear walls | 1.5 | 1.5 | 1.5 |
| Light-framed walls sheathed with wood structural panels or diagonal sheathing | 4 | 2.5 | 3 |
| Other light-framed walls10 | 2.5 | 2.5 | 2.5 |
| Moment Resisting Frame Systems |  |  |  |
| Steel moment frames |  |  |  |
| Special Moment Frame per 6th Edition SBC2 | 8 | 3 | 5.5 |
| Ordinary Moment Frame per 6th Edition SBC2 | 3.5 | 3.5 | 3.5 |
| Moment frame, otherwise4 | 3 | 3 | 3 |
| Reinforced concrete moment frames |  |  |  |
| Class A8 | 5 | 3 | 4.5 |
| Class B9 | 2.5 | 2.5 | 2.5 |
| Dual Systems (See ASCE 7, Section 12.2.5.1) |  |  |  |
| Steel concentrically braced frame (CBF) with steel moment frames (MF) |  |  |  |
| CBF and Special Moment Frame, per 6th Edition SBC2 | 5 | 2.5 | 4.5 |
| CBF and Moment Frame per 1st through 5th Editions SBC2, except V, Inverted V or K Braced Frames | 3.5 | 2.5 | 3.5 |
| CBF and Moment Frame per 1st through 5th Editions SBC2, with V, Inverted V or K Braced Frames | 3 | 2.5 | 3 |
| Otherwise | 1.5 | 1.5 | 1.5 |
| Reinforced concrete shear walls with boundary elements and without coupling beams, in accordance with 780 CMR 1113.5.1.4a, 5th Edition, with reinforced concrete moment frames, Class A8 | 6 | 2.5 | 5 |
| Ordinary reinforced concrete shear walls, as defined in 8th Edition SBC, with reinforced concrete moment frames, Class A8 | 5.5 | 2.5 | 4.5 |
| Notes: 1. Systems of previous editions of the State Building Code that meet the ductility requirements of the 8 th Edition of the Code are not included in this table. 2. SBC refers to 780 CMR Commonwealth of Massachusetts State Building Code. 3. A diagonal brace is one that frames from a beam-to-column connection diagonally to another beam-to-column connection or to a column at its base plate. 4. The seismic resistance of the frame shall be based on its seismic connections being subject to two times the computed forces and moments resulting from seismic load. 5. Class A reinforced masonry shear walls have a minimum total area of reinforcement in the vertical and horizontal direction at least 0.0020 times the gross cross-sectional area of the wall, with a minimum area in each direction at least 0.0007 times the gross cross-sectional area of the wall. Maximum spacing of reinforcing steel bars in grouted cells or bond courses is 6'-0" in one direction and 4'-0" in the other direction, but not more than 1/3 of the length or height of the wall, whichever is less, in each direction. Class A walls satisfy other requirements for reinforced masonry of the base code. 6. Class B reinforced masonry shear walls satisfy all requirements for Class A walls, except that spacing limits for reinforcing steel bars are exceeded. 7. Class C reinforced masonry shear walls satisfy all requirements for reinforced masonry of the base code. 8. Class A reinforced concrete moment frames satisfy requirements of Sections 1113.5.1, 1113.5.1.1, 1113.5.1.2 and 1113.5.1.3 of 780 CMR 5th Edition and Sections 11.12.1.1 and 11.12.1.2 of ACI 318-83 for reinforcing of beam to column joints. 9. Class B reinforced concrete moment frames do not satisfy requirements for Class A reinforced concrete moment frames. 10. Wood siding over horizontal or diagonal boards, plaster on wood or metal lath, and stucco on metal lath may be used to resist in-plane shear, where the walls are anchored to floors and to the floor or roof construction above such that they can transfer the shear between floors and to the foundation. Gypsum sheathing, lath, wall board, drywall, fiberboard and particle board are not permitted to resist in-plane shear unless originally designed in accordance with 780 CMR for that purpose. |  |  |  |

34.00:   continued

101.5.4.2 Add these exceptions to Item 1.

Exceptions:

1.   780 CMR using 50% of prescribed forces when directed here by sections 807.4.3

2.   780 CMR using either

a. 50 % of prescribed forces when directed here by Section 1003.3.1 and when the vertical addition increases the building area less than or equal to 30% or,

b. 75% of prescribed forces when directed here by section 1003.3.1 and when the vertical addition increases the building area more than 30% but less than 50%.

101.9 Add subsection:

101.9 Cumulative Effects of Alterations, Additions, or Changes of Occupancy on Structural Elements.  As noted in several sections of this code, evaluation of structural elements and their connections shall consider the cumulative effects of alterations, additions, or changes of occupancy since original construction.

Exception. When structural work:

- does not involve more than 2% of the total tributary area of horizontal framing members of any existing framed floor or roof and,

- does not alter shear walls above the foundation and,

- does not alter columns or diagonal braces and,

- does not create an opening in any framed floor or roof that has an area more than 2% of the framed floor or roof and,

- does not alter any floor or roof diaphragm and its connections such that in-plane shear resistance is reduced by more than 5% and,

- does not remove or reconfigure lateral load resisting frames, or foundations supporting them.

102.2 Replace as follows:

102.2 Other Laws and Specialty Codes.  See 780 CMR 1.

The original proposal deleted most of the Section 102 MA amendments by incorporation of the requirements into Table 101.2. Upon further review C34AC incorporated others into Table 101.2 as well and recommended deletion of the 102.2.1.3 amendment pertaining to Change in Commodities or Storage Arrangements since it singles out this one particular change of use.

PART 2 – ADMINISTRATION AND ENFORCEMENT and all sections contained within it, replace with:

PART 2 – ADMINISTRATION AND ENFORCEMENT.  For administration and enforcement provisions refer to 780 CMR 1.

202 Replace two and add two definitions as follows:

Two definitions were added to sync with 780 CMR Chapter 2.

CODE OFFICIAL. See BUILDING OFFICIAL in 780 CMR 2.

COMPLIANCE ALTERNATIVE. An alternative life-safety construction feature which meets or exceeds the requirements or intent of a specific provision of 780 CMR.  The building official is authorized to approve or disapprove compliance alternatives.  Compliance alternatives are allowed only for existing buildings.

HOUSE MUSEUM.  A house museum is an historic building or structure.  The principal use of such must be as an exhibit of the building or the structure itself which is open to the public not less than 12 days per year, although additional uses, original and/or ancillary to the principal use shall be permitted within the same building up to maximum of 40% of the gross floor area.  All entries into the house museum list shall be certified by the Massachusetts Historical Commission.  The list can be found at http://www.sec.state.ma.us/mhc/

REGISTERED DESIGN PROFESSIONAL IN RESPONSIBLE CHARGE. See REGISTERED DESIGN PROFESSIONAL in 780 CMR 2.

301.1.1 Add a last sentence as follows:

‘Addition or replacement of roofing or replacement of equipment shall comply with Sections 606.2 and 606.3 as applicable.’

302.3 After the first sentence, add this sentence:

The cumulative effect of the load increase since original construction shall be considered.

303.3 After the first sentence, add this sentence:

The cumulative effect of the load increase since original construction shall be considered.

303.7 Add Section:

303.7 Seismic Hazards.  Compliance with this section is required where the work area exceeds 50 percent of the aggregate area of the building.

303.7.1 Wall anchors for concrete and masonry buildings.  For any building assigned to Seismic Design Category B, C, D, E or F with a structural system consisting of concrete or reinforced masonry walls with flexible roof or floor diaphragms or unreinforced masonry walls with any type of roof or floor diaphragm, the alteration work shall include installation of wall anchors at the roof and floor levels to resist the reduced IBC-level seismic forces specified in Section 101.5.4.2, unless an evaluation demonstrates compliance of existing wall anchorage.

303.7.2 Bracing for unreinforced masonry parapets.  Parapets constructed of unreinforced masonry in buildings assigned to Seismic Design Category B, C, D, E or F shall have bracing installed as needed to resist the reduced IBC-level seismic forces specified in Section 101.5.4.2, unless an evaluation demonstrates compliance of such items. Parapet corrective work shall be performed in conjunction with the installation of tension roof anchors. The minimum height of a parapet above any wall anchor shall be 12 inches.

Exception:  If the maximum height of an unbraced unreinforced masonry parapet above the lower of either the level of tension anchors or the roof sheathing does not exceed a height-to-thickness ratio of 2.5, then bracing is not required.

Section 303.7.2:The parapet exception language was reviewed and clarified by SAC and carried through to section 606.3.1 and 807.5.2.

606.2 To exceptions 1 and 2, add a second sentence as follows:

The cumulative effect of the load increase since original construction shall be considered.

606.3.1 Add this exception:

Exception:  If the maximum height of an unbraced unreinforced masonry parapet above the lower of either the level of tension anchors or the roof sheathing does not exceed a height-to-thickness ratio of 2.5, then bracing is not required.

606.3.2 Modify as follows:

606.3.2 Roof diaphragms resisting wind loads in high wind regions. Where roofing materials are removed from the entire roof diaphragm of a building located where the basic wind speed is 115 mph and the occupancy category is type IV as defined in Table 1604.5 of 780 CMR,  roof diaphragms and connections that are part of the main wind-force resisting system shall be evaluated for the wind loads specified in 780 CMR., including wind uplift. If the diaphragms and connections in their current condition do not comply with those wind provisions, they shall be replaced or strengthened in accordance with the loads specified in 780 CMR.

Section 606.3.2: The wind speed of 120 mph was changed to 115 mph to synch with the change to the Chapter 16 wind speed table which now has a max value of 115 mph.

701.1 Replace the exception as follows:

Exception.  Buildings in which the reconfiguration is exclusively the result of compliance with the accessibility requirements of 521 CMR.

Section 704.2.2: C34AC reviewed this section and approved the 'two year' time period vs. the revised 'three year'. C34AC was not the original proponent of the change from two to three years. Two years has been the requirement since the 8th edition was originally promulgated.

704.2.2 Add this exception:

Exception.  R-2 structures of three units, undergoing Level 2 renovations, are exempt from the requirements of this section provided that:

1.   The work area is on a single unit and,

2.   No other permits for Level 2 work have been issued for the building in the previous two years.

704.2.2 Item 3.,704.2.3, and 704.2.4 Item 2.  Delete the word ‘municipal’

704.2.5 Replace as follows:

704.2.5 Supervision.  Fire sprinkler systems required by this section shall be supervised in accordance with 780 CMR 9

704.4.1.1 through 704.4.1.7, and 704.4.3  Replace ‘International Fire Code’ with 780 CMR 9.

705.2 Delete Exception 1.

705.4.4 Insert after the ‘100’ text as follows:

‘and Nightclubs with an occupant load of 50 or greater’

707.4 Add this as a second sentence to Exception 1:

The cumulative effect of the stress increase since original construction shall be considered for the purposes of this exception.

707.5.1 Add subsection:

707.5.1 Irregularities.  Where the alteration results in a structural irregularity as defined in ASCE 7, the lateral load-resisting structural elements shall comply with the structural requirements specified in section 807.4.

802.1 Replace this section as follows:

802.1 High-rise buildings.  High-rise buildings as defined by 780 CMR 2 shall comply with the requirements of Sections 802.1.1.

804.1.1 Delete the word ‘municipal’ which occurs in two locations.

804.2.1 Delete Exception 2.

807.4.3: At the end of this section add these two sentences:

For the purposes of calculating demand-capacity ratios, the demand shall consider applicable load combinations with design lateral loads or forces in accordance with 780 CMR 1609 and 1613. For purposes of this section, comparisons of demand-capacity ratios and calculation of design lateral loads, forces, and capacities shall account for the cumulative effects of additions and alterations since original construction.

807.5 Add sections:

807.5 Seismic Hazards.  Compliance with this section is required only when the work area exceeds 50 percent of the aggregate area of the building.

807.5.1 Wall anchors for concrete and masonry buildings.  For any building assigned to Seismic Design Category B, C, D, E or F with a structural system consisting of concrete or reinforced masonry walls with flexible roof or floor diaphragms or unreinforced masonry walls with any type of roof or floor diaphragm, the alteration work shall include installation of wall anchors at the roof and floor levels to resist the reduced IBC-level seismic forces specified in Section 101.5.4.2, unless an evaluation demonstrates compliance of existing wall anchorage.

807.5.2 Bracing for unreinforced masonry parapets.  Parapets constructed of unreinforced masonry in buildings assigned to Seismic Design Category B, C, D, E or F shall have bracing installed as needed to resist the reduced IBC-level seismic forces specified in Section 101.5.4.2, unless an evaluation demonstrates compliance of such items. Parapet corrective work shall be performed in conjunction with the installation of tension roof anchors. The minimum height of a parapet above any wall anchor shall be 12 inches.

Exception:  If the maximum height of an unbraced unreinforced masonry parapet above the lower of either the level of tension anchors or the roof sheathing does not exceed a height-to-thickness ratio of 2.5, then bracing is not required.

902.1 Add items 10.  and 11.  and the note as follows:

10.   Day care.  (see 780 CMR for classification)

11.   Group homes.

Note.  Also see section 912 when change of occupancy classification occurs

907.1 Add this as a second sentence to the exception:

The cumulative effect of the stress increase since original construction shall be considered for the purpose of this exception.

MA amendment 907.3.1 was shortened and clarified but there was no change in the requirements.

907.3.1 Replace first paragraph and Exception 1 as follows:

907.3.1 Compliance with the International Building Code level seismic forces. Where a building or portion thereof is subject to a change of occupancy that results in the building being assigned to a higher occupancy category based on 780 CMR Table 1604.5, the building shall comply with seismic forces as specified in Section 101.5.4.1 for the new occupancy category.

Exceptions:

1. Any occupancy being changed to Group A, E, I-1, R-1, R-2 or R-4 occupancies for buildings less than six stories in height and in Seismic Design Category A, B or C.

1002.3 Delete

1003.2 To exception 1 add a second sentence as follows:

The cumulative effect of the stress increase since original construction shall be considered for the purpose of this exception.

1003.3.1 Add a second sentence as follows:

Where the addition increases the building area less than 50%, the evaluation and analysis shall demonstrate compliance with reduced seismic force levels as specified in section 101.5.4.2.

SAC reviewed 1003.3.4 and recommended deletion since structural irregularity does not apply to additions.

1003.4 To exception 1 add a second sentence as follows:

The cumulative effect of the stress increase since original construction shall be considered for the purpose of this exception.

1101.1 Replace this section as follows:

1101.1 Scope.  It is the intent of this chapter to provide means for the preservation of historic buildings as certified by the Massachusetts Historical Commission.  There is no obligation for owners of historic buildings to use the provisions of this chapter.  This chapter shall preempt all other regulations of 780 CMR governing the reconstruction, renovation, alteration, change of use and occupancy, repair, maintenance and additions for the conformity of historic buildings and structures to 780 CMR, with the exception of 780 CMR 113 for appeals, or unless otherwise specified.  In case of fire or other casualty to a historic building, said building may be rebuilt, in total or in part, using such techniques and materials as are necessary to restore it to its original condition and use group.  If a building or structure as a result of proposed work would become eligible for certification as a historic building and the Massachusetts Historical Commission so certifies by affidavit, and such affidavit is submitted to the building official with the permit application, then the building official shall have the authority to allow the work to proceed under the provisions of this chapter.

1101.3 Replace all references to ‘museum’ with ‘house museum’

C34AC recommended that MA amendment 1102.5 be deleted so as to retain the original IEBC requirements for repair or replacement of existing or missing historic features, with the exception of glazing found in 'hazardous' locations. IEBC commentary states that glazing reproductions of proper material have negligible cost increases vs. those that do not.  Also an owner can seek a compliance alternative if this glazing requirement is problematic.

C34AC recommended that MA amendment 1103.2 and 1103.2.1 (Maximum Occupancy) be rewritten, deleted, or combined into 1103.3. The effect of these original amendment(s) was unclear because of an inconsistency in the section numbering. Also Maximum Occupancy of a house museum will be determined per the Report requirements of section 1101.2.

1103.3 Add a second paragraph as follows:

Where one or more floors of a house museum are limited to one means of egress, the occupancy load shall be computed as follows:

1.   Floors below the First Story.  Not more than one occupant per 100 square feet of gross floor area with a maximum occupancy of 49.

2.   First Story.  Not more than one occupant per 50 square feet of gross floor area.

3.   Second Story and Above.  Not more than one occupant per 100 square feet of gross floor area, or 30 occupants per 22 inch unit of egress width, whichever condition results in the lesser occupancy load.

1103.12 Replace as follows:

1103.12 Fire Protection Equipment.  Fire protection equipment shall be provided for house museums according to the following requirements:

1.   Manual Fire Extinguishing Equipment.  All use groups, other than R-3 and R-4, shall have approved manual fire extinguishing equipment, as determined by the head of the local fire department.

2.   Fire Alarm Systems.  Use groups R-1, R-2 and R-3 shall conform to the requirements of 780 CMR 907, as applicable.  All other use groups shall comply with Section 1103.12 items 2.(a) and (b)

(a)   Locations.  Provide smoke detectors in accordance with manufacturers listing and spacing requirements, but not less than one, for every 1200 square feet of floor area per level.  In addition, all lobbies, common corridors, hallways and exitway access and discharge routes shall be provided with approved smoke detectors installed in accordance with the manufacturers listing and spacing requirements but not more than 30 feet spacing between detectors.  All required smoke detectors shall have an alarm audible throughout the structure or building.

(b)    Single Station and Multiple Station Smoke Detection Devices.  As required by 780 CMR 9.

3.   Manual Pull Stations.  A manual fire alarm pull station shall be provided in the natural path of egress in all use groups except R-3 and R-4.  Manual pull stations shall be connected to the building fire warning system in conformance with NFPA 72.

Exception.  House museums which are provided with an approved automatic fire-extinguishing system throughout shall not be required to be provided with manual fire extinguishing equipment.  Smoke detection devices shall not be required in occupancies other than Use Groups R-1, R-2, and R-3.

1103.12.1 Supervision.  Fire alarm systems required by this section shall be supervised in accordance with the requirements 780 CMR 9.

Exception.  Residential single and multiple station smoke detectors.

1106.1 Add a second exception as follows:

Exceptions

2.    House museums need not comply with the wind load and seismic load requirements of this code.

1301.1.2

MA amendment 1301.1.2 which precludes the owner of any R-Use building the option of using the Performance Compliance Method unless the building has a sprinkler system, was included in the original proposal. C34AC did not propose this change in its recommended revisions per the Model 15 effort. C34AC reviewed this MA amendment and recommended that it be deleted. It recommended that the Prescriptive Method retain this identical amendment but not the Performance Method. When one uses this method all life safety systems of the building are considered and if the building official is uncomfortable with the plans a peer review by a registered design professional can be requested.

1301.2 Delete the first sentence of this section.

Section 1301.2: The original MA amendment and section 101.5 had an inherent conflict. Section 101.5 allows the owner to choose the compliance method, while section 1301.2 did not.

The amendment, as written now, which deletes the first sentence of the section removes the conflict..

1301.3.4 Add section:

1301.3.4 Peer review.  At the discretion of the building official, the owner shall engage a registered design professional to review the performance compliance evaluation and methodologies proposed to determine compliance with this section.  The registered design professional shall prepare a written report to the building official summarizing the results of their review.  Items identified by the registered design professional as needing modification in order to be in compliance with this section shall be addressed to the satisfaction of the building official prior to the issuance of a building permit.

1301.6.17 Add note as follows:

Note.  Automatic sprinklers required by M.G.L. c. 148 § 26G need not be considered “Required sprinklers” for the purposes of this section.

1401.1 Add two notes at the end of this section:

Note 1.  As applicable, Department of Environmental Protection (DEP) Regulations, 310 CMR 7.09: U Dust, Odor, Construction and Demolition, and the requirements of M.G.L. c. 111 § 150A, addressing disposal of demolition debris, must be satisfied.

Note 2.  As applicable, 527 CMR, in conjunction with M.G.L. c. 148 § 27A must be satisfied if fire protection systems are to be dismantled, shut-off, or modified.

1401.4.1 Add section:

1401.4.1 Removal of Waste Material.  Material shall not be dropped by gravity or thrown outside the exterior walls of a building during demolition or erection, Chutes shall be provided for the removal of such materials.  Where the removal of any material will cause an excessive amount of dust, such material shall be wet down to prevent the creation of a nuisance.

Exception.  The requirements of this section may be waived based on site conditions if approved by the building official.

1401.5 Replace ‘the International Plumbing Code’ with ‘the requirements of DPH and 248 CMR, as applicable’.

1407.1 Replace ‘section 110.3’ with 780 CMR 1.

1409 Delete this section.

Appendix A106.2 Add subsection 4 as follows:

4.   The values contained in Table A106.2 shall be used as material property values of the existing material listed therein, unless values are specified by other provisions in this chapter, or values are used, based on available historical information for a particular type of masonry construction, prevailing codes, and assessment of existing conditions.

A106.2 Insert TABLE A106.2 MATERIAL PROPERTY VALUES

TABLE A106.2 MATERIAL PROPERTY VALUES

| Symbol/ Notation | Description | Maximum Value | Notes |
| --- | --- | --- | --- |
| f΄m | See Section A104 | 300 psi | Per section A108.3 |
| Em | Elastic Modulus in Compression | 550,000 psi | Based on f΄m = 1,000 psi |
| f΄sp | See Section A104 | 0 psi | - |
| vm | Masonry with running bond lay-up | 20 psi | - |
| vm | Masonry, fully grouted, with a lay-up other than running bond | 20 psi | - |
| vm | Masonry, partially grouted or ungrouted, with a lay-up other than running bond | 10 psi | - |

The original MA amendment allowed use of Resource A if OK with the building official. Instead Resource A is allowed via a change to the language of Compliance Alternatives in Section 101.5.0