RADON SCREENING SURVEY Abington Early Education/Pre-K, Middle, High School 201 Gliniewicz Way Abington, MA Prepared by: Massachusetts Department of Public Health Bureau of Environmental Health Indoor Air Quality Program Radon Assessment Unit May, 2019

# Background

| Dates of Assessment: | 3/18/2019 through 3/20/2019 |
| --- | --- |
| Building Name: | Abington Early Education/PreK, Middle, High School |
| Address: | 201 Gliniewicz Way, Abington, MA |
| Assessment Requested by: | Abington Public School Dept. |
| Massachusetts Department of Public Health Bureau of Environmental Health (MDPH/BEH) Staff Conducting Assessment: | Lisa A. Hébert, Senior Technical Radon Specialist, Indoor Air Quality (IAQ) Program, Radon Unit |

# Methods

Radon samples were collected for the purpose of this radon survey using the United States Environmental Protection Agency (US EPA) Method #402-R-92-004 Liquid Scintillation (LS). Sampling devices were obtained through AccuStar Labs, a certified radon laboratory. One hundred seventy nine devices were deployed throughout the building for a minimum 48-hour time period. Devices were deployed on 3/18/2019 and collected on 3/20/2019.

# Results

Tests were taken during normal operations at Abington Early Education/Pre-K, Middle, High School. Of the 179 areas where test devices were deployed, devices from 175 areas were collected and submitted to AccuStar Labs. The lab results from the survey appear in Appendix A.

# Discussion

Radon Unit staff reviewed the lab results from AccuStar Labs and found all quality assurance parameters within acceptable limits. Appendix A shows that radon levels in the building ranged from less than 0.4 pCi/L to 5.7 pCi/L. Two areas screened had radon levels above the US EPA action guideline of 4 picocuries per liter of air pCi/L (Custodial Rm (adjacent to 1007, Room M1-A). Both rooms are currently unoccupied. Radon levels were not elevated elsewhere.  Please note that four vials could not be submitted due to being missing/tampered/found on floor. Five additional areas were not tested due to either lack of access or due to being unoccupied spaces.  These areas were:

•	IDF4 - (Vial # 3136166)

•	High School Boys Locker Rm – (Vial # 3136126)

•	Middle School Boys Locker Rm – (Vial # 3136129)

•	Middle School Girls Locker Rm – (Vial # 3136130)

•	Electric and IDF rooms adjacent to HS Men’s Locker Rm

•	Storage room in athletic office 1026

•           1204C Acid Tank Room

•           Custodial near 1226

## Radon Gas

According to the National Research Council (NRC, 1999), “low levels of radon are present in all the air we breathe.” Radon is a naturally occurring, radioactive gas that is produced by the natural decay of uranium in the soil. The average outdoor radon level is about 0.4 pCi/L (US EPA, 2009). Once radon is formed, it migrates through various pathways in the soil and can enter a building through cracks, holes, and joints in a building’s foundation (US EPA, 2009). The EPA recommends mitigation for indoor radon levels at or above 4 pCi/L.

According to the US EPA (2009), radon gas “decays into radioactive particles that can get trapped in your lungs when you breathe. As they break down further, these particles release small bursts of energy.” This activity can damage your lung tissue and increase a person’s risk of developing lung cancer (US EPA, 2009). Radon is the leading cause of lung cancer in non-smokers. In 2005, the U.S. Surgeon General issued a health advisory stating that indoor radon is the second leading cause of lung cancer (US EPA, 2013).

# Recommendations

Based on the measurements and observations made during the visit, the following recommendations are made.

It would be prudent to contact certified radon measurement and mitigation specialists to confirm the results found (Rooms 1007, M1-A) and to assess any occupied rooms above the rooms in question and to mitigate any elevated areas. The two organizations that certify radon measurement and mitigation specialists are:

  - National Radon Safety Board (NRSB) www.nrsb.org

  - American Association of Radon Scientists and Technologists (AARST) http://aarst-nrpp.com/wp/.

It would be prudent for your radon measurement specialist to test areas with missing/disturbed/tampered sampling devices, untested occupied rooms above unoccupied untested areas during confirmation testing. These areas include:

  - IDF4

  - High School Boys Locker Rm

  - Middle School Boys Locker Rm

  - Middle School Girls Locker Rm

  - Electric and IDF rooms adjacent to HS Men’s Locker Rm

  - Storage room in athletic office 1026

  - 1204c Acid tank room

  - Custodial near 1226

Refer to resource manual and other related IAQ documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings. These documents are available at: http://mass.gov/dph/iaq.

If you have any questions or concerns, please call the Massachusetts Department of Public Health Radon Assessment Unit at (413) 586-7525.

References

National Research Council (NRC). 1999. Risk Assessment of Radon in Drinking Water, National Academy Press.

United States Environmental Protection Agency (US EPA). 2009. “A Citizen’s Guide to Radon.  The Guide To Protecting Yourself and Your Family From Radon”. US Environmental Protection Agency.  EPA402/K-09/001. January 2009.

United States Environmental Protection Agency (US EPA). 2013. “Home Buyers and Seller’s Guide to Radon”. US Environmental Protection Agency. EPA402/K-13/002. September 2013.

# Appendix A

# Radon Survey Results

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

### Log Number

Device Number

Test Exposure Duration:

Area Tested

Result

pCi/L

2455783  3135886

2455784  3135887

2455785  3135888

2455786  3135889

2455787  3135890

2455788  3135891

2455789  3135892

2455790  3135893

2455791  3135894

2455792  3135895

2455793  3135896

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

1:30 pm

1:40 pm

1:40 pm

1:40 pm

1:45 pm

1:50 pm

1:55 pm

1:55 pm

2:00 pm

2:00 pm

2:05 pm

03/20/2019  2:45 pm

03/20/2019  2:50 pm

03/20/2019  2:50 pm

03/20/2019  2:50 pm

03/20/2019  2:50 pm

03/20/2019  2:55 pm

03/20/2019  2:55 pm

03/20/2019  2:55 pm

03/20/2019  2:55 pm

03/20/2019  3:00 pm

03/20/2019  3:00 pm

Room M-1 Mechanical Room E-1

Room EE-1

Room 1005 Room MDF1 Room 1006A Room 1006B Room MDF-2 Room 1006C Room 1006D Room 1007

< 0.4

< 0.4

< 0.4

0.4

0.4

0.7

0.7

1.5

0.8

0.7

0.4

Comment:

A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

### Log Number

Device Number

Test Exposure Duration:

Area Tested

Result

pCi/L

2455794  3135897

2455795  3135898

2455796  3135899

2455797  3135900

2455798  3136101

2455799  3136102

2455800  3136103

2455801  3136104

2455802  3136105

2455803  3136106

2455804  3136107

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

2:05 pm

1:55 pm

1:55 pm

2:05 pm

2:15 pm

2:20 pm

2:25 pm

2:25 pm

2:30 pm

2:35 pm

2:35 pm

03/20/2019  3:00 pm

03/20/2019  2:55 pm

03/20/2019  2:55 pm

03/20/2019  3:05 pm

03/20/2019  3:10 pm

03/20/2019  3:10 pm

03/20/2019  3:10 pm

03/20/2019  3:10 pm

03/20/2019  3:15 pm

03/20/2019  3:15 pm

03/20/2019  3:15 pm

Room Custodial QA-1

QA-2

QA-3

Room 1008B

Room Middle School Gym NW Room Middle School Gym NE Room Gym Storage 1010D

Room Gym Storage and Workout 1010C Room HS Gym 1010B NE

Room HS Gym 1010B SE

4.5

1.0

1.5

< 0.4

< 0.4

< 0.4

< 0.4

0.5

< 0.4

< 0.4

0.4

Comment:

A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

### Log Number

Device Number

Test Exposure Duration:

Area Tested

Result

pCi/L

2455805  3136108

2455806  3136109

2455807  3136110

2455808  3136111

2455809  3136113

2455810  3136114

2455811  3136115

2455812  3136116

2455813  3136117

2455814  3136118

2455815  3136119

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

2:40 pm

2:40 pm

2:45 pm

2:50 pm

2:50 pm

2:50 pm

2:50 pm

2:55 pm

2:55 pm

3:00 pm

2:15 pm

03/20/2019  3:20 pm

03/20/2019  3:20 pm

03/20/2019  3:20 pm

03/20/2019  3:20 pm

03/20/2019  3:25 pm

03/20/2019  3:25 pm

03/20/2019  3:25 pm

03/20/2019  3:30 pm

03/20/2019  3:30 pm

03/20/2019  3:35 pm

03/20/2019  3:10 pm

Room HS Gym 1010B SW Room HS Gym 1010B NW Room 1015 Fitness Center Room 1017 Auditorium E Room 1017 Auditorium W Room Stage Left

Room Stage Right

Room 1017 Auditorium Upper Room 1016 Athletic Office Room 1013

QA-4

< 0.4

< 0.4

< 0.4

0.4

0.5

0.4

0.4

0.4

0.9

0.4

0.4

Comment:

A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

| Log Number | Device Number | Result Test Exposure Duration: Area Tested pCi/L |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2455816 | 3136120 | 03/18/2019 | 2:55 pm | 03/20/2019 | 3:30 pm | QA-5 | 1.0 |
| 2455817 | 3136121 | 03/18/2019 | 3:00 pm | 03/20/2019 | 3:35 pm | QA-6 | < 0.4 |
| 2455818 | 3136122 | 03/18/2019 | 3:05 pm | 03/20/2019 | 3:50 pm | Room HS Girls 1012D | 0.4 |
| 2455819 | 3136123 | 03/18/2019 | 3:05 pm | 03/20/2019 | 3:50 pm | Girls Locker Room | 0.5 |
| 2455820 | 3136124 | 03/18/2019 | 3:10 pm | 03/20/2019 | 3:55 pm | Room Girls Locker Office | 0.4 |
| 2455821 | 3136125 | 03/18/2019 | 3:15 pm | 03/20/2019 | 3:40 pm | Room Custodial | 2.3 |
| 2455822 | 3136127 | 03/18/2019 | 3:20 pm | 03/20/2019 | 3:45 pm | Room HS 1011D | 1.7 |
| 2455823 | 3136128 | 03/18/2019 | 3:20 pm | 03/20/2019 | 3:44 pm | Room HS Locker 1011A | 0.5 |
| 2455824 | 3136131 | 03/18/2019 | 3:35 pm | 03/20/2019 | 4:00 pm | Room 1003 Music | 0.6 |
| 2455825 | 3136132 | 03/18/2019 | 3:35 pm | 03/20/2019 | 4:00 pm | Room 1003C | 0.6 |
| 2455826 | 3136133 | 03/18/2019 | 3:40 pm | 03/20/2019 | 4:05 pm | Room 1003B | 0.8 |

## Comment:

### A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

| Log Number | Device Number | Result Test Exposure Duration: Area Tested pCi/L |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2455827 | 3136134 | 03/18/2019 | 3:40 pm | 03/20/2019 | 4:05 pm | Room 1003A | 0.6 |
| 2455828 | 3136135 | 03/18/2019 | 3:40 pm | 03/20/2019 | 4:05 pm | Room 1004 | 0.9 |
| 2455829 | 3136136 | 03/18/2019 | 3:45 pm | 03/20/2019 | 4:10 pm | Room IDF1-A | 0.7 |
| 2455830 | 3136137 | 03/18/2019 | 3:45 pm | 03/20/2019 | 4:10 pm | Room M1-A | 5.7 |
| 2455831 | 3136138 | 03/18/2019 | 3:45 pm | 03/20/2019 | 4:10 pm | Room E1-A | 0.7 |
| 2455832 | 3136139 | 03/18/2019 | 3:20 pm | 03/20/2019 | 3:45 pm | QA-7 | 1.6 |
| 2455833 | 3136140 | 03/18/2019 | 3:35 pm | 03/20/2019 | 4:00 pm | QA-8 | 0.6 |
| 2455834 | 3136141 | 03/18/2019 | 3:40 pm | 03/20/2019 | 4:10 pm | QA-9 | < 0.4 |
| 2455835 | 3136142 | 03/18/2019 | 3:50 pm | 03/20/2019 | 4:15 pm | 1017B | 0.6 |
| 2455836 | 3136143 | 03/18/2019 | 3:55 pm | 03/20/2019 | 4:15 pm | Room 1018 | 0.7 |
| 2455837 | 3136144 | 03/18/2019 | 4:00 pm | 03/20/2019 | 4:20 pm | Room Green Wave Café | 1.0 |

## Comment:

### A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

### Log Number

Device Number

Test Exposure Duration:

Area Tested

Result

pCi/L

2455838  3136146

2455839  3136147

2455840  3136148

2455841  3136149

2455842  3136150

2455843  3136151

2455844  3136152

2455845  3136153

2455846  3136154

2455847  3136155

2455848  3136156

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

4:00 pm

4:00 pm

4:05 pm

4:05 pm

4:10 pm

4:10 pm

4:15 pm

4:15 pm

4:20 pm

4:20 pm

4:20 pm

03/20/2019  4:25 pm

03/20/2019  4:25 pm

03/20/2019  4:30 pm

03/20/2019  4:30 pm

03/20/2019  4:30 pm

03/20/2019  4:30 pm

03/20/2019  4:35 pm

03/20/2019  4:35 pm

03/20/2019  4:35 pm

03/20/2019  4:35 pm

03/20/2019  4:40 pm

Room 1019A Room 1000F Room 1100A Room 1000C Room 1100A E-3

Room M-3 Room 1001 Room IDF3 Room 1002A Room 1002B

0.7

0.6

< 0.4

0.6

< 0.4

2.1

1.3

0.8

0.6

< 0.4

< 0.4

Comment:

A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

### Log Number

Device Number

Test Exposure Duration:

Area Tested

Result

pCi/L

2455849  3136157

2455850  3136158

2455851  3136159

2455852  3136160

2455853  3136161

2455854  3136162

2455855  3136163

2455856  3136164

2455857  3136165

2455858  3136167

2455859  3136168

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

4:25 pm

4:25 pm

4:30 pm

3:50 pm

3:55 pm

4:25 pm

4:30 pm

4:35 pm

4:35 pm

4:40 pm

4:40 pm

03/20/2019  4:40 pm

03/20/2019  4:40 pm

03/20/2019  4:40 pm

03/20/2019  4:15 pm

03/20/2019  4:15 pm

03/20/2019  4:40 pm

03/20/2019  4:45 pm

03/20/2019  4:45 pm

03/20/2019  4:45 pm

03/20/2019  4:50 pm

03/20/2019  4:55 pm

Room 1002C Room 1002D Room 1104 QA-10

QA-11

QA-12

Room 1106

Room 1108

Room 1110 Room Custodial Room 1122

< 0.4

< 0.4

< 0.4

0.5

0.4

< 0.4

1.0

< 0.4

0.4

1.5

< 0.4

Comment:

A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

### Log Number

Device Number

Test Exposure Duration:

Area Tested

Result

pCi/L

2455860  3136169

2455861  3136170

2455862  3136171

2455863  3136172

2455864  3136173

2455865  3136174

2455866  3136175

2455867  3136176

2455868  3136177

2455869  3136179

2455870  3136180

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

4:45 pm

4:45 pm

4:50 pm

4:50 pm

4:50 pm

4:50 pm

4:55 pm

4:55 pm

5:00 pm

5:00 pm

5:00 pm

03/20/2019  4:55 pm

03/20/2019  4:55 pm

03/20/2019  4:55 pm

03/20/2019  5:00 pm

03/20/2019  5:00 pm

03/20/2019  5:00 pm

03/20/2019  5:00 pm

03/20/2019  5:05 pm

03/20/2019  5:05 pm

03/20/2019  5:10 pm

03/20/2019  5:10 pm

Room 1124

Room 1126

Room 1127

Room 1125

Room 1123

Room 1121

Room 1120

Room 1111

Room 1112

Room 1114

Room 1116

< 0.4

< 0.4

< 0.4

0.4

< 0.4

< 0.4

< 0.4

< 0.4

< 0.4

0.8

0.4

Comment:

A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

### Log Number

Device Number

Test Exposure Duration:

Area Tested

Result

pCi/L

2455871  3136181

2455872  3136182

2455873  3136183

2455874  3136184

2455875  3136185

2455876  3136186

2455877  3136187

2455878  3136188

2455879  3136189

2455880  3136190

2455881  3136191

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

4:45 pm

4:45 pm

4:45 pm

5:05 pm

5:05 pm

5:10 pm

5:10 pm

5:15 pm

5:15 pm

5:20 pm

5:20 pm

03/20/2019  4:55 pm

03/20/2019  4:55 pm

03/20/2019  5:10 pm

03/20/2019  5:10 pm

03/20/2019  5:15 pm

03/20/2019  5:15 pm

03/20/2019  5:15 pm

03/20/2019  5:35 pm

03/20/2019  5:40 pm

03/20/2019  5:30 pm

03/20/2019  5:30 pm

QA-13 QA-14 QA-15

Room 1118

Room 1117

Room 1115

Room 1113 Room E-4 Room IDF-4A Room 1109

Room 1107

< 0.4

< 0.4

< 0.4

0.4

0.4

0.6

0.6

0.8

0.4

0.5

0.4

Comment:

A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

### Log Number

Device Number

Test Exposure Duration:

Area Tested

Result

pCi/L

2455882  3136192

2455883  3136193

2455884  3136194

2455885  3136195

2455886  3136196

2455887  3136197

2455888  3136198

2455889  3136199

2455890  3136200

2455891  3136201

2455892  3136202

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

5:20 pm

5:25 pm

5:25 pm

5:25 pm

5:30 pm

5:30 pm

5:05 pm

5:05 pm

5:30 pm

5:35 pm

5:35 pm

03/20/2019  5:35 pm

03/20/2019  5:35 pm

03/20/2019  5:40 pm

03/20/2019  5:40 pm

03/20/2019  5:45 pm

03/20/2019  5:45 pm

03/20/2019  5:10 pm

03/20/2019  5:15 pm

03/20/2019  5:40 pm

03/20/2019  5:50 pm

03/20/2019  5:50 pm

Room 1105 Room 1105A Room 1103 Room 1103A Room 1103B Room 1103C QA-16

QA-17 QA-18

Room 1103D Room 1103E

< 0.4

0.5

< 0.4

0.6

0.5

0.7

< 0.4

< 0.4

< 0.4

0.5

0.5

Comment:

A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

| Log Number | Device Number | Result Test Exposure Duration: Area Tested pCi/L |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2455893 | 3136203 | 03/18/2019 | 5:35 pm | 03/20/2019 | 5:50 pm | Room 1103G | 0.6 |
| 2455894 | 3136204 | 03/18/2019 | 5:40 pm | 03/20/2019 | 5:50 pm | Room 1103F | 0.7 |
| 2455895 | 3136205 | 03/18/2019 | 5:40 pm | 03/20/2019 | 5:50 pm | Room 1103H | 0.7 |
| 2455896 | 3136206 | 03/18/2019 | 5:40 pm | 03/20/2019 | 5:50 pm | Room 1100G | 0.7 |
| 2455897 | 3136207 | 03/18/2019 | 5:40 pm | 03/20/2019 | 5:55 pm | Room 1100E | 0.7 |
| 2455898 | 3136208 | 03/18/2019 | 5:45 pm | 03/20/2019 | 5:55 pm | Room 1100D | 0.5 |
| 2455899 | 3136209 | 03/18/2019 | 5:45 pm | 03/20/2019 | 5:55 pm | Room 1100C | 0.9 |
| 2455900 | 3136210 | 03/18/2019 | 5:45 pm | 03/20/2019 | 5:55 pm | Room 1100B | 0.5 |
| 2455901 | 3136211 | 03/18/2019 | 5:45 pm | 03/20/2019 | 5:55 pm | Room 1100F | 0.9 |
| 2455902 | 3136212 | 03/18/2019 | 5:50 pm | 03/20/2019 | 6:00 pm | Room 1100A | 0.7 |
| 2455903 | 3136213 | 03/18/2019 | 5:50 pm | 03/20/2019 | 6:00 pm | Room 1101 | 0.5 |

## Comment:

### A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

### Log Number

Device Number

Test Exposure Duration:

Area Tested

Result

pCi/L

2455904  3136214

2455905  3136215

2455906  3136216

2455907  3136217

2455908  3136219

2455909  3136220

2455910  3136221

2455911  3136222

2455912  3136223

2455913  3136224

2455914  3136225

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

5:50 pm

5:55 pm

6:00 pm

6:00 pm

5:40 pm

5:40 pm

6:00 pm

6:05 pm

6:05 pm

6:05 pm

6:10 pm

03/20/2019  6:05 pm

03/20/2019  6:05 pm

03/20/2019  6:30 pm

03/20/2019  6:30 pm

03/20/2019  5:50 pm

03/20/2019  5:55 pm

03/20/2019  6:20 pm

03/20/2019  6:35 pm

03/20/2019  6:35 pm

03/20/2019  6:35 pm

03/20/2019  6:35 pm

Room 1101A Room 1101A Room 1102 Nurse Room 1102A

QA-19

QA-20 QA-21

Room 1202

Room 1203A Nurse Conference Room 1202A Nurse Exam Room 1201

< 0.4

< 0.4

< 0.4

< 0.4

0.6

0.4

< 0.4

0.5

0.6

0.4

0.6

Comment:

A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

| Log Number | Device Number | Result Test Exposure Duration: Area Tested pCi/L |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2455915 | 3136226 | 03/18/2019 | 6:10 pm | 03/20/2019 | 6:40 pm | Room HS Main Office | 0.6 |
| 2455916 | 3136227 | 03/18/2019 | 6:10 pm | 03/20/2019 | 6:40 pm | Room 1200B | 0.8 |
| 2455917 | 3136228 | 03/18/2019 | 6:10 pm | 03/20/2019 | 6:40 pm | Room 1200E | 0.9 |
| 2455918 | 3136229 | 03/18/2019 | 6:15 pm | 03/20/2019 | 6:40 pm | Room 1200C | 0.5 |
| 2455919 | 3136230 | 03/18/2019 | 6:15 pm | 03/20/2019 | 6:40 pm | Room 1200D | 0.4 |
| 2455920 | 3136231 | 03/18/2019 | 6:15 pm | 03/20/2019 | 6:40 pm | Room 1203G | 0.5 |
| 2455921 | 3136232 | 03/18/2019 | 6:15 pm | 03/20/2019 | 6:45 pm | Room 1203F | 0.4 |
| 2455922 | 3136233 | 03/18/2019 | 6:15 pm | 03/20/2019 | 6:45 pm | Room 1200F | 0.6 |
| 2455923 | 3136234 | 03/18/2019 | 6:20 pm | 03/20/2019 | 6:45 pm | Room 1200G | 0.9 |
| 2455924 | 3136235 | 03/18/2019 | 6:20 pm | 03/20/2019 | 6:45 pm | Room 1203E | 0.6 |
| 2455925 | 3136236 | 03/18/2019 | 6:20 pm | 03/20/2019 | 6:45 pm | Room 1203D | 0.6 |

## Comment:

### A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

| Log Number | Device Number | Result Test Exposure Duration: Area Tested pCi/L |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2455926 | 3136237 | 03/18/2019 | 6:20 pm | 03/20/2019 | 6:45 pm | Room 1203C | 0.6 |
| 2455927 | 3136238 | 03/18/2019 | 6:25 pm | 03/20/2019 | 6:45 pm | Room 1203B | 0.7 |
| 2455928 | 3136239 | 03/18/2019 | 6:10 pm | 03/20/2019 | 6:35 pm | QA-22 | 0.5 |
| 2455929 | 3136240 | 03/18/2019 | 6:10 pm | 03/20/2019 | 6:40 pm | QA-23 | 0.6 |
| 2455930 | 3136241 | 03/18/2019 | 6:25 pm | 03/20/2019 | 6:45 pm | QA-24 | < 0.4 |
| 2455931 | 3136242 | 03/18/2019 | 6:25 pm | 03/20/2019 | 6:50 pm | Room 1203 | 0.7 |
| 2455932 | 3136243 | 03/18/2019 | 6:30 pm | 03/20/2019 | 6:50 pm | Room Student Dining 1204A | < 0.4 |
| 2455933 | 3136244 | 03/18/2019 | 6:30 pm | 03/20/2019 | 6:50 pm | Room Student Dining 2 1204A | 0.4 |
| 2455934 | 3136245 | 03/18/2019 | 6:35 pm | 03/20/2019 | 6:55 pm | Room 1205 | 0.8 |
| 2455935 | 3136246 | 03/18/2019 | 6:35 pm | 03/20/2019 | 6:55 pm | Room 1205A | 1.0 |
| 2455936 | 3136247 | 03/18/2019 | 6:40 pm | 03/20/2019 | 6:55 pm | Room 1207 | 0.7 |

## Comment:

### A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

| Log Number | Device Number | Result Test Exposure Duration: Area Tested pCi/L |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2455937 | 3136248 | 03/18/2019 | 6:40 pm | 03/20/2019 | 6:55 pm | Room IDF HS | 0.6 |
| 2455938 | 3136249 | 03/18/2019 | 6:40 pm | 03/20/2019 | 6:55 pm | Room Custodial | 1.0 |
| 2455939 | 3136250 | 03/18/2019 | 6:40 pm | 03/20/2019 | 7:00 pm | Room E-5 | 1.4 |
| 2455940 | 3136251 | 03/18/2019 | 6:45 pm | 03/20/2019 | 7:00 pm | Room 1214 | 0.4 |
| 2455941 | 3136252 | 03/18/2019 | 6:45 pm | 03/20/2019 | 7:00 pm | Room 1216 | < 0.4 |
| 2455942 | 3136254 | 03/18/2019 | 6:50 pm | 03/20/2019 | 7:00 pm | Room 1218 | 0.6 |
| 2455943 | 3136255 | 03/18/2019 | 6:50 pm | 03/20/2019 | 7:05 pm | Room 1217 | 1.6 |
| 2455944 | 3136256 | 03/18/2019 | 6:50 pm | 03/20/2019 | 7:05 pm | Room 1215 | 0.5 |
| 2455945 | 3136257 | 03/18/2019 | 6:55 pm | 03/20/2019 | 7:05 pm | Room 1213 | 0.4 |
| 2455946 | 3136258 | 03/18/2019 | 6:55 pm | 03/20/2019 | 7:10 pm | Room 1212 | 0.7 |
| 2455947 | 3136259 | 03/18/2019 | 7:00 pm | 03/20/2019 | 7:10 pm | Room 1212A | 0.7 |

## Comment:

### A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

| Log Number | Device Number | Result Test Exposure Duration: Area Tested pCi/L |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2455948 | 3136260 | 03/18/2019 | 6:25 pm | 03/20/2019 | 6:50 pm | QA-25 | 0.5 |
| 2455949 | 3136261 | 03/18/2019 | 6:35 pm | 03/20/2019 | 6:55 pm | QA-26 | 0.6 |
| 2455950 | 3136262 | 03/18/2019 | 7:00 pm | 03/20/2019 | 7:10 pm | QA-27 | < 0.4 |
| 2455951 | 3136263 | 03/18/2019 | 7:05 pm | 03/20/2019 | 7:10 pm | Room 1212B | 0.7 |
| 2455952 | 3136264 | 03/18/2019 | 7:05 pm | 03/20/2019 | 7:15 pm | Room 1212C | 1.0 |
| 2455953 | 3136265 | 03/18/2019 | 7:05 pm | 03/20/2019 | 7:15 pm | Room 1210 | 0.4 |
| 2455954 | 3136266 | 03/18/2019 | 7:10 pm | 03/20/2019 | 7:15 pm | Room 1221A | 0.7 |
| 2455955 | 3136267 | 03/18/2019 | 7:15 pm | 03/20/2019 | 7:20 pm | Room 1221 | 0.7 |
| 2455956 | 3136268 | 03/18/2019 | 7:15 pm | 03/20/2019 | 7:20 pm | Room 1223 | 0.5 |
| 2455957 | 3136269 | 03/18/2019 | 7:20 pm | 03/20/2019 | 7:35 pm | Room 1225 | 0.5 |
| 2455958 | 3136270 | 03/18/2019 | 7:20 pm | 03/20/2019 | 7:35 pm | Room 1227B | 0.4 |

## Comment:

### A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

| Log Number | Device Number | Result Test Exposure Duration: Area Tested pCi/L |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2455959 | 3136271 | 03/18/2019 | 7:20 pm | 03/20/2019 | 7:35 pm | Room 1227D | < 0.4 |
| 2455960 | 3136272 | 03/18/2019 | 7:20 pm | 03/20/2019 | 7:40 pm | Room 1227C | < 0.4 |
| 2455961 | 3136273 | 03/18/2019 | 7:25 pm | 03/20/2019 | 7:40 pm | Room 1227A | 0.6 |
| 2455962 | 3136274 | 03/18/2019 | 7:25 pm | 03/20/2019 | 7:40 pm | Room 1226 | 0.4 |
| 2455963 | 3136275 | 03/18/2019 | 7:25 pm | 03/20/2019 | 7:40 pm | Room 1224 | 0.5 |
| 2455964 | 3136276 | 03/18/2019 | 7:30 pm | 03/20/2019 | 7:40 pm | Room 1222 | 0.6 |
| 2455965 | 3136277 | 03/18/2019 | 7:30 pm | 03/20/2019 | 7:40 pm | Room 1220 | 0.5 |
| 2455966 | 3136278 | 03/18/2019 | 7:35 pm | 03/20/2019 | 7:45 pm | Room 1209 | 1.6 |
| 2455967 | 3136279 | 03/18/2019 | 7:35 pm | 03/20/2019 | 7:45 pm | Room 1208 | 1.0 |
| 2455968 | 3136280 | 03/18/2019 | 7:05 pm | 03/20/2019 | 7:10 pm | QA-28 | 0.7 |
| 2455969 | 3136281 | 03/18/2019 | 7:05 pm | 03/20/2019 | 7:15 pm | QA-29 | 1.0 |

## Comment:

### A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

### Log Number

Device Number

Test Exposure Duration:

Area Tested

Result

pCi/L

2455970  3136282

2455971  3136283

2455972  3136284

2455973  3136285

2455974  3136286

2455975  3136287

2455976  3136289

2455977  3136290

2455978  3136291

2455979  3136292

2455980  3136293

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

7:30 pm

7:40 pm

7:40 pm

7:45 pm

7:45 pm

7:50 pm

7:50 pm

7:50 pm

7:55 pm

7:55 pm

7:55 pm

03/20/2019  7:45 pm

03/20/2019  7:45 pm

03/20/2019  7:50 pm

03/20/2019  7:50 pm

03/20/2019  7:50 pm

03/20/2019  8:00 pm

03/20/2019  8:00 pm

03/20/2019  8:00 pm

03/20/2019  8:05 pm

03/20/2019  8:05 pm

03/20/2019  8:05 pm

QA-30

Room 1206A Room 1206 Room 1204B Room 1204

Room 2202 Room 2204A Room 2205 Room 2204B Room 2212

Room 2215

< 0.4

0.8

0.4

0.5

< 0.4

< 0.4

< 0.4

< 0.4

< 0.4

< 0.4

< 0.4

Comment:

A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.

NELAC NY 11769

NRPP 103216 AL NRSB ARL0017

# Laboratory Report for:	Property Tested: Peter Schafer, Superintendent

EPA Method #402-R-92-004

Liquid Scintillation NRPP Device Code 8088 NRSB Device Code 12193

# Abington Public Schools 1071 Washington Street

Abington Pre-K, Middle, High School 201 Gliniewicz Way

Abington  MA	02351	Abington MA  02351

### Log Number

Device Number

Test Exposure Duration:

Area Tested

Result

pCi/L

2455981  3136294

2455982  3136295

2455983  3136296

2455984  3136297

2455985  3228324

2455986  3228335

2455987  3228336

2455988  3136298

2455989  3136299

2455990  3136300

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

03/18/2019

8:00 pm

8:00 pm

8:05 pm

8:05 pm

8:10 pm

8:10 pm

8:15 pm

7:40 pm

7:40 pm

7:40 pm

03/20/2019  8:10 pm

03/20/2019  8:10 pm

03/20/2019  8:15 pm

03/20/2019  8:15 pm

03/20/2019  8:15 pm

03/20/2019  8:20 pm

03/20/2019  8:20 pm

03/20/2019  7:45 pm

03/20/2019  7:50 pm

03/20/2019  8:20 pm

Room 2220

Room 2103

Room 2108 Room 2108A Room 2121 Room 2121A Room 2114 QA-31

QA-32 QA-33

< 0.4

< 0.4

< 0.4

< 0.4

< 0.4

< 0.4

< 0.4

1.0

< 0.4

< 0.4

Comment:

A copy of this report was emailed to lisa.hebert@state.ma.us.

Distributed by: Dept of Public Health-Western Regional

Date Received: 03/22/2019

Date Logged:

03/22/2019

Date Analyzed: 03/23/2019

Date Reported:

03/25/2019

Disclaimer:

Report Reviewed By: _   ____   ___   ___

Report Approved By: ___   ___   ___   ____   __

Shawn Price, Director of Laboratory Operations, AccuStar Labs

The uncertainty of this radon measurement is ~+/- 10 %. Factors contributing to uncertainty include statistical variations, daily and seasonal variations in radon concentrations, sample collection techniques and operation of the dwelling. Interference with test conditions may influence the test results.

This report may only be transferred to a third party in its entirety. Analytical results relate to the samples AS RECEIVED BY THE LABORATORY. Results shown on  this report represent levels of radon gas measured between the dates shown in the room or area of the site identified above as "Property Tested". Incorrect information will affect results. The results may not be construed as either predictive or supportive of measurements conducted in any area of this structure at any other time. AccuStar Labs, its employees and agents are not responsible for the consequences of any action taken or not taken based upon the results reported or any verbal or written interpretation of the results.