## Slide 1: Article 8 permit application
Energy from Waste Facility
Alexandria / Arlington, VA
[Facility Photo]

## Slide 2: Energy-from-Waste Process
Partner with municipalities to sustainably dispose of waste
Technologically advanced facilities combust waste at high temperatures
Resulting steam used to produce electricity for sale or sold directly
Metals are retrieved from the process and recycled
500 – 750 kWh of Power
~50 lbs. of Recycled Metal
Ash: ~10% of Original Volume
One Ton of Municipal Solid Waste (MSW)

## Slide 3: Covanta Alexandria/Arlington, Inc.
 | Permit Limit/Unit | 2001 – 2017 Actual Results | % Below Limit
Particulate (mg/dscm) | 27 | 1.09/Unit (avg) | 96.0%
PM10 (filterable) (mg/dscm) | 27 | 1.55/Unit (avg) | 94.3%
Dioxin/Furan (ng/dscm) | 30 | 1.97/Unit (avg) | 93.4%
Mercury (ug/dscm) | 80 | 1.94/Unit (avg) | 97.6%
Lead (ug/dscm) | 440 | 4.09/Unit (avg) | 99.1%
Cadmium (ug/dscm) | 40 | 0.35/Unit (avg) | 99.1%
SO2 (ppm) | 29 | 1.29/Unit (avg) | 95.6%
HCL (ppm) | 29 | 1.82/Unit (avg) | 93.7%
NOx (ppm) | 205 | 172.85/Unit (avg) | 15.7%
CO (ppm) | 100 | 36.58/Unit (avg) | 63.4%
Excellent Air Emission Results (Actual Results vs. Permit Limit)

## Slide 4: Alexandria/Arlington Energy-from-Waste Facility
Began commercial operation in February 1988 and serves residents in the County of Arlington, the City of Alexandria and the surrounding metro area
Three units with nominal design of 975 tons-per-day of municipal solid waste (MSW)
Generates up to 23 megawatts of renewable energy that is sold to Dominion Power
Recovers 8,000 tons per year of ferrous metal for recycling
Best Available Control Technology (fabric filter baghouses, activated carbon injection, spray dryer absorbers, ammonia injection)

## Slide 5: Air Quality Permitting
Facility steam generation is limited by VADEQ permit to 1,170,400 tons per year (rolling 12-month basis)
  Fixed compliance formula is based on a ratio of 3.34 lbs steam per lb MSW processed
  This equates to a MSW processing limit of 350,419 tons (rolling 12-month total)
  This formula does not reflect the changing energy value of MSW
Market forces are driving higher MSW volumes
Client communities prefer Energy from Waste solutions vs landfill disposal
Facility proposes the following:
  Elimination of the outdated fixed steam-to-MSW ratio in lieu of more accurate direct steam flow measurement
  Annual steam limit to remain unchanged
  Annual MSW receipts increase by an approximate 30,000 tons

## Slide 6: Air Quality Permitting (continued)
Using direct steam measurement to demonstrate compliance with current 12-month rolling steam limit would enable facility to operate more hours per year
There would be no change in short-term (hourly/daily) MSW firing rates or actual emissions
  Facility operating permit does not limit MSW throughput on a short-term basis; the facility design basis is a nominal 975 tons-per-day (TPD)
  Average daily MSW firing rate based on 350,419 tons-per-year (TPY) is 960 TPD
  Facility currently limits annual MSW firing to stay within the 12-month rolling steam limit
  Average daily MSW firing rate based on proposed projected annual firing rate of 380,419 TPY (includes 30,000 TPY increase) is 1,042 TPD
  Daily facility MSW firing rates have eclipsed these values (based on operations since January 2015)
    960 TPD – 770 days
    975 TPD – 653 days
    1042 TPD – 131 days

## Slide 7: Air Quality Permitting (continued)
“Paper” increase in hourly PM2.5/PM10 emissions
  No current PM2.5 emission limit
  Current PM10 emission limit does not include condensables
  Projected maximum hourly emissions based on BACT-based permit limit
  Increase resulting from difference between projected maximum hourly and baseline actual emission rates
  Actual hourly PM2.5/PM10 emissions will not change as a result of the project
Nitrogen Oxides
  Facility is subject to NOx RACT (Reasonably Available Control Technology) as a Major Source in the Northern VA Ozone Non-attainment area
  Final RACT Plan submitted to VADEQ on September 2017
  Separate from this project, Covanta proposes to install Low NOx (LNTM) technology to meet lower NOx RACT limits
    Current limit – 205 ppmdv7 (24-hr avg.)
    Proposed limits – 110 ppmdv7 (24-hr avg.) and 90 ppmdv7 (annual avg.)
    Schedule – First unit in 4th quarter 2019, Second unit in 4th quarter 2020, Third unit in 4th quarter 2021*

## Slide 8: Facility Location Map

## Slide 9: Estimated Project Schedule
Permit Application Submittal [4Q18]
Draft Permit Issuance
Final Permit Issuance
Implement
Public Review/ Comment

## Slide 10
Emission Parameter | Baseline Years | Baseline Actual Emissions (TPY) | Projected Actual Emissions (TPY) | Projected Emissions Changes (TPY) | Article 8 Significance Threshold (TPY) | Significant (Y/N)**
Particulate Matter | 2010/2011 | 5.49 | 8.40 | 2.91 | 25 | N
PM-10 | 2016/2017 | 3.82 | 5.59 | 1.77 | 15 | N
PM-10* | 2011/2012 | 22.18 | 56.16 | 33.98 | 15 | Y
PM-2.5* | 2011/2012 | 21.38 | 56.16 | 34.78 | 10 | Y
SO2 | 2010/2011 | 9.00 | 12.49 | 3.49 | 40 | N
VOC | 2008/2009 | 1.80 | 2.31 | 0.51 | 25 | N
NOx | 2008/2009 | 478.09 | 457.41^ | -20.68 | 25 | N
CO | 2008/2009 | 72.59 | 89.11 | 16.52 | 100 | N
MWC Metals (CdPbHg) | 2008/2009 | 0.0385 | 0.1187 | 0.0802 | 12 | N
Lead | 2008/2009 | 0.0356 | 0.0730 | 0.0374 | 0.6 | N
MWC Acid Gases (SO2,HCl) | 2010/2011 | 13.90 | 20.96 | 7.06 | 40 | N
PCDD/PCDF | 2011/2012 | 2.89E-06 | 5.27E-06 | 2.38E-06 | 3.50E-06 | N
Fluorides (as HF) | 2008/2009 | 0.52 | 0.90 | 0.38 | 3 | N
Sulfuric Acid Mist | 2011/2012 | 0.53 | 0.99 | 0.46 | 7 | N
Greenhouse Gases | 2010/2011 | 302,022 | 338,712 | 36,710 | 75,000 | N
Emissions Applicability

## Slide 11: Class I Area Assessment
Class I Area | Distance to Facility
Shenandoah National Park (VA) | 92 km
Dolly Sods Wilderness Area (WV) | 195 km
Otter Creek Wilderness Area (WV) | 218 km
James River Face Wilderness Area (VA) | 244 km

## Slide 12: Class I Area Assessment
FLM uses “Q/D” screening for Air Quality Related Value (AQRV) analysis requirement
For modifications Q (ton/yr) is based on increase in short-term emission rates and assumed 8760 hours/year operation.
  No increase in short-term emission rates for proposed project
  Projected increase in annual actual emissions due to increased operating hours
Proposed project subject to NSR for PM10/PM2.5 only
Q/D ratio conservatively based on projected BACT-based maximum annual emission rate
  PM10/PM2.5 – 56 tons/yr
  Distance to nearest Class I Area (D) = 92 km (Shenandoah National Park)
  Q/D = 0.61
Conclusion – Q/D is << 10 and no AQRV analysis should be required project

## Slide 13: Class I & II Assessments
Class I Assessment
  Class I Air Quality modeling
    PM10 & PM2.5
  Modeling Approach
    AERMOD
    Receptors at 50 km
Class II Assessment
  Class II Air Quality modeling
    PM10 & PM2.5
  Modeling Approach
    AERMOD
    Modeling to assess impacts relative to applicable SILs, PSD Increments and NAAQS compliance
    Emission Inventory provided by VADEQ (and MDE, as required)
    Ambient background levels from VADEQ monitoring network
Class I & II modeling protocols
  Combined protocol for VADEQ approval

## Slide 14: BACT Analysis
Best Available Control Technology (BACT) Process
  Required for Emissions Parameters that exceed Article 8 Significance Thresholds
    PM10 & PM2.5
  Identify potentially applicable control technologies
    EPA RACT/BACT/LAER Clearinghouse
    State permit databases
    Demonstrated permits approvals issued for operating Energy-from-Waste facilities
  Evaluate technical feasibility (considering facility-specific conditions)
  Rank control technologies based on effectiveness
  Evaluate options
    Considering energy/environmental/economic impacts
  Select control technology(ies) based on this analysis

## Slide 15
Thank You