8450 Cole Parkway    Shawnee, KS  66227    Phone: 913-422-0707    Fax: 913-422-0808

E-mail: onsite@biomicrobics.com    www.biomicrobics.com    800-753-FAST (3278)

FIELD INSPECTION & SERVICE REPORT

# BioBarrier® MBR Systems

| INSTALLATION | AUTHORIZED SERVICE PROVIDER |
| --- | --- |
| Installation Address | Name |
| Owner Name | Street |
| Mail Address City State Zip | Mail Address City State Zip |
| Phone Fax e-mail | Phone Fax e-mail |
| INSTALLATION INFORMATION |
| Model No. | Blower Brand and Size | Serial No. | Date of Installation | Date of last pump-out |
| COMPONENT | FUNCTION | PROCEDURE | RESULT |
| BLOWER | OPERATION | Open blower housing, check to confirm that blower is running (be sure blower is ON and shows ON in the BB panel. |  |
|  | INTAKE FILTER | Remove wing nut from intake assembly on blower, remove all debris from filter element. Put assembly back together. |  |
| CONTROL PANEL | AUDIO & VISUAL FUNCTION | Place control panel into MANUAL MODE then turn the blower OFF. See "Manual Mode" directions in service manual for proper execution of this task. |  |
| REACTION CHAMBER | BEING AERATED | Remove cover from manhole over BioBarrier system and check to be sure vigorous boiling is ocurring (unless panel indicates the system is in LTRP mode). |  |
|  | SOLIDS REMOVAL | Check Solids Removal procedure in the Service Manual. |  |

| COMPONENT | FUNCTION | PROCEDURE | RESULT |
| --- | --- | --- | --- |
| VENTS & INTAKES | CLEAR VENTS AND INTAKES ON BLOWER HOUSING | Remove any obstructions from the intake louvres on the blower housing and vents |  |
| SANITEE® EFFLUENT SCREEN | CLEAN THE SCREEN | Clean by using the built in swab feature or other method |  |
| WATER QUALITY | VIEW EFFLUENT | Visually observe final effluent of BioBarrier system. Effluent should be clear. |  |
|  | CHECK ODOR | Smell odor at BioBarrier vent, it should be a damp, earthy odor |  |
|  | COLLECT SAMPLE | Refer to the "COLLECTION OF EFFLUENT SAMPLE" section of the Service Manual |  |
| MEMBRANE CARTRIDGE CHEMICAL CLEANING | CLEAN IN PLACE | Check FILT time on control panel. If it exceeded 16:00 hrs OR the vacuum reading on the filtration pump is -7 psi (-14” Hg) or LESS, AND the system floats are operating correctly, then perform the CIP procedure according to the instructions in the Service Manual. | FILT Reading: REST Reading: |
|  | INTENSE OXIDATIVE CLEANING & CITRIC ACID CLEANING | Perform this cleaning procedure after four consecutive CIP procedures have been performed. See the Service Manual for proper procedure |  |
| OTHER SYSTEM COMPONENTS |  |  |  |
| OWNER SIGNATURE | TECHNICIAN SIGNATURE | SERVICE DATE |

Please send completed form by mail to the address above, FAX to 913-422-0808,

or e-mail to tcoulthard@biomicrobics.com