## Intro
Last edit: 6/1/2022
This spreadsheet was developed by the Massachusetts Leading by Example Program to highlight examples of buildings and campuses that have decarbonized, or have undertaken plans to decarbonize, existing buildings. These institutions were selected due to their similarities to MA campuses, particularly in size, climate, and existing energy systems.
Please contact Ryan.Kingston@mass.gov with any questions or suggestions for this document.

## Decarbonization Case Studies
Campus or Building | State | Summary | System to be Replaced / Fuels Used | New Energy System | Square Footage Affected | Year Started (if known) | Year Completed | System Capacity (Btu) | System Capacity (tons) | System Capacity (MW) | Total Project Cost | Expected Enviromental Impact | Links
West Virginia University | West Virginia | Feasibility studies completed 2017-2019 for installation of a district geothermal system. |  | Electrification: GSHP: District |  | Not yet started | [6 empty] | https://researchrepository.wvu.edu/etd/7397/ https://wvutoday.wvu.edu/stories/2017/11/06/wvu-to-study-of-possible-geothermal-use-thanks-to-doe-grant
Oberlin College | Ohio | The four-year project will convert buildings throughout Oberlin’s 440-acre campus to geothermal heating and cooling, drawing on 1,100 wells that harness the earth’s natural underground temperatures to replace Oberlin’s current heat source, natural gas. The project will also replace century-old steam pipes with an efficient, low-temperature distribution network that will save 5 million gallons of water a year and reduce operating costs by more than $1 million annually. At the same time, Oberlin’s buildings are being upgraded to accommodate the new system, conserve energy, and modernize electrical and communication technologies. | Natural gas, steam | Geothermal, low temperature hot water |  | 2021 | 2025 (estimated) |  |  |  | 140000000 |  | https://www.oberlin.edu/news/oberlin-college-and-conservatory-secures-80-million-certified-climate-bonds-sustainable https://carbonneutral.oberlin.edu/
West Chester University | Pennsylvania | Conversion to GSHP from coal plants for ~half of campus buildings (remainder use NG boilers), reducing by ~7500 tons of CO2 emission annually. | Central steam plant; burns coal | Electrification: GSHP: District | [5 empty] | 16.1 | 33000000 | -7,500 tons CO2, -70,000 tons of coal, and -200,000 gal fuel oil a year | https://www.wcupa.edu/Sustainability/initiatives.aspx https://www.energy.gov/eere/buildings/recovery-act-funded-geothermal-heat-pump-projects
Weber State | Utah | Partial/hybrid replacement of old boiler/chiller systems with geothermal system, for ~75% reduction in NG in those buildings. This will include 200+ deep-water wells in the parking lot. | Steam and chilled water | Electrification: GSHP: District |  | 2016 | [6 empty] | https://www.standard.net/news/environment/geothermal-wells-deepen-weber-state-s-sustainability-efforts/article_68aa8cb0-eb31-5c8e-ab9b-e33a227a9b1f.html
University of New Hampshire | New Hampshire | In 2005, UNH installed a $20‐million CHP plant to generate electricity for UNH’s 6‐million‐sq.‐ft. campus, and heat and cool 80 campus buildings (4 million sq. ft.). In 2009, UNH replaced the CHP’s natural gas fuel source with processed landfill gas via the $49‐million “EcoLine” project, which cleans landfill gas at the Turnkey landfill in Rochester, NH and transports processed landfill gas 12.7 miles to UNH’s CHP system. | Natural gas CHP | Alternative Fuel: Landfill Gas | 6000000 | 2009 | 2009 |  |  |  |  | 36,000 tons of CO2 reduced per year after switching to landfill gas | https://chptap.lbl.gov/profile/254/UNH-Project_Profile.pdf
University of Maine Farmington (1) | Maine | Conversion from fuel oil boiler to partial GSHP. Estimated elimination of ~800 tons CO2 and $90,000 in savings from GSHP annually. | Fuel Oil | Electrification: GSHP: District | 50000 | [5 empty] | 1550000 | - ~800 tons CO2 | http://www2.umf.maine.edu/edcenter/wp-content/uploads/sites/83/2009/08/2009_tourprotocol_new1.pdf http://www.dailybulldog.com/db/features/umfs-geothermal-systems-construction-underway/ http://www2.umf.maine.edu/sustainablecampus/buildings-and-grounds/biomass-central-heating-plant/ https://www.pressherald.com/2017/05/09/university-of-maine-at-farmington-biomass-plant-exceeds-expectations-in-first-year-of-operation/#
University of Maine Farmingon (2) | Maine | Full conversion from fuel oil to biomass heating plant for remaining buildings not on GSHP. Estimated 90% FF reduction and $900,000 in savings from biomass plant annually. | Fuel Oil | Alternative Fuel: Biomass Heating Plant | 800000 |  | 2016 |  |  |  | 11000000 | -90% in fossil fuel consumption | http://www2.umf.maine.edu/edcenter/wp-content/uploads/sites/83/2009/08/2009_tourprotocol_new1.pdf http://www2.umf.maine.edu/sustainablecampus/buildings-and-grounds/biomass-central-heating-plant/
SUNY Albany | New York | Student housing center with geothermal system, expected annual savings of $300,000. |  | New: Electrification: GSHP: Building | 200000 |  | 2012 |  | ~400 |  |  | -50% energy use (1 building) | https://www.energy.gov/articles/university-albany-students-head-back-school-powered-renewable-energy
Stanford University | California | Full replacement of CHP with grid-sourced electricity and heat recovery chiller system designed to capture waste heat from buildings. Three thermal energy storage tanks are heated and cooled during off-peak hours and provide up to a half-day's supply of heating and cooling to the campus. GHG emissions reduced by 68%, eliminating ~150,000 tons of CO2 annually, as well as estimated $420 million in energy savings over 35 years. | Gas-fired cogeneration plant | Electrification: District energy system | 12000000 |  | March 2015 | 120000000 | 7500 |  | 485000000 | - 150,000 tons CO2 | https://sustainable.stanford.edu/sites/default/files/ZGF_Stanford_CEF.pdf ; https://sustainable.stanford.edu/sites/default/files/E%26C%20Plan%202016.6.7.pdf http://eprijournal.com/electric-university/ https://news.stanford.edu/press-releases/2019/05/07/campus-energy-admized-replicated/
Smith College | Massachusetts | Campus decarbonization study completed Jan 31, 2017 recommends switching from natural gas to B100 for CHP plant in short term, switch to low temperature water heating network, add GSHP and heat recovery chillers in medium-long term, and eventually source electricity from renewables to offset increased demand of GSHP system. | Natural gas CHP | Alternative fuel: Biodiesel (B100) Electrification: GSHP, HRC, District | 2899000 | Not yet started | [6 empty] | https://www.smith.edu/sites/default/files/media/Documents/Sustainability/decarbonization_study.pdf https://www.smith.edu/about-smith/sustainable-smith/climate-leadership
Skidmore College | New York | Installation of innovative district geothermal system, currently serving ~35% of campus with plans to expand to serve 60% of the campus by 2025. |  | Electrification: GSHP: District |  |  | 2014/ ongoing | [5 empty] | https://www.skidmore.edu/sustainability/renewable-energy/geothermal.php
SC Johnson Headquarters | Wisconsin | Installing a GeoExchange system to replace boiler system on campus, for annual energy use reduction of ~42%. | boiler | Electrification: GSHP: District |  | 2019 | 2020 |  |  |  |  | Expect -42% energy use | https://www.scjohnson.com/en/press-releases/2019/april/sc-johnson-plans-shift-to-geothermal-power-at-headquarters-significantly-reducing-energy-use ; https://journaltimes.com/business/local/sc-johnson-plans-shift-to-geothermal-power-at-headquarters/article_2e2017ce-d846-5b7e-a8b3-b0295167cf0d.html
Richard Stockton College of New Jersey | New Jersey | Full replacement of old boiler/chiller systems with water-source heat pumps, reducing the school's NG consumption by ~70%. Considered a model system and continually in operation/updated | old boiler/chiller | Electrification: WSHP: District | 5100000 | 1993 | 1994 |  | 1480 |  |  | -70% natural gas reduction ; -25% electricity | https://www.achrnews.com/articles/84331-nj-college-continues-to-benefit-from-pioneering-geothermal-system
Ohio State | Ohio | OSU's climate action plan includes converting steam system to low temperature hot water, building a CHP plant that can convert to renewable natural gas or hydrogen, and procurement of renewable energy. Ohio State Energy Partners, a consortium made up of ENGIE North America and Axium Infrastructure, is required to meet the university’s goal of a 25 percent improvement in energy efficiency on the Columbus campus. |  | b |  | Not yet started | [6 empty] | https://si.osu.edu/sites/default/files/CAP_Final_04082020.pdf https://www.osu.edu/energymanagement/index.php?id=7
New School & Performing Arts Center (Philadelphia) | Pennsylvania | Installation of GSHP system. Unique as a historically valuable building. |  | Electrification: GSHP: Building | 23000 | 2010-05-01 | January 2014 |  | 206 |  | 1700000 |  | https://www.energy.gov/sites/prod/files/2014/02/f7/gshp_colman_avenue_arts.pdf
Montana Tech | Montana | Installation of GSHP (single building) using contaminated groundwater from a mine, for ~39% reduction in CO2 emissions and $17,000 in annual savings. Successful but relatively unique. |  | Electrification: GSHP: Building | 56000 |  | 2014 |  | 50 |  | 1100000 | ~39% emissions, -88% heating needs | https://mtstandard.com/news/local/mining-for-heat-not-copper-tech-project-uses-mine-water/article_0dd01fef-b661-51ad-b9ad-5a6f856a5666.html
Monroe County Community College | Michigan | Replaciement of old boiler/chiller with GSHP for 5 campus buildings, reducing by ~1000 tons of CO2 and $275,000 in savings annually. | old boiler/chiller | Electrification: GSHP: District |  |  | 2017 |  | 625 |  | 16100000 | -160,000 kWh / year ; -1000 tonnes Carbon/year | https://www.gmb.com/our-projects/geothermal-campus-conversion ; https://www.monroeccc.edu/news/2017/ribbon-cut-on-energy-efficient-and-earth-friendly-geothermal-hvac-system
Missouri University of Science & Technology | Missouri | Large-scale Installation of geothermal as hybrid with boiler system, supplying 17 buildings. Estimated reduction of 25,000 tons CO2 emissions, -50% energy use for campus, and ~$1 million in savings annually. In successful operation. | Gas boilers | Hybrid System (District GSHP and gas boiler) | 1075000 |  | 2014 | 40727000 |  |  | 54344000 | -25,000 mtco2e | http://mepassociates.com/content/markets/pdfs/4/MEP%20Campus%20Utilities_SOQ.pdf ; https://www.jedunn.com/project/missouri-university-science-technology-geothermal-energy-system
Middlebury College | Vermont | Middlebury will shift to using renewable natural gas and eliminate the use of natural gas, a fossil fuel, as a supplemental energy source for its on-campus biomass-gasification plant. That plant already meets most of the campus’s heating and cooling needs and cogenerates 15–20 percent of Middlebury’s electricity needs. | Biomass gasification plant | Renewable natural gas |  |  | Anticipated by 2028 | [5 empty] | https://www.middlebury.edu/office/energy2028
Michigan State Capitol Building | Michigan | Full replacement of old boiler/chiller with geothermal system (single building), for ~$250,000 in annual savings. Ongoing project. | old boiler/chiller | Electrification: GSHP: Building |  | 2018 | Ongoing |  |  |  | 4000000 |  | https://michiganbattleofthebuildings.org/geothermal-energy-comes-michigans-state-capitol-building/ ; http://capitol.michigan.gov/Content/Files/Capitol/MSCC-Report-October-Issue.pdf
Miami University (Ohio) | Ohio | Partial replacement of old coal fired steam plant with geothermal heating/cooling, with plans for expansion. Current carbon emissions reduction by 45% and total energy use by 39%. | old coal-fired steam plant | Electrification: GSHP: District | 748318 | 2011 | 2017 | 49355000 | 2350 |  | 15000000 | 45% CO2 reduction, -39% decrease in total energy use | https://www.wlwt.com/article/miami-university-turning-to-geothermal-energy-at-oxford-campus/3535752 ; https://miamioh.edu/news/top-stories/2019/11/converting-campus-off-steam-by-2026.html ; http://mepassociates.com/content/markets/pdfs/4/MEP%20Campus%20Utilities_SOQ.pdf
Indiana Institute of Technology | Indiana | Conversion to GSHP from gas fired boiler for multiple campus buildings, for ~57% reduction in CO2 emissions for those buildings. CO2 is used as the compressor refrigerant. | gas-fired boiler | Electrification: GSHP: District |  | 2009 | 2011 |  | 130-1440 |  | 2670000 | -57% (~242 tons) | https://openei.org/wiki/Pioneering_Heat_Pump_Project_Geothermal_Project ; http://ahattersley.com/project/indiana-tech-geothermal-project/
Illinois National Guard State HQ Building | Illinois | Replacement of boiler/chiller with geothermal retrofit (single building). Original plans to utilize mine water as a heat sink were unsuccessful, and the project plans to move forward with conventional geothermal. | boiler/chiller | Electrification: GSHP: Building | 74000 | 2010-05-01 | August 2014 |  |  |  | 1600000 | -275,600 kWh | https://www.energy.gov/sites/prod/files/2014/02/f7/gshp_lee_illinois_national_guard.pdf https://www.osti.gov/servlets/purl/1179248/
Haverhill Public Library | Massachusetts | Replacement of old boiler/chiller with geothermal system (single building), for 9 MWh reduction in energy use. Successful operation. | old boiler/chiller | Electrification: GSHP: Building | 44000 |  | 1994 |  | 107 |  | 209000 | -9 MWh | http://northeastgeo.com/haverhill-public-library-haverhill-ma/ ; https://www.geothermal-energy.org/pdf/IGAstandard/ISS/2001Romania/bloomquist_hp.pdf ; http://cloud.cdhenergy.com/presentations/Haverhill.pdf
Hamilton College | New York | Replacement of old boiler/chiller with GSHP for single dormitory building, for ~60% reduction in energy use and $11,000 in savings annually. Successful in operation and historical preservation. | old boiler/chiller | Electrification: GSHP: Building | 21000 |  | 2004 |  |  |  | 80000 | -60% energy use | https://blog.nwf.org/2008/12/ground-source-heat-from-lipscomb-to-yale/ https://www.hamilton.edu/news/story/skenandoa-house-goes-green
Furman University | South Carolina | Replacement of old HVAC with geothermal heating and chilling in student multifamily housing buildings, for a reduction in energy consumption of 32 kWh/month. | Aging heat pumps | Electrification: GSHP: District | 300000 | 2010 | August 2013 |  |  |  | 2500000 | -32% kWh/month | https://news.furman.edu/2013/01/18/north-village-geothermal-project-nearly-complete/ https://www.energy.gov/eere/buildings/recovery-act-funded-geothermal-heat-pump-projects http://www2.furman.edu/sites/sustainability/WhatWeAreDoing/Pages/Energy.aspx
Eastern Washington University | Washington | Plans for a Zero Net Energy building using district energy system including combination of electric boiler, air-to-water heat pump, thermal storage, heat recovery chiller, waterside economizer, and water-cooled chiller |  | New: Electrification: District energy system | 150000 |  | Under construction | [5 empty] | W:\LBE\Colleges and Universities\Campus Energy Planning and Technologies\Eastern Washington University https://www.ewu.edu/stories/ewu-joins-partners-in-celebrating-topping-out-of-catalyst-building/ https://news.wsu.edu/2019/11/13/making-energy-efficient-buildings-healthy-people/ https://register.gotowebinar.com/recording/5061670349985081100
Loyola Chicago | Illinois | Moved away from a central steam plant to 5 low temp boiler loops. Still have a central chiller loop. Have added geothermal for 220,000 sf. but limited land and regulatory issues with lake access (primary campus on Lake Michigan) keep us from larger geothermal addition. | Steam and chilled water | Low temp boiler loops (5), central chiller loop, small geothermal | [8 empty] | https://elaraeng.com/wp-content/uploads/2018/05/Elara-Project-LUC-Steam-Plant.pdf https://www.elaraeng.com/wp-content/uploads/2017/04/Elara-Project-LUC-Institute-of-Env-1.pdf https://www.scb.com/project/institute-of-environmental-sustainability/
Dartmouth College | New Hampshire | Plan to build a biomass heating plant to replace a No 6. Fuel Oil heating plant, for an estimated 50% reduction in carbon emissions. However, reconsidering due to concerns from scientists about using biomass | No.6 Fuel Oil heating plant | Alternative Fuel: Biomass Heating Plant |  | Stalled--planned to begin 2020 but now reconsidering | [5 empty] | 50% | https://www.thedartmouth.com/article/2019/10/college-reconsiders-biomass-plant-proceeds-work-on-heating-system https://ramboll.com/projects/usa/dartmouth-campus-heat-distribution-system
Cornell University | New York | Cornell faculty and staff conducting study exploring ways to optimize and improve the economics of the geothermal system. This exploration may suggest ways in which the capital investment in deep geothermal may be shared by its beneficiaries. Cornell pursued a similarly ambitious project with its Lake Source Cooling system, which in July 2000 became one of the most significant energy initiatives to promote sustainability undertaken by an American university. The project established a system that pumps cold lake water through a heat exchanger to cool water circulated throughout campus. As a result, Cornell has seen an 86 percent reduction in energy use for campus cooling. |  | Electrification: GSHP: District | [8 empty] | https://research.cornell.edu/research/geothermal-energy-cornells-ithaca-campus http://deepgeothermalheat.engineering.cornell.edu/ https://news.cornell.edu/stories/2016/09/geothermal-project-could-warm-campus-expand-energy-study
City of Eagan MN Ice Arena | Minnesota | Replacement of fossil fuel CHP with central GSHP for single ice rink, for estimated CO2 reduction of 795 tons annually. Appears to be successful in operation. | Fossil fuel CHP | Electrification: GSHP: Building |  | 2010-02-01 | July 2010 |  | 240 |  | 2676000 | ~795 tons CO2, -64% energy consumption | https://www.energy.gov/sites/prod/files/2014/02/f7/gshp_lutz_eagan_ice_arena.pdf https://www.osti.gov/servlets/purl/1043168/
Chesapeake College | Maryland | Installation of geothermal systems for 6 campus buildings, in comination with energy efficiency retrofits and solar + storage for total annual savings of $250,000. |  | Electrification: GSHP: Building | 236000 |  | 2002-2015 | [5 empty] | https://www.montgomerycollege.edu/_documents/offices/facilities/md-cc-fpc/fmps/chesapeake-fmp-2016.pdf https://www.energy.gov/eere/articles/energy-department-recognizes-better-buildings-partner-chesapeake-college-energy
Carleton College | Minnesota | Full replacement of 100-year old CHP with geothermal system, replacing steam distribution system with hot water. Combined Utility Master Plan estimates 35% reduction in GHG emissions. | Central steam plant | Electrification: GSHP: District | 1800000 | 2016 | Planned 2021 | 9600000 |  |  | 38000000 | -3,600 tons CO2 | https://apps.carleton.edu/geothermal/ https://www.carleton.edu/community/news/geothermal-energy-system-a-hot-topic-at-carleton/
Blaine County School District | Idaho | Replacement of natural gas boilers with GSHP for schools in the district and retrofit HVAC systems with higher efficiency systems. Estimated 50% reduction in carbon emissions. | Natural gas boilers | Electrification: GSHP: District |  | 2010-03-01 | May 2011 |  | 275 |  | 15585773 | 50% | https://openei.org/wiki/District_Wide_Geothermal_Heating_Conversion_Blaine_County_School_District_Geothermal_Project https://geothermal.org/PDFs/Final_Idaho.pdf https://www.osti.gov/servlets/purl/1119877
Ball State University | Indiana | Full conversion to GSHP replacing four coal plants, provding heading and cooling nearly 50 buildings and spanning more than 600 acres, making this America's largest ground-source district geothermal heating and cooling system. Reduced GHG emissions by almost half, eliminating ~75,000 tons of CO2 annually, alongside ~$2 million in annual savings. | Coal boilers | Electrification: GSHP: District | 5600000 | 2009 | 2014 | 152000000 |  |  | 83000000 | -75,000 tons CO2 | http://mepassociates.com/content/markets/pdfs/4/MEP%20Campus%20Utilities_SOQ.pdf https://www.districtenergy.org/HigherLogic/System/DownloadDocumentFile.ashx?DocumentFileKey=b0f3ed01-7c78-e7bd-df18-f5a9213efec9&forceDialog=0 http://mepassociates.com/projects/2/ball-state-university https://www.energy.gov/articles/ball-state-building-massive-geothermal-system
Swarthmore College | Pennsylvania | Central steam loop powered by natural gas, #2 oil for backup. Some standalone buildings with natural gas systems. Two buildings use GSHP and solar thermal water. Some buildings have ASHP. One building has a solar hot water loop that is being expanded. The new system will transition the campus from steam to low temperature hot water. After deep energy retrofits, 100% of heating and cooling needs will be met without onsite combustion of fossil fuels. | Central steam plant | Electrification: GSHP: District |  | 2020 | Under construction; 2035 |  |  |  | 69000000 | 98% of emissions | https://www.swarthmore.edu/sustainability/decarbonizing-swarthmores-energy-systems
Note on J23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 130 tons phase 1, 440 tons phase 2
Note on A27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not MA climate
Note on A28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New construction
Note on A33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not MA climate
Note on F34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2,000,000 sq ft building/conditioned space, but only 1.8M sf on district system