# Background/Introduction

At the request of the Barnstable Public Schools (BPS), the Massachusetts Department of Public Health (MDPH), Bureau of Environmental Health (BEH) provided assistance and consultation regarding indoor air quality (IAQ) at the Centerville Elementary School (CES) located at 658 Bay Lane, Centerville, Massachusetts.  On March 1, 2013, Cory Holmes, Environmental Analyst/Regional Inspector in BEH’s IAQ Program visited the school to perform an assessment.  The assessment was part of an on-going effort to monitor and improve IAQ conditions in each of the Barnstable Public schools.

The CES is a one-story brick building that was built the 1950s; a two-story addition was constructed in the 1970s.  The building contains general classrooms, library, kitchen, cafeteria, gymnasium, faculty workrooms/lounge and office space.  Windows are openable throughout the building.

# Methods

Air tests for carbon monoxide, carbon dioxide, temperature and relative humidity were conducted with the TSI, Q-Trak, IAQ Monitor, Model 7565.  Air tests for airborne particle matter with a diameter less than 2.5 micrometers were taken with the TSI, DUSTTRAK™ Aerosol Monitor Model 8520.  BEH/IAQ staff also performed visual inspection of building materials for water damage and/or microbial growth.

# Results

The school houses approximately 380 students in grades pre-K through 3 with a staff of approximately 45.  Tests were taken during normal operations at the school.  Results appear in Table 1.

# Discussion

## Ventilation

It can be seen from Table 1 that carbon dioxide levels were below 800 parts per million (ppm) in 17 out of 19 areas, indicating adequate air exchange in the large majority of areas surveyed during the assessment.  Fresh air in classrooms is supplied by unit ventilators (univents) (Pictures 1 and 2).  A univent is designed to draw air from outdoors through a fresh air intake located on the exterior wall of the building (Picture 3).  Return air is drawn through an air intake located at the base of each unit where fresh and return air are mixed, filtered, heated or cooled and provided to classrooms through an air diffuser located in the top of the unit (Figure 1).

Univents have fan settings of “low”, “med” and “high” (or just “low” and “high” in the 1970s wing) (Pictures 4 and 5).  Univents were found deactivated or obstructed with classroom items in several areas (Pictures 4 and 6; Table 1).  In order for univents to provide fresh air as designed, intakes/returns must remain free of obstructions.  Importantly, these units must remain on and be allowed to operate while rooms are occupied.

The type of filter medium used by the school comes in a bulk roll and must be cut to size before it is inserted into a metal lattice “cage” (Pictures 7 and 8).  This method is extremely time intensive, and the results are variable.  If the filter medium is not properly fitted, gaps can allow unfiltered air into the room and/or reduce the useful life of the unit.  Disposable filters with an appropriate dust spot efficiency and similar cost can be installed in univents.  The dust spot efficiency is the ability of a filter to remove particulates of a certain diameter from air passing through the filter.  Filters that have been determined by ASHRAE to meet its standard for a dust spot efficiency of a minimum of 40 percent would be sufficient to reduce many airborne particulates (Thornburg, D., 2000; MEHRC, 1997; ASHRAE, 1992).  Pleated filters with a Minimum Efficiency Reporting Value dust-spot efficiency of 9 or higher are recommended.  Note that increasing filtration can reduce airflow (called pressure drop), which can subsequently reduce the efficiency of the unit due to increased resistance.  Prior to any increase of filtration, each AHU should be evaluated by a ventilation engineer to ascertain whether it can maintain function with more efficient filters.  In addition, the metal univent filter racks examined were found to be corroded and disintegrating, which compromises their ability to function (Pictures 8 through 10).

Note that the univents are original equipment, more than 30-50 years old.  Function of equipment of this age is difficult to maintain, since compatible replacement parts are often unavailable.  According to the American Society of Heating, Refrigeration and Air-Conditioning Engineers (ASHRAE), the service life for a unit heater, hot water or steam is 20 years, assuming routine maintenance of the equipment (ASHRAE, 1991).  Despite attempts to maintain the univents, the operational lifespan of the equipment has been exceeded.  Maintaining the balance of fresh air to exhaust air will become more difficult as the equipment ages and as replacement parts become increasingly difficult to obtain.

Mechanical ventilation in the gym is provided by an AHU located in the stage area (Picture 11).  BEH/IAQ staff examined the unit and it appeared that the air intake louver actuator was disconnected (Picture 12).  During an exterior examination of the building it appeared that the fresh air intake for the gymnasium AHU was sealed (Picture 13), thereby prohibiting the introduction of fresh air.

Exhaust ventilation in classrooms of the 1950s wing is provided by wall-mounted vents ducted to rooftop motors.  It is important to note that exhaust vents are located near hallway doors, which are generally left open (Picture 14).  However, with the hallway doors open, the exhaust vent will tend to draw air from the hallway into the classroom, instead of drawing stale air from the classroom.  Therefore it is recommended that classroom doors remain shut while exhaust vents are operating to function as designed.

Exhaust ventilation in the 1970s wing is provided by vents located in the ceilings of coat closets (Picture 15) powered by rooftop motors.  Air is drawn into the coat closet from the classroom via undercut closet doors (Picture 16).  However, the design of the closet vents allows them to be easily blocked by stored materials.  As with univents, in order to function properly, exhaust vents must be activated and remain free of obstructions.

To maximize air exchange, the MDPH recommends that both supply and exhaust ventilation operate continuously during periods of occupancy.  In order to have proper ventilation with a mechanical supply and exhaust system, the systems must be balanced to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room.  It is recommended that heating, ventilating and air conditioning (HVAC) systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).  The date of the last balancing of these systems was not available at the time of the assessment.

Minimum design ventilation rates are mandated by the Massachusetts State Building Code (MSBC).  Until 2011, the minimum ventilation rate in Massachusetts was higher for both occupied office spaces and general classrooms, with similar requirements for other occupied spaces (BOCA, 1993).  The current version of the MSBC, promulgated in 2011 by the State Board of Building Regulations and Standards (SBBRS), adopted the 2009 International Mechanical Code (IMC) to set minimum ventilation rates.  Please note that the MSBC is a minimum standard that is not health-based.  At lower rates of cubic feet per minute (cfm) per occupant of fresh air, carbon dioxide levels would be expected to rise significantly.  A ventilation rate of 20 cfm per occupant of fresh air provides optimal air exchange resulting in carbon dioxide levels at or below 800 ppm in the indoor environment in each area measured.  MDPH recommends that carbon dioxide levels be maintained at 800 ppm or below.  This is because most environmental and occupational health scientists involved with research on IAQ and health effects have documented significant increases in indoor air quality complaints and/or health effects when carbon dioxide levels rise above the MDPH guidelines of 800 ppm for schools, office buildings and other occupied spaces (Sundell et al., 2011).  The ventilation must be on at all times that the room is occupied.  Providing adequate fresh air ventilation with open windows and maintaining the temperature in the comfort range during the cold weather season is impractical.  Mechanical ventilation is usually required to provide adequate fresh air ventilation.

Carbon dioxide is not a problem in and of itself.  It is used as an indicator of the adequacy of the fresh air ventilation.  As carbon dioxide levels rise, it indicates that the ventilating system is malfunctioning or the design occupancy of the room is being exceeded.  When this happens, a buildup of common indoor air pollutants can occur, leading to discomfort or health complaints.  The Occupational Safety and Health Administration (OSHA) standard for carbon dioxide is 5,000 parts per million parts of air (ppm).  Workers may be exposed to this level for 40 hours/week, based on a time-weighted average (OSHA, 1997).

The MDPH uses a guideline of 800 ppm for publicly occupied buildings.  A guideline of 600 ppm or less is preferred in schools due to the fact that the majority of occupants are young and considered to be a more sensitive population in the evaluation of environmental health status.  Inadequate ventilation and/or elevated temperatures are major causes of complaints such as respiratory, eye, nose and throat irritation, lethargy and headaches.  For more information concerning carbon dioxide, consult Appendix A.

Indoor temperature measurements ranged from 63 (F to 76 (F (Table 1), which were within the MDPH recommended comfort range on the day of the assessment, with the exception of the gym.  The MDPH recommends that indoor air temperatures be maintained in a range of 70 (F to 78 (F in order to provide for the comfort of building occupants.  In many cases concerning indoor air quality, fluctuations of temperature in occupied spaces are typically experienced, even in a building with an adequate fresh air supply.

The relative humidity measured in the building ranged from 23 to 36 percent, which was below the MDPH recommended comfort range in all areas surveyed during the assessment (Table 1).  The MDPH recommends a comfort range of 40 to 60 percent for indoor air relative humidity.  Relative humidity levels in the building would be expected to drop during the winter months due to heating.  The sensation of dryness and irritation is common in a low relative humidity environment.  Low relative humidity is a very common problem during the heating season in the northeast part of the United States.

## Microbial/Moisture Concerns

Water-damaged ceiling tiles and wood above windows in classrooms were observed in a few areas (Table 1), which appear to be from current/historic roof/window leaks, plumbing leaks or other source of water infiltration (Pictures 17 and 18).  Water-damaged ceiling tiles can provide a source of mold and should be replaced after a water leak is discovered and repaired.  During the assessment, an active leak was reported in the Guidance office by school maintenance staff.

Like many public buildings on Cape Cod, the CES has issues with elevated relative humidity and chronic dampness during summer months.  This condition was most apparent along the northwest side of the building (Picture 19), where it has resulted in severe oxidation of metal univent and heating/building components on the inside of the building (Pictures 20 and 21), and staining and moss growth on the exterior.  Aside from aesthetic issues, the conditions of severe oxidation make cleaning difficult and can reduce operational lifespan of equipment as well as providing a source of debris/particulate material.

The US Environmental Protection Agency (US EPA) and the American Conference of Governmental Industrial Hygienists (ACGIH) recommend that porous materials (e.g., carpeting, gypsum wallboard) be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2001; ACGIH, 1989).  If not dried within this time frame, mold growth may occur.  Once mold has colonized porous materials, they are difficult to clean and should be removed/discarded.

Visible mold growth was observed on the gaskets of the refrigerator and freezer in the teacher’s lounge (Pictures 22 and 23) the gaskets are composed of non-porous material that should be cleaned and disinfected using an appropriate antimicrobial.

Plants were noted in a few classrooms (Table 1).  Plants can be a source of pollen and mold which can be respiratory irritants to some individuals.  Plants should be properly maintained and equipped with drip pans and should be located away from univents to prevent the aerosolization of dirt, pollen and mold.

BEH/IAQ staff examined the exterior of the building to identify breaches in the building envelope and/or other issues that could provide a source of water penetration.  Several potential sources were identified:

- The exterior door to the gym had damaged/missing weather-stripping, and light could be seen penetrating through the spaces underneath the door (Pictures 24 and 25).  Spaces around exterior doors can serve as sources of drafts and/or water penetration into the building, causing water damage and potentially leading to mold growth.  In addition, these spaces can serve as pathways for insects, rodents and other pests into the building.

- Plants and shrubbery were observed growing in close proximity to the foundation and univent air intakes (Picture 26), which can draw in moisture and pollen.  Shrubbery/plants in close proximity to the building envelope can cause water damage to the foundation and exterior.  Water can eventually penetrate the cracks and breaches subsequently freezing and thawing during the winter.  This freezing/thawing action can weaken masonry and other building materials, resulting in damage;

- Accumulated leaves and debris against foundation (Pictures 27);

- Missing/damaged gutters and downspouts (Pictures 27 through 31);

- Open holes/breaches in the building’s exterior (Picture 32); and

- Rotted/damaged wooden trim along roof’s edge (Pictures 33 and 34);

These conditions can undermine the integrity of the building envelope and provide a means of water entry by capillary action into the building through exterior walls, foundation concrete and masonry (Lstiburek & Brennan, 2001).  In addition, these breaches in exterior areas can provide a means of drafts and pest entry into the building.

## Other IAQ Evaluations

Indoor air quality can be negatively influenced by the presence of respiratory irritants, such as products of combustion.  The process of combustion produces a number of pollutants.  Common combustion emissions include carbon monoxide, carbon dioxide, water vapor and smoke (fine airborne particle material).  Of these materials, exposure to carbon monoxide and particulate matter with a diameter of 2.5 micrometers (μm) or less (PM2.5) can produce immediate, acute health effects upon exposure.  To determine whether combustion products were present in the indoor environment, BEH/IAQ staff obtained measurements for carbon monoxide and PM2.5.

### Carbon Monoxide

Carbon monoxide is a by-product of incomplete combustion of organic matter (e.g., gasoline, wood and tobacco).  Exposure to carbon monoxide can produce immediate and acute health effects.  Several air quality standards have been established to address carbon monoxide and prevent symptoms from exposure to these substances.  The MDPH established a corrective action level concerning carbon monoxide in ice skating rinks that use fossil-fueled ice resurfacing equipment.  If an operator of an indoor ice rink measures a carbon monoxide level over 30 ppm, taken 20 minutes after resurfacing within a rink, that operator must take actions to reduce carbon monoxide levels (MDPH, 1997).

The American Society of Heating Refrigeration and Air-Conditioning Engineers (ASHRAE) has adopted the National Ambient Air Quality Standards (NAAQS) as one set of criteria for assessing indoor air quality and monitoring of fresh air introduced by HVAC systems (ASHRAE, 1989).  The NAAQS are standards established by the US EPA to protect the public health from six criteria pollutants, including carbon monoxide and particulate matter (US EPA, 2006).  As recommended by ASHRAE, pollutant levels of fresh air introduced to a building should not exceed the NAAQS levels (ASHRAE, 1989).  The NAAQS were adopted by reference in the Building Officials & Code Administrators (BOCA) National Mechanical Code of 1993 (BOCA, 1993), which is now an HVAC standard included in the Massachusetts State Building Code (SBBRS, 2011).  According to the NAAQS, carbon monoxide levels in outdoor air should not exceed 9 ppm in an eight-hour average (US EPA, 2006).

Carbon monoxide should not be present in a typical, indoor environment.  If it is present, indoor carbon monoxide levels should be less than or equal to outdoor levels.  On the day of the assessment, outdoor carbon monoxide concentrations were non-detect (ND) (Table 1).  No measurable levels of carbon monoxide were detected inside the building (Table 1).

### Particulate Matter

The US EPA has established NAAQS limits for exposure to particulate matter.  Particulate matter includes airborne solids that can be irritating to the eyes, nose and throat.  The NAAQS originally established exposure limits to PM with a diameter of 10 μm or less (PM10).  In 1997, US EPA established a more protective standard for fine airborne particulate matter with a diameter of 2.5 μm or less (PM2.5).  This more stringent PM2.5 standard requires outdoor air particle levels be maintained below 35 μg/m3 over a 24-hour average (US EPA, 2006).  Although both the ASHRAE standard and BOCA Code adopted the PM10 standard for evaluating air quality, MDPH uses the more protective PM2.5 standard for evaluating airborne PM concentrations in the indoor environment.

Outdoor PM2.5 concentrations were measured at 12 μg/m3 (Table 1).  PM2.5 levels measured in the school were between 5 to 11 μg/m3 (Table 1), which were below the NAAQS PM2.5 level of 35 μg/m3.  Frequently, indoor air levels of particulates (including PM2.5) can be at higher levels than those measured outdoors.  A number of activities that occur indoors and/or mechanical devices can generate particulate during normal operations.  Sources of indoor airborne particulates may include but are not limited to particles generated during the operation of fan belts in the HVAC system, use of stoves and/or microwave ovens in kitchen areas; use of photocopiers, fax machines and computer printing devices; operation of an ordinary vacuum cleaner and heavy foot traffic indoors.

### Volatile Organic Compounds

Indoor air concentrations can be greatly impacted by the use of products containing volatile organic compounds (VOCs).  VOCs are carbon-containing substances that have the ability to evaporate at room temperature.  Frequently, exposure to low levels of total VOCs (TVOCs) may produce eye, nose, throat and/or respiratory irritation in some sensitive individuals.  For example, chemicals evaporating from a paint can stored at room temperature would most likely contain VOCs.  In an effort to identify materials that can potentially increase indoor VOC concentrations, BEH/IAQ staff examined rooms for products containing these respiratory irritants.

Classrooms contained dry erase boards and related materials.  Materials such as dry erase markers and dry erase board cleaners may contain VOCs, such as methyl isobutyl ketone, n-butyl acetate and butyl-cellusolve (Sanford, 1999), which can be irritating to the eyes, nose and throat.

## Other Conditions

Other conditions that can affect IAQ were observed during the assessment.  In many classrooms, large numbers of items were on floors, windowsills, tabletops, counters, bookcases and desks, which provide a source for dusts to accumulate.  These items (e.g., papers, folders, boxes) make it difficult for custodial staff to clean.  Items should be relocated and/or be cleaned periodically to avoid excessive dust build up.  In addition, dust and debris can accumulate on flat surfaces (e.g., desktops, shelving and carpets) in occupied areas and subsequently be re-aerosolized causing further irritation.

A box filled with used cans was observed in the teacher’s lunchroom (Picture 35).  Food/beverage containers, even when emptied/cleaned, can contain residues that can cause odors or be attractive to pests.

Finally, fluorescent light fixtures were missing covers in a number of areas (Picture 36).  Fixtures should be equipped with access covers installed with bulbs fully secured in their sockets.  Breakage of glass can cause injuries and may release mercury and/or other hazardous compounds.

# Conclusions/Recommendations

Some of the conditions listed in this report can be remedied by the actions of building occupants.  Other remediation efforts will require alteration to the building structure and equipment.  For these reasons, a two-phase approach is recommended.  The first consists of short-term measures to improve air quality and the second consists of long-term measures that will require planning and resources to adequately address overall IAQ conditions.  In view of the findings at the time of the visit, the following recommendations are made:

## Short-Term Recommendations

Operate all ventilation systems throughout the building (e.g., gym, cafeteria, classrooms) continuously during periods of occupancy to maximize air exchange.  If increased airflow is desired, operate univents in fan “high” mode.

Contact HVAC engineering firm to restore fresh air intake for gym AHU and make repairs to actuator as needed for proper operation.

Remove all blockages/items from the surface of univent air diffusers and return vents (along front/bottom) and coat closet exhausts to ensure adequate airflow.

Ensure classroom doors are closed for proper operation of mechanical ventilation system/air exchange.

- Consider adopting a balancing schedule of every 5 years for all mechanical ventilation systems, as recommended by ventilation industrial standards (SMACNA, 1994).

- Consider replacing metal filter racks with properly fitting disposable filters with an equal or greater dust-spot efficiency to eliminate the time needed to replace filters from bulk material rolls.  Prior to any increase of filtration, each piece of air handling equipment should be evaluated by a ventilation engineer as to whether it can maintain function with more efficient filters.

- For buildings in New England, periods of low relative humidity during the winter are often unavoidable.  Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low.  To control dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended.  Avoid the use of feather dusters.  Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

During summer months, monitor conditions in classrooms to avoid elevated relative humidity (>70%) for extended periods of time, which can create conditions for condensation generation and/or mold growth.

- Continue to supplement the mechanical ventilation system, as needed, in susceptible/problem areas with portable dehumidifiers during humid months.

- Ensure that dehumidifiers are cleaned and maintained per the manufacturer’s instructions, to prevent standing water and mold growth.

- Do not open windows in classrooms if air-conditioning (where installed) and/or dehumidifiers are operating.

- Ensure roof/plumbing leaks are repaired (e.g., Guidance office) and replace any remaining water-damaged ceiling tiles.  Examine the area above these tiles for mold growth.  Disinfect areas of water leaks with an appropriate antimicrobial, as needed.

- Ensure leaks around windows are fixed and make replace/repair water-damaged wooden trim above/around windows.

- Ensure plants, trees and shrubs are located at least five feet away from exterior walls/foundation of the building, particularly those in close proximity to univent fresh air intakes.

- Make repairs to existing gutter and downspout systems; replace missing elbow extensions to drain water away from the building.

- Replace missing/damaged weather-stripping on exterior doors (e.g., gym) to prevent drafts, moisture infiltration and pest entry.  Ensure tightness of doors by monitoring for light penetration and drafts around doorframes.

- Remove rodent harborages (e.g., leaves/debris) from the exterior of the building.

- Repair/replace rotted/damaged sections of wooden exterior/trim along roof edge to prevent water/pest infiltration/damage.

- Seal spaces around open utility holes around exterior of the building.

- Clean mold from refrigerator/freezer in teacher's lounge with an appropriate antimicrobial, then rinse with clean water.  If it cannot be adequately cleaned, replace.

- Ensure indoor plants are equipped with drip pans.  Examine drip pans periodically for mold growth and disinfect with an appropriate antimicrobial, as needed.  Move plants away from the air stream of mechanical ventilation equipment.

- Store used recyclables (bottles/cans) in tightly-sealed container to prevent the attraction of insects and rodents.

- Relocate or consider reducing the amount of materials stored in classrooms to allow for more thorough cleaning of classrooms.  Clean items regularly with a wet cloth or sponge to prevent excessive dust build-up.

- Replace covers for fluorescent light fixtures.

- Consider adopting the US EPA (2000) document, “Tools for Schools”, as an instrument for maintaining a good indoor air quality environment in the building.  This document is available at: http://www.epa.gov/iaq/schools/index.html

- Refer to resource manual and other related indoor air quality documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings.  These documents are available at: http://mass.gov/dph/iaq.

## Long-Term Recommendations

- In regards to classroom univents and exhaust vents, maintaining the balance of fresh air to exhaust air will become more difficult as the equipment ages and as replacement parts become increasingly difficult to obtain.  Based on the age, physical deterioration and availability of parts, the BEH recommends that an HVAC engineering firm evaluate options to determine feasibility of repairing/replacing the equipment.

- Examine the feasibility of replacement versus cleaning/refinishing of severely oxidized metal building and heating/ventilation components in areas of chronic moisture conditions.

- Restore gutter/downspout/drainage system building-wide as was originally designed.

- Consider a long-term plan to replace windows (where needed) to prevent air/moisture infiltration.

# References

ACGIH.  1989.  Guidelines for the Assessment of Bioaerosols in the Indoor Environment.  American Conference of Governmental Industrial Hygienists, Cincinnati, OH.

ASHRAE.  1989.  Ventilation for Acceptable Indoor Air Quality.  American Society of Heating, Refrigeration and Air Conditioning Engineers.  ANSI/ASHRAE 62-1989.

ASHRAE.  1991.  ASHRAE Applications Handbook, Chapter 33 “Owning and Operating Costs”.  American Society of Heating, Refrigeration and Air Conditioning Engineers, Atlanta, GA.

ASHRAE.  1992.  Gravimetric and Dust-Spot Procedures for Testing Air-Cleaning Devices Used in General Ventilation for Removing Particulate Matter.  American Society of Heating, Refrigeration and Air Conditioning Engineers.  ANSI/ASHRAE 52.1-1992.

BOCA.  1993.  The BOCA National Mechanical Code/1993.  8th ed.  Building Officials and Code Administrators International, Inc., Country Club Hill, IL.

Lstiburek, J. & Brennan, T.  2001.  Read This Before You Design, Build or Renovate.  Building Science Corporation, Westford, MA.  U.S. Department of Housing and Urban Development, Region I, Boston, MA.

MDPH.  1997.  Requirements to Maintain Air Quality in Indoor Skating Rinks (State Sanitary Code, Chapter XI).  105 CMR 675.000.  Massachusetts Department of Public Health, Boston, MA.

MEHRC.  1997.  Indoor Air Quality for HVAC Operators & Contractors Workbook.  MidAtlantic Environmental Hygiene Resource Center, Philadelphia, PA.

OSHA.  1997.  Limits for Air Contaminants.  Occupational Safety and Health Administration.  Code of Federal Regulations.  29 C.F.R 1910.1000 Table Z-1-A.

Sanford.  1999.  Material Safety Data Sheet (MSDS No: 198-17).  Expo( Dry Erase Markers Bullet, Chisel, and Ultra Fine Tip.  Sanford Corporation.  Bellwood, IL.

SBBRS.  2011.  Mechanical Ventilation.  State Board of Building Regulations and Standards.  Code of Massachusetts Regulations, 8th edition.  780 CMR 1209.0

SMACNA.  1994.  HVAC Systems Commissioning Manual.  1st ed.  Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

Sundell, J., H. Levin, W. W. Nazaroff, W. S. Cain, W. J. Fisk, D. T. Grimsrud, F. Gyntelberg, Y. Li, A. K. Persily, A. C. Pickering, J. M. Samet, J. D. Spengler, S. T. Taylor, and C. J. Weschler.  2011.  Ventilation rates and health: multidisciplinary review of the scientific literature.  Indoor Air, Volume 21: pp 191–204.

Thornburg, D.  2000.  Filter Selection: a Standard Solution.  Engineering Systems 17:6  pp. 74-80.

US EPA.  2000.  Tools for Schools.  Office of Air and Radiation, Office of Radiation and Indoor Air, Indoor Environments Division (6609J).  EPA 402-K-95-001, Second Edition.  http://www.epa.gov/iaq/schools/tools4s2.html.

US EPA.  2001.  Mold Remediation in Schools and Commercial Buildings. US Environmental Protection Agency, Office of Air and Radiation, Indoor Environments Division, Washington, D.C.  EPA 402-K-01-001.  March 2001.

US EPA.  2006.  National Ambient Air Quality Standards (NAAQS).  US Environmental Protection Agency, Office of Air Quality Planning and Standards, Washington, DC.  http://www.epa.gov/air/criteria.html.

Picture 1

Classroom univent 1950s vintage

Picture 2

Classroom univent 1970s vintage

Picture 3

Univent fresh air intake

Picture 4

1950s Univent controls, note unit switched to “off” position

Picture 5

1970s Univent controls

Picture 6

Items on top of univent air diffuser and in front of return vent (along bottom)

Picture 7

Bulk rolls of filter media for univents

Picture 8

Metal univent filter racks, note oxidation/corrosion

Picture 9

Severe oxidation/corrosion (interior of univent)

Picture 10

Oxidation/corrosion (metal filter rack)

Picture 11

Air handling unit in gym (arrow)

Picture 12

Air handling unit actuator disconnected in gym

Picture 13

Fresh air intake for gymnasium sealed

Picture 14

1950s classroom exhaust vent, note proximity to open hallway door

Picture 15

Exhaust vent in top of coat closet 1970s wing

Picture 16

Coat closet exhaust undercut (arrow indicates airflow)

Picture 17

Water-damaged ceiling tiles

Picture 18

Water-damaged wood above windows in classroom

Picture 19

Northwest side of building subject to chronic moisture

Picture 20

Severe oxidation of metal heating components in classroom

Picture 21

Severe oxidation of metal building components in classroom

Picture 22

Mold growth on refrigerator/freezer gasket

Picture 23

Mold growth on refrigerator/freezer gasket

Picture 24

Light penetrating through space under gym exterior door

Picture 25

Missing/damaged weather-stripping on gym exterior door

Picture 26

Shrubbery in front of univent air intake

Picture 27

Leaves/debris against foundation, note missing elbow extension on downspout

Picture 28

Missing/damaged downspout

Picture 29

Damaged gutter

Picture 30

Removal of gutter system causing trench along exterior and splashback

on building foundation/exterior walls

Picture 31

Abandoned underground drainage pipes/downspouts removed (arrows), note trench parallel to building

Picture 32

Open utility hole in exterior wall

Picture 33

Rotted/damaged wooden trim along roof’s edge

Picture 34

Rotted/damaged wooden trim along roof’s edge

Picture 35

Recyclable cans in Teacher’s Lunchroom

Picture 36

Missing covers on fluorescent lights

| Location/ Room | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | Temp (°F) | Relative Humidity (%) | PM2.5 (µg/m3) | Occupants in Room | Windows Openable | Ventilation | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Background | 390 | ND | 52 | 39 | 12 |  |  |  |  | Partly cloudy, winds NNW 9-17 mph, gusts up to 29 mph |
| Gym | 590 | ND | 63 | 36 | 10 | 20 | N | Y | Y | Missing/damaged air intake actuator, AHU, spaces under exterior door, air intake appears to be sealed on exterior wall |
| Library | 770 | ND | 71 | 32 | 6 | 27 | N | Y | Y | Exhaust off/backdrafting, 1 of 2 UVs off, DO |
| Teacher’s Lounge | 755 | ND | 73 | 30 | 5 | 7 | Y | Y | Y | Missing fluorescent light covers, cans in box, PCs, mold on refrigerator gaskets |
| 11 | 740 | ND | 72 | 26 | 11 | 21 | Y | Y | Y | Coat closet exhaust-obstructed, DO |
| 12 | 787 | ND | 72 | 29 | 7 | 23 | Y | Y | Y | Window open, DO, UV-off |
| 14 | 732 | ND | 76 | 28 | 6 | 2 | Y | Y | Y | UV-deactivated, window leaks, WD wood along top/windows |
| 15 | 621 | ND | 75 | 23 | 6 | 1 | Y | Y | Y | Missing florescent light covers, 16 occupants at lunch~ 5 mins, DO |
| 17 | 1007 | ND | 74 | 29 | 8 | 1 | Y | Y | Y | 18 occupants gone~10 mins, DO |
| 18 | 900 | ND | 74 | 28 | 6 | 21 | Y | Y | Y | PF, DO |
| Hallway (outside rooms 18 & 19) |  |  |  |  |  |  |  |  |  | Spaces under exterior door |
| 19 | 508 | ND | 73 | 24 | 7 | 0 | Y | Y | Y | DO |
| 20 | 464 | ND | 73 | 23 | 6 | 1 | Y | Y | Y | 23 occupants gone 45 mins, 3 WD CT, WD wood over windows, DO, items on UV |
| 21 | 666 | ND | 73 | 24 | 6 | 16 | Y | Y | Y | PF-dusty, DO |
| 22 | 485 | ND | 71 | 24 | 6 | 1 | Y | Y | Y | 7 WD CTs, window open |
| 23 | 672 | ND | 72 | 26 | 6 | 17 | Y | Y | Y | Plants |
| 24 | 476 | ND | 73 | 25 | 6 | 1 | Y | Y | Y |  |
| 25 | 715 | ND | 72 | 26 | 7 | 16 | Y | Y | Y | DO |
| 26 | 483 | ND | 71 | 24 | 6 | 4 | Y | Y | Y | DO |
| 27 | 609 | ND | 71 | 25 | 7 | 18 | Y | Y | Y | DO |
| 1st Fl Teacher’s Restroom |  |  |  |  |  |  | N | N | Y | Exhaust off |
| Cafeteria | 791 | ND | 75 | 30 | 7 | ~75 | Y | Y | Y |  |

# Footnotes

The service life is the median time during which a particular system or component of …[an HVAC]… system remains in its original service application and then is replaced.  Replacement may occur for any reason, including, but not limited to, failure, general obsolescence, reduced reliability, excessive maintenance cost, and changed system requirements due to such influences as building characteristics or energy prices (ASHRAE, 1991).

# Text boxes

INDOOR AIR QUALITY ASSESSMENT

Centerville Elementary School

658 Bay Lane

Centerville, Massachusetts

Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health

Indoor Air Quality Program

April 2013