| Massachusetts Department of Environmental Protection Bureau of Resource Protection – Drinking Water Program Items to be Considered and Addressed upon Discovery of Coliform Bacteria |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Items to be Considered and Addressed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| For PWS Use Only – not to be returned to MassDEP. PWSs may find this self-evaluation form a useful tool. | • Sampling and Results • System Specifics, Supply Specifics, Storage Specifics • Backflow Prevention Devices • Potential For Biofilm • Public Notification Public Relations • Remedial Options Considered A. Chlorination of Supply B. Chlorination of Storage C. Chlorination of Distribution System • Summary and Conclusions, Comments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A. Sampling & Results |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Important: When filling out forms on the computer, use only the tab key to move your cursor - do not use the return key. | Date of Sampling |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total Number of Samples |  |  |  |  |  |  |
|  | Number of total Coliform positive |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Number of fecal or E. coli positive |  |  |  |  |  |  |
|  | Total Number of Repeat Samples |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Number of Repeat Positive Samples |  |  |  |  |  |  |
|  | 1. Are these positive samples located in one general area of the distribution system? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 2. Is the discovery of coliform bacteria a recurring situation? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 2a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3. Was the previous cause for coliform bacteria in the system determined? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 3a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 4. What is the background bacterial count at positive sites? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5. Have the background bacteria counts been increasing in the system? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 5a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 6. Has the background bacteria been increasing in the area of concern? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 6a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 7. The immediate matter of concern is total coliform Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 8. The immediate matter of concern is fecal coliform Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 9. The immediate matter of concern is E.coli Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 10. The immediate matter of concern is background bacteria Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 11. The immediate matter of concern is other Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A. Sampling & Results (cont.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 12. Contact with laboratory indicates a potential sampling or analysis problem Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 12a. Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 13. Contact with surrounding communities indicate similar problems Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 13a. Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 14. Were standard sampling procedures utilized to the best of your knowledge? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 14a. If not, explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15. Are Personnel collecting samples the same? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 16. Is there a change in sampling locations? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 17. Was there any change at the sample tap? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 18. Was there a change in pH? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 19. Was there a change in water temperature? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | B. System Specifics |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 20. List the main supply to the area of concern (well/ wells, surface supply, etc.): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 21. Was all source water free of positive results? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 21a. If not, explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 22. List the storage facilities feeding the area of concern: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 23. Was all storage water free of positive results? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 23a. If not, explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 24. Have any repairs recently been made in the distribution system? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 24a. Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 25. Have any system improvements recently been made in the distribution system? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 25a. Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | B. System Specifics (cont.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 26. Were these improvements new mains? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 27. Were these mains chlorinated? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 28. Has a temporary connection to a hydrant for service or pool filling been made? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 29. Has a new development water system been recently connected? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 30. Was the system disinfected? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 31. Was a report received? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 32. Has there been a recent fire? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 33. Is a flushing program ongoing? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 34. Have street sweeping operations utilizing hydrants been ongoing? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 35. Have any new wells feeding irrigation systems recently been put on line? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 36. Were there any recent changes in system hydraulics, reverse flow, etc? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 36a. Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 37. Is the area of concern on town sewer? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 38. Percent on septic systems: |  |  |  |  |  |  |  |  |  |  | % |  |  |  |  |  |  |  |  |  |  |  |
|  | 39. Are there reports of major failure of septic systems in area of concern? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 39a. Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 40. Has input from the Board of Health been received? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 40a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | C. Supply Specifics |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 41. Have any repairs or modifications been made at the supplies? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 42. List the supply modifications, including repairs, changes in chemical feed, etc. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 43. Is the system normally chlorinated? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 44. Compound added: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | C. Supply Specifics (cont.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 45. Desired residual at supply: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 46. Residual at last test: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 47. Desired residual in system: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 48. Residual at last test in area of concern: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 49. Is the chlorination system operating satisfactorily? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 50. Is a corrosion control program in effect? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 50a. Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 51. Have any changes been made in the corrosion control compound utilized? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 51a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 52. Has the feed rate changed? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 53. Is pH adjustment utilized? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 54. Is chlorine added to day tank? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 54a. Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 55. Which supplies are located in close proximity to surface waters, wetlands, etc? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 56. Are any of the supplies surface water? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 57. Are any groundwater supplies designated as being influenced by surface water? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 58. Has there been an above average amount of precipitation during the past month? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 59. Was flooding evident in the area of the supplies? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 60. Has there been an increase in pumping at these supplies? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 60a. Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 61. Has there been a noticeable decrease in water level in the area of the supplies? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 62. Has there been any unusual activity ongoing within the Zone I of the supplies? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 62a. Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | C. Supply Specifics (cont.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 63. Has there been any unusual activity ongoing within the Zone II of the supplies? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 63a. Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | D. Storage Specifics |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 64. Have any repairs or modifications been made to the storage facilities? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 65. Has an inspection of the storage facilities recently been performed? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 65a. If yes, when? |  |  |  |  |  |  | Date |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 66. Were any deficiencies in the roof noted? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 67. Were there any deficiencies noted on the roof hatch? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 68. Was it locked? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 69. Is cathodic protection provided? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 70. Are the cover plates water tight? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 71. Is there an exterior weir box? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 72. Was the overflow screen checked? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 73. Has the interior floor of the storage facility been recently inspected for residue? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 74. Is there evidence or a history of roosting birds on this facility? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | E. Backflow Prevention Devices |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 75. List the backflow devices in the general area of concern: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 76. Do any of these have a history of failure? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 76a. Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 77. List those recently tested: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 78. Did any fail? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 78a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 79. List those to be tested: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | E. Backflow Prevention Devices (cont.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 80. Is an active cross-connection program in effect? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | F. Potential for Biofilm |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 81. Was the drinking water temperature at its highest at the time of positive results? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 82. Has the system experienced or suspected a biofilm problem in the past? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 83. Was it confirmed? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 83a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 84. Has a microbiological species identification been completed? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 85. The predominant species are: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Escherichia Coll (E-coli) Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Klebsiella Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Enterobacter Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Citrobacter Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Serratia Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Campylobacter Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Vibro cholerae Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Aeromonas Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Salmonella Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Pseudomonas Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Legionella Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Pneumophila Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Bactillus Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Micrococcus Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | - Other |  | (specify) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Y N |
|  | F. Potential for Biofilm (cont.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 86. Has fire flow testing indicated tuberculation buildup in piping (decrease flow)? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 87. Has a new corrosion control facility been recently activated? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 88. Is pH adjustment utilized in this facility? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 89. What is the pH change at the supply? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 90. What is the desired pH in the system? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 91. What is the actual pH in the area of concern? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 92. Have phosphates recently been added as a corrosion control measure? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 93. What is the compound utilized: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a. Orthophosphate Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b. Polyphosphate Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | c. Blended Phosphate Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | d. Silicates Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | e. Other |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Y N |  |
|  | 94. Have there been any unusual occurrences that could cause increases of biofilm nutrients such as increases in organic carbon, nitrogen, or phosphorus at the supplies (heavy rainfall, excessive surface water runoff, flooding, etc.)? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 94a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | G. Public Notification |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 95. Do you suspect the problem to be biofilm oriented? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 95a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 96. Has MassDEP been notified? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 96a. Date notified: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 97. Recommendations received from MassDEP |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 98. Is public notification necessary? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | G. Public Notification (cont.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 99. Has public notification been completed? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 100. Where was public notice published/ posted? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 100a. Date published/ posted: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 101. Has MassDEP indicated a mailing will be necessary? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 102. How is the mailing to be accomplished? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 102a. Date of mailing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 103. Was the public notification waived? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 103a. By whom? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 103b. Date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | H. Public Relations |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 104. What measures are to be taken for public relations? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 105. Has your staff answering the phones been instructed regarding potential questions and the proper responses? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 105a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 106. Have the various town boards/officials been made aware of the problem and action being taken? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 107. Have local medical care facilities and doctors been made aware of the problem and action being taken? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 108. Are newspaper announcements necessary to inform the public of the progress being made to eliminate the problem? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 109. What would you do differently in public relations if this situation occurs again? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 110. From the testing to date, does the discovery of coliform bacteria appear to be a health threat? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 110a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | I. Remedial Options Considered |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 111. Is temporary chlorination of the supplies a viable option? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A. Chlorination of Supply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 112. How will it be instituted? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 113. Desired free chlorine residual: |  |  |  |  |  |  |  |  |  |  |  |  | mg/L |  |  |  |  |  |  |  |  |  |
|  | 114. Compound to be utilized: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a. Ca(ClO)2, calcium hypochlorite (HTH @ 65% chlorine) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b. NaClO, sodium hypochlorite (12.5% chlorine) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | c. Other |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 115. Supply discharge rate: |  |  |  |  |  |  |  |  | gpm |  |  |  |  |  |  |  |  |  |  |  | (gpm x 1440 = gpd) |  |
|  | Calculations for HTH feed for a 24 hour period |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | #HTH = chlorine (ppm) x rate (gpd) x 8.34 #/gal 1,000,000 x .65 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sample Problem (HTH) Chlorination of Supply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Want to feed a concentration of 1.2 ppm (mg/I) free chlorine to a supply with a discharge rate of 500 gallons per minute. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 500 gpm x 1440 min/day = 720,000 gpd #HTH = 1.2 ppm x 720,000 gpd x 8.34 #/gal = 11.08 pounds HTH per day 1,000,000 x .65 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Calculation for chlorination at Well # utilizing HTH |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | #HTH = _______ (ppm) x _______ gpd x 8.34 #/gal = pounds HTH per day 1,000,000 x .65 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Calculations for sodium hypochlorite (NaOCI) for a 24 hour period |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | In general, a solution of NaOCI at 12.5% solution yields 1 pound of chlorine per gallon |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | gallons of 12.5% NaOCI = chlorine (ppm) X rate (qpd) X 8.34 #/qal (or #s of chlorine) 1,000,000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | I. Remedial Options Considered (cont.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sample Problem (12.5% NaOCI) chlorination of supply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Want to feed a concentration of 1.2 ppm (mg/0 free chlorine to a supply with a discharge rate of 500 gallons per minute. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 500 gpm X 1440 min/day = 720000 gpd |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | gallons 12.5% NaOCI = 1.2 ppm X 720,000 gpd X 8.34 #/gal = 7.2 gallons NaOCI per day 1,000,000 or 7.2 # chlorine |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | If chlorine solution concentration different, use same calculation with ratio of concentration used as a multiplier. If solution is 5.5%, calculate as follows: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 12.5%/5.5% = 2.272 multiply calculation solution by 2.272 (for sample problem) 2.272 x 7,2 gallons NaOCI = 16.4 gallons NaOCI per day |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Calculation for chlorination at supply utilizing NaOCI |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | gallons 12.5% NaOCI = ppm x qpd x 8.34 #/gal = gallons NaOCI per day 1,000,000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | B. Chlorination of Storage Facility |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 116. Is chlorination of the storage facilities a viable option? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 117. How will it be instituted? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 118. Desired free chlorine residual: |  |  |  |  |  |  |  |  |  |  |  |  |  | mg/L |  |  |  |  |  |  |  |  |
|  | 119. Compound to be utilized: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | a. Ca(ClO)2, calcium hypochlorite (HTH @ 65% chlorine) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | b. NaClO, sodium hypochlorite (12.5% chlorine) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | c. Other: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | d. Storage capacity |  |  |  |  |  |  | gallons |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Calculations for HTH feed for a water storage facility |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | #HTH = chlorine (ppm) x capacity (gallons) x 8.34 #/gal 1,000,000 x .65 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sample Problem (HTH) chlorination of storage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Want to attain a concentration of 1.2 ppm (mg/}) free chlorine within a 2,000,000 million gallon storage facility. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | #HTH = 1.2 ppm x 2.000,000 gallons x 8.34 #/gal = 30.8 pounds HTH 1,000,000 X .65 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | I. Remedial Options Considered (cont.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Calculation for chlorination of storage utilizing HTH |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | # HTH = _________ppm x gallons x 8.34 #/gal pounds HTH 1,000,000 x .65 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Calculations for sodium hypochlorite (NaOCI) feed for a water storage facility |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Remember a solution of NaOCI at 12.5% solution has 1 pound of chlorine per gallon |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | gallons of 12.5% NaOCI = chlorine (ppm) x volume (gallons) x 8.34 #/gal (or #’s of chlorine) 1,000,000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Sample Problem (12.5% NaOCI) chlorination of supply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Want to feed a concentration of 1.2 ppm (mg/I) free chlorine, to a supply with a discharge rate of 500 gallons per minute. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 500 gpm x 1440 min/day = 720,000 gpd |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | gallons NaOCI = 1.2 ppm x 2,000,000 gallons X 8.34 #/gal = 7.2 gallons NaOCI per day (or #'s of chlorine) 1,000,000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Calculation for chlorination at storage utilizing NaOC1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | gallons NaOCI = _________ppm x gpd x 8.34 al/gal = gallons NaOCI per day 1,000,000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | C. Distribution System Chlorination |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 120. Is site specific chlorination in the distribution system warranted? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 121. How will it be instituted? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 122. Is the flow basically in one direction? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 123. Can a flow rate be determined? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 124. Can a bleeder be installed to maintain a relatively constant flow? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 125. What is the desired residual in the system? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | mg/L |  |  |  |  |  |  |
|  | 126. What is the chlorine feed rate at the site of injection? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | mg/L |  |  |  |  |
|  | 127. Has flushing in the area of concern been instituted? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 127a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 128. Can the area be isolated to insure against reverse flow carrying contamination to other sections of the system? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 128a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Calculations the same for feeding in the distribution system as at the supply, once an average flow rate is determined |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | J. Summary and Conclusions |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 129. Was the problem determined? Y N |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 129a. Explain: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 129b. If not, what is suspected? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 130. Reason for this suspicion: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 131. Recommendations for eliminating this problem in the future: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 132. Recommendations for investigating future similar problems: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | General Comments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 134. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 135. If this situation occurs again, would you do anything differently? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |