INDOOR AIR QUALITY REASSESSMENT

Massachusetts Department of Children and Families

110 Mulberry Street

Brockton, Massachusetts

Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health

Indoor Air Quality Program

September 2009

# Background/Introduction

In response to a request from William Kelley, Area Director for the Massachusetts Department of Children and Families (DCF), the Massachusetts Department of Public Health (MDPH), Bureau of Environmental Health (BEH), provided assistance and consultation regarding indoor air quality concerns at the DCF office located at 110 Mulberry Street, Brockton, Massachusetts.  The request was prompted by occupant complaints of recurring respiratory effects.

On June 16, 2009, a visit to conduct an indoor air quality reassessment was made to the DCF by Cory Holmes, Environmental Analyst/Inspector in BEH’s Indoor Air Quality (IAQ) Program.  Mr. Holmes was accompanied by Mr. Kelley for portions of the reassessment.  BEH staff previously visited the building in September of 2006, and a report was issued (MDPH, 2006).  The report showed that problems were identified and provided recommendations on how to correct those problems.

Actions on Previous MDPH Recommendations

As mentioned, MDPH staff had previously visited the building and issued a report with recommendations to improve indoor air quality (MDPH, 2006).  A summary of actions taken on previous recommendations is included as Appendix A.

Methods

Air tests for carbon dioxide, temperature and relative humidity were taken with the TSI, Q-Trak, IAQ Monitor 8551.  Air tests for airborne particle matter with a diameter less than 2.5 micrometers were taken with the TSI, DUSTTRAK™ Aerosol Monitor Model 8520.  BEH staff performed a visual inspection of building materials for water damage and/or microbial growth.  Moisture content of porous building materials was measured with a Delmhorst, BD-2000 Model, Moisture Detector equipped with a Delmhorst Standard Probe.

Results

The DCF has an employee population of approximately 115 and is visited by up to 30 individuals daily.  The tests were taken during normal operations.  Test results appear in Table 1.

Discussion

Ventilation

It can be seen from Table 1 that carbon dioxide levels were below 800 parts per million (ppm) in all but one area surveyed indicating adequate air exchange throughout the building the day of the assessment.  Several readings were recorded over the course of the visit in Ms. Caledonia’s office, carbon dioxide levels ranged from 674 to 808.  Mechanical ventilation is provided by rooftop air-handling units (AHUs) (Picture 1).  Fresh air is drawn into the AHUs and delivered to occupied areas via ceiling-mounted air diffusers (Picture 2).  Return air is drawn into ceiling-mounted vents in common areas and ducted back to the AHUs (Picture 3).  Offices are not equipped with return vents but rely on undercut doors, which allow stale air to exit the office into common areas where return vents are located.

Occupants in the row of offices including Ms. Caledonia’s expressed complaints of thermal discomfort and lack of airflow.  It is important to note that the nearest return vent is approximately 20 to 25 feet down the corridor (Picture 4), which may result in a lack of air exchange at times in this area.  Mr. Kelley reported that the building management and his HVAC vendor are examining ways to improve air exchange in this area.  A supply vent in Ms. White’s office that was obstructed with what looked like a manila envelope above the diffuser was also observed (Picture 5).  This alteration can create an imbalance in the system, resulting in uneven heating/cooling conditions leading to occupant discomfort.  In subsequent correspondence with Mr. Kelley, MDPH learned that the obstruction has been removed.  No provision for mechanical ventilation was observed in the reception area, nor is this area equipped with a window.

Three digital wall-mounted thermostats control the heating, ventilating and air conditioning (HVAC) system.  Thermostats have fan settings of “on” and “automatic”.  Thermostats were set to the “on” setting during the assessment (Picture 6), which is recommended by the MDPH to provide optimal air circulation.

To maximize air exchange, the MDPH recommends that both supply and exhaust ventilation operate continuously during periods of occupancy.  In order to have proper ventilation with a mechanical supply and exhaust system, the systems must be balanced to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room.  It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).  During the assessment Mr. Kelley contacted building management who reported that the system was completely balanced five years ago with adjustments to certain areas over the past year.

The Massachusetts Building Code requires a minimum ventilation rate of 20 cubic feet per minute (cfm) per occupant of fresh outside air or have openable windows in each room (SBBRS, 1997; BOCA, 1993).  The ventilation must be on at all times that the room is occupied.  Providing adequate fresh air ventilation with open windows and maintaining the temperature in the comfort range during the cold weather season is impractical.  Mechanical ventilation is usually required to provide adequate fresh air ventilation.

Carbon dioxide is not a problem in and of itself.  It is used as an indicator of the adequacy of the fresh air ventilation.  As carbon dioxide levels rise, it indicates that the ventilating system is malfunctioning or the design occupancy of the room is being exceeded.  When this happens, a buildup of common indoor air pollutants can occur, leading to discomfort or health complaints.  The Occupational Safety and Health Administration (OSHA) standard for carbon dioxide is 5,000 parts per million parts of air (ppm).  Workers may be exposed to this level for 40 hours/week, based on a time-weighted average (OSHA, 1997).

The MDPH uses a guideline of 800 ppm for publicly occupied buildings.  A guideline of 600 ppm or less is preferred in schools due to the fact that the majority of occupants are young and considered to be a more sensitive population in the evaluation of environmental health status.  Inadequate ventilation and/or elevated temperatures are major causes of complaints such as respiratory, eye, nose and throat irritation, lethargy and headaches.  For more information concerning carbon dioxide, please see Appendix B.

Temperature readings ranged from 69o F to 76 o F, which were within or very close to the lower end of the MDPH recommended comfort guidelines in all areas surveyed.  The MDPH recommends that indoor air temperatures be maintained in a range of 70 o F to 78 o F in order to provide for the comfort of building occupants.  In many cases concerning indoor air quality, fluctuations of temperature in occupied spaces are typically experienced, even in a building with an adequate fresh air supply.

Relative humidity measurements in the building ranged from 44 to 55 percent, which were within the MDPH recommended comfort range in all areas surveyed the day of the assessment.  The MDPH recommends a comfort range of 40 to 60 percent for indoor air relative humidity.  Relative humidity levels in the building would be expected to drop during the winter months due to heating.  The sensation of dryness and irritation is common in a low relative humidity environment.  Low relative humidity is common during the heating season in the northeast part of the United States.

Microbial/Moisture Concerns

Several areas had water damaged ceiling tiles.  Water damaged ceiling tiles can provide a source of mold and should be replaced after a water leak is discovered and repaired.  Water damaged tiles in conference room D (Picture 7), reportedly occurred from leakage of the air-conditioning unit that was under repair at the time of the assessment.  Water damaged tiles in exterior areas (Pictures 8 and 9) appear to be from water penetration through the building envelope/exterior walls.  Mold concerns were expressed in Ms. Robidoux office, which had been an area of previous water leaks.  BEH staff removed a water stained tile to examine conditions above the ceiling (Picture 10).  The area had a large open space, which would facilitate drying in the event of a leak.  No visible mold or current water damage was observed.

In order for building materials to support mold growth, a source of water exposure is necessary.  Identification and elimination of water moistening building materials is necessary to control mold growth.  Materials with increased moisture content over normal concentrations may indicate the possible presence of mold growth.  All materials tested in Ms. Robidoux’s office were found to have low (i.e., normal) moisture content (Table 1) at the time of the assessment.

What appeared to be visible mold growth on a water damaged ceiling tile was observed in the kitchen/break room (Picture 11).  The tile was found to be wet at the time of the assessment.  BEH staff removed the tile and found a damaged pipe above it that appeared to be the source of moisture (Picture 12).

The US Environmental Protection Agency (US EPA) and the American Conference of Governmental Industrial Hygienists (ACGIH) recommend that porous materials be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2001; ACGIH, 1989).  If not dried within this time frame, mold growth may occur.  Once mold has colonized porous materials (e.g., ceiling tiles) they are difficult to clean and should be removed/discarded.

Finally, pooling water around clogged roof drains was observed on the roof (Pictures 13 and 14).  The freezing and thawing of water during winter months can lead to roof leaks and subsequent water penetration into the interior of the building.  Pooling water can also become stagnant, which can lead to mold and bacterial growth, and serve as a breeding ground for mosquitoes.

Other IAQ Evaluations

Indoor air quality can be negatively influenced by the presence of respiratory irritants, such as products of combustion.  The process of combustion produces a number of pollutants.  Common combustion emissions include carbon monoxide, carbon dioxide, water vapor and smoke (fine airborne particle material).  Of these materials, exposure to carbon monoxide and particulate matter with a diameter of 2.5 micrometers (μm) or less (PM2.5) can produce immediate, acute health effects upon exposure.  To determine whether combustion products were present in the building, BEH staff obtained measurements for carbon monoxide and PM2.5.

Carbon Monoxide

Carbon monoxide is a by-product of incomplete combustion of organic matter (e.g., gasoline, wood and tobacco).  Exposure to carbon monoxide can produce immediate and acute health affects.  Several air quality standards have been established to address carbon monoxide and prevent symptoms from exposure to these substances.  The MDPH established a corrective action level concerning carbon monoxide in ice skating rinks that use fossil-fueled ice resurfacing equipment.  If an operator of an indoor ice rink measures a carbon monoxide level over 30 ppm, taken 20 minutes after resurfacing within a rink, that operator must take actions to reduce carbon monoxide levels (MDPH, 1997).

The American Society of Heating Refrigeration and Air-Conditioning Engineers (ASHRAE) has adopted the National Ambient Air Quality Standards (NAAQS) as one set of criteria for assessing indoor air quality and monitoring of fresh air introduced by HVAC systems (ASHRAE, 1989).  The NAAQS are standards established by the US EPA to protect the public health from six criteria pollutants, including carbon monoxide and particulate matter (US EPA, 2006).  As recommended by ASHRAE, pollutant levels of fresh air introduced to a building should not exceed the NAAQS levels (ASHRAE, 1989).  The NAAQS were adopted by reference in the Building Officials & Code Administrators (BOCA) National Mechanical Code of 1993 (BOCA, 1993), which is now an HVAC standard included in the Massachusetts State Building Code (SBBRS, 1997).  According to the NAAQS, carbon monoxide levels in outdoor air should not exceed 9 ppm in an eight-hour average (US EPA, 2006).

Carbon monoxide should not be present in a typical, indoor environment.  If it is present, indoor carbon monoxide levels should be less than or equal to outdoor levels.  On the day of assessment, outdoor carbon monoxide concentrations were non-detect (ND) to 1 ppm (Table 1).  No detectable levels of carbon monoxide were measured inside the building at the time of the assessment (Table 1).

Particulate Matter (PM2.5)

The US EPA has established NAAQS limits for exposure to particulate matter.  Particulate matter is airborne solids that can be irritating to the eyes, nose and throat.  The NAAQS originally established exposure limits to particulate matter with a diameter of 10 μm or less (PM10).  According to the NAAQS, PM10 levels should not exceed 150 microgram per cubic meter (μg/m3) in a 24-hour average (US EPA, 2006).  These standards were adopted by both ASHRAE and BOCA.  Since the issuance of the ASHRAE standard and BOCA Code, US EPA established a more protective standard for fine airborne particles.  This more stringent PM2.5 standard requires outdoor air particle levels be maintained below 35 μg/m3 over a 24-hour average (US EPA, 2006).  Although both the ASHRAE standard and BOCA Code adopted the PM10 standard for evaluating air quality, MDPH uses the more protective PM2.5 standard for evaluating airborne particulate matter concentrations in the indoor environment.

Outdoor PM2.5 concentrations were measured at 2 μg/m3 (Table 1).  PM2.5 levels measured indoors ranged from 1 to 5 μg/m3 (Table 1), which were below the NAAQS PM2.5 level of 35 μg/m3.  Frequently, indoor air levels of particulates (including PM2.5) can be at higher levels than those measured outdoors.  A number of mechanical devices and/or activities that occur in buildings can generate particulate during normal operations.  Sources of indoor airborne particulates may include but are not limited to particles generated during the operation of fan belts in the HVAC system, cooking in stoves and microwave ovens; use of photocopiers, fax machines and computer printing devices; operation of an ordinary vacuum cleaner and heavy foot traffic indoors.

Other Conditions

AHUs are equipped with filters that strain particulates from airflow.  BEH staff conducted an inspection of rooftop AHUs and filters.  Filters examined during the 2006 assessment were of a high efficiency pleated type (Picture 15).  The filters examined in the unit during the reassessment were found to be of a low efficiency mesh type that provides minimal filtration of respirable dusts (Picture 16).  In subsequent correspondence, MDPH learned that Mr. Kelley requested that the HVAC vendor replace the low efficiency mesh filters with the high efficiency pleated filters.  In order to decrease aerosolized particulates, disposable filters with an increased dust spot efficiency should be installed.  The dust spot efficiency is the ability of a filter to remove particulates of a certain diameter from air passing through the filter.  Filters that have been determined by ASHRAE to meet its standard for a dust spot efficiency of a minimum of 40 percent (Minimum Efficiency Reporting Value equal to 9) would be sufficient to reduce many airborne particulates (Thornburg, D., 2000; MEHRC, 1997; ASHRAE, 1992).

Finally, fluorescent light fixtures were missing covers in a number of areas (Picture 17 and 18).  Fixtures should be equipped with access covers installed with bulbs fully secured in their sockets.  Breakage of glass can cause injuries and may release mercury and/or other hazardous compounds.

Conclusions/Recommendations

DCF officials, working in conjunction with building management, staff and maintenance personnel, have improved indoor environmental conditions in the building by implementing the majority of BEH’s previous recommendations.  In view of the findings at the time of the reassessment, the following recommendations are made to further improve indoor air quality:

Continue to implement all applicable recommendations listed in the previous MDPH report (MDPH, 2006).

In order to improve thermal comfort/temperature control it is recommended that DCF staff work in conjunction with building management and their HVAC vendor to examine options to increase air exchange near the Caledonia suite of offices.  Consider adding ducted return vent or local exhaust.

Install supply vent in reception area and/or install passive vent in door to allow for air exchange.

Supplement airflow by using openable windows to control for comfort (with the exception of periods of high outdoor relative humidity to avoid condensation problems).  Care should be taken to ensure windows are properly closed at night and weekends to avoid pipe freezing and potential flooding (during winter months).

Continue with plans to repair AC unit in conference room D.

Consider balancing mechanical ventilation systems every five years as per ventilation industrial standards (SMACNA, 1994).

Continue to encourage DCF staff to report any complaints concerning temperature control/preventive maintenance issues.  Consider creating a work order form/system to report building related issues and efforts to address those issues.

For buildings in New England, periods of low relative humidity during the winter are often unavoidable.  Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low.  To control for dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended.  Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

Ensure leaks are repaired and replace water damaged ceiling tiles.  Examine the area above and around these areas for mold growth.  Disinfect areas of water leaks with an appropriate antimicrobial as needed.

Consider contacting a building envelope specialist to determine the most likely routes of water penetration into the building.

Make repairs to pipe above ceiling tiles in the kitchen/breakroom.

Remove accumulated debris from roof drains and inspect regularly for proper drainage.

Increase the dust-spot efficiency of HVAC filters.

Replace all covers for fluorescent light fixtures.

Continue to clean carpeting annually or semi-annually in soiled high traffic areas as per the recommendations of the Institute of Inspection, Cleaning and Restoration Certification (IICRC).  Copies of the IICRC fact sheet can be downloaded at: http://www.cleancareseminars.com/carpet_cleaning_faq4.htm (IICRC, 2005).

Refer to resource manuals and other related indoor air quality documents for further building-wide evaluations and advice on maintaining public buildings.  Copies of these materials are located on the MDPH’s website: http://mass.gov/dph/iaq.

References

ACGIH.  1989.  Guidelines for the Assessment of Bioaerosols in the Indoor Environment.  American Conference of Governmental Industrial Hygienists, Cincinnati, OH.

ASHRAE.  1989.  Ventilation for Acceptable Indoor Air Quality.  American Society of Heating, Refrigeration and Air Conditioning Engineers. ANSI/ASHRAE 62-1989.

ASHRAE.  1992.  Gravimetric and Dust-Spot Procedures for Testing Air-Cleaning Devices Used in General Ventilation for Removing Particulate Matter.  American Society of Heating, Refrigeration and Air Conditioning Engineers. ANSI/ASHRAE 52.1-1992.

BOCA.  1993.  The BOCA National Mechanical Code/1993.  8th ed.   Building Officials and Code Administrators International, Inc., Country Club Hill, IL.  Section M-308.1.1.

IICRC.  2005.  Carpet Cleaning FAQ 4 Institute of Inspection, Cleaning and Restoration Certification.  Institute of Inspection Cleaning and Restoration, Vancouver, WA.

MDPH.  1997.  Requirements to Maintain Air Quality in Indoor Skating Rinks (State Sanitary Code, Chapter XI).  105 CMR 675.000.  Massachusetts Department of Public Health, Boston, MA.

MDPH.  2006.  Indoor Air Quality Assessment.  Department of Social Services, 110 Mulberry Street, Brockton, MA.  Massachusetts Department of Public Health, Center of Environmental Health, Boston, MA.

MEHRC.  1997.  Indoor Air Quality for HVAC Operators & Contractors Workbook.  MidAtlantic Environmental Hygiene Resource Center, Philadelphia, PA.

OSHA.  1997.  Limits for Air Contaminants.  Occupational Safety and Health Administration.  Code of Federal Regulations.  29 C.F.R 1910.1000 Table Z-1-A.

SBBRS.  1997.  Mechanical Ventilation.  State Board of Building Regulations and Standards.  Code of Massachusetts Regulations.  780 CMR 1209.0

SMACNA.  1994.  HVAC Systems Commissioning Manual.  1st ed.  Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

Thornburg, D.  2000.  Filter Selection: a Standard Solution.  Engineering Systems 17:6  pp. 74-80.

US EPA.  2001.  Mold Remediation in Schools and Commercial Buildings.  US Environmental Protection Agency, Office of Air and Radiation, Indoor Environments Division, Washington, DC.  EPA 402-K-01-001.  March 2001.

US EPA.  2006.  National Ambient Air Quality Standards (NAAQS).  US Environmental Protection Agency, Office of Air Quality Planning and Standards, Washington, DC.  http://www.epa.gov/air/criteria.html.

Picture 1

Rooftop AHUs

Picture 2

Ceiling-Mounted Supply Diffuser

Picture 3

Ceiling-Mounted Return Vent

Picture 4

Nearest Return Vent to (Caladonia) Row of Offices

Picture 5

Supply Diffuser in Ms. White’s Office Obstructed with a Manila Envelope

Picture 6

Digital Thermostat Set to Fan “On” Position

Picture 7

Water Damaged Ceiling Tiles in Conference Room D

Picture 8

Water Damaged Ceiling Tile along Exterior Wall

Picture 9

Water Damaged Ceiling Tile along Exterior Wall

Picture 10

Water Damaged Ceiling Tile along Exterior Wall in Ms. Robidoux’s Office

Picture 11

Water Damaged Ceiling Tile and Dark Staining That Appeared to be Mold Growth

(as Indicated by Arrow) in Kitchen/Breakroom

Picture 12

Damaged Pipe Directly above the Water Damaged Ceiling Tile in Kitchen/Breakroom

Picture 13

Pooling Water around Clogged Roof Drain

Picture 14

Close-Up of Clogged Roof Drain

Picture 15

High Efficiency Pleated Air Filters On-Site, Note Box Full of Filters (Top Left)

Picture 16

Low Efficiency Mesh Filter Installed in Rooftop AHUs

Picture 17

Fluorescent Light Fixture Missing Cover Exposing Bulbs

Picture 18

Fluorescent Light Fixture Missing Cover Exposing Bulbs

| Location/ Room | Occupants in Room | Temp (°F) | Relative Humidity (%) | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | PM2.5 (µg/m3) | Windows Openable | Ventilation | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| Background |  | 63 | 66 | 422 | ND - 1 | 2 |  |  |  | Cool, overcast/cloudy, winds NE 1-13 MPH gusts up to 18 mph, moderate truck traffic in area |
| Mcguinness Unit | 2 | 73 | 55 | 578 | ND | 3 | Y | Y | Y |  |
| Case File Room | 1 | 73 | 54 | 567 | ND | 3 | N | Y | N | Plastic odors from binders, DO |
| Robidoux Unit | 3 | 73 | 53 | 572 | ND | 2 | Y | Y | Y | Plants, toaster |
| Robidoux Office | 1 | 73 | 52 | 586 | ND | 3 | Y | Y | N | 2 CT along window-low moisture Carpet and drywall-low moisture, no visible mold growth above CTs |
| Mcguinness Office | 0 | 73 | 51 | 602 | ND | 2 | N | Y | N |  |
| Copy Area | 1 | 74 | 52 | 627 | ND | 3 | N | Y | Y |  |
| Geary Unit | 3 | 74 | 51 | 686 | ND | 3 | Y | Y | N | No return vent in general area |
| Geary Office | 1 | 75 | 48 | 733 | ND | 4 | Y | Y | N | No return vent in general area |
| Caledonia Office | 1 | 75 | 48 | 746 | ND | 4 | N | Y | N | DO, No return vent in general area ~ 11:00 AM |
| Garibotto Unit | 3 | 75 | 46 | 702 | ND | 3 | N | Y | N | No return vent in general area, plants |
| Garibotto Office | 1 | 75 | 45 | 708 | ND | 4 | N | Y | N | DO, No return vent in general area |
| Caledonia Unit | 3 | 76 | 46 | 728 | ND | 4 | N | Y | Y |  |
| Closed File Room | 2 | 74 | 45 | 666 | ND | 4 | N | Y | N | Files, clutter, DO |
| Joyce Office | 1 | 74 | 47 | 576 | ND | 3 | Y | Y | N |  |
| Area Director Admin | 1 | 74 | 47 | 576 | ND | 3 | Y | Y | N |  |
| Area Director Conference Room | 0 | 74 | 47 | 611 | ND | 3 | Y | Y | Y |  |
| Admin | 3 | 74 | 48 | 618 | ND | 3 | Y | Y | Y |  |
| Kelley Office | 0 | 74 | 48 | 615 | ND | 4 | Y | Y | N | DO |
| Castellina Office | 0 | 73 | 47 | 576 | ND | 4 | Y | Y | N | DO |
| Horber Office | 0 | 73 | 48 | 563 | ND | 3 | Y | Y | N | DO |
| Conference Room E | 0 | 74 | 49 | 674 | ND | 2 | N | Y | Y | DO |
| Reception Desk | 1 | 75 | 50 | 754 | ND | 4 | N | N | N | Recommend install supply vent/passive vent door |
| Malave Ongoing Unit | 2 | 74 | 48 | 602 | ND | 3 | Y | Y | N |  |
| Malave Office | 0 | 74 | 47 | 589 | ND | 3 | N | Y | N | DO |
| Landoli Office | 1 | 74 | 47 | 587 | ND | 3 | N | Y | N | DO |
| Cullen Office | 1 | 74 | 47 | 608 | ND | 3 | N | Y | N | DO, plants |
| Meting Room Family Resources | 0 | 73 | 47 | 594 | ND | 4 | N | Y | N | DO |
| Sheppard Office | 0 | 73 | 48 | 599 | ND | 4 | Y | Y | N | DO |
| Adoption Unit | 2 | 73 | 48 | 653 | ND | 4 | Y | Y | N | WD CT corner |
| Lownds Unit | 4 | 73 | 49 | 698 | ND | 4 | N | Y | N |  |
| Medeiros Office | 1 | 74 | 47 | 679 | ND | 4 | N | Y | N | DO |
| Rucker Unit | 6 | 74 | 48 | 721 | ND | 4 | N | Y | N |  |
| Lownds Office | 0 | 74 | 47 | 714 | ND | 4 | N | Y | N | DO |
| McGrath Unit | 5 | 74 | 47 | 687 | ND | 4 | N | Y | N |  |
| Rucker Office | 0 | 74 | 47 | 709 | ND | 3 | N | Y | N |  |
| Kapp Office | 1 | 73 | 46 | 658 | ND | 5 | N | Y | N |  |
| Kapp Unit | 4 | 74 | 48 | 691 | ND | 4 | N | Y | N |  |
| McGrath Office | 2 | 74 | 48 | 713 | ND | 5 | N | Y | N | DO |
| French Unit | 4 | 74 | 49 | 730 | ND | 4 | N | Y | N |  |
| French Office | 0 | 74 | 49 | 713 | ND | 3 | N | Y | N |  |
| Curran Unit | 3 | 71 | 49 | 689 | ND | 5 | Y | Y | N |  |
| Curran Office | 0 | 72 | 49 | 672 | ND | 5 | N | Y | N |  |
| Foster Care Unit | 1 | 71 | 48 | 684 | ND | 3 | N | Y | Y | Exterior door spaces-light penetration |
| Midge’s Attic (Storage) | 0 | 71 | 49 | 680 | ND | 4 | N | N | N | DO |
| Adolescent Unit | 2 | 70 | 47 | 709 | ND | 4 | N | Y | Y | 1 WD CT |
| Pierce Unit | 2 | 69 | 48 | 699 | ND | 4 | Y | Y | Y | 1 WD CT over fire alarm light |
| Pierce Office | 0 | 71 | 48 | 610 | ND | 4 | N | Y | N | DO |
| Kitchen Breakroom | 0 | 72 | 51 | 648 | ND | 4 | N | Y | Y | WD CT dark staining appears to be mold growth, leaking pipe over tile, moisture measurement-wet/saturated |
| Hartstone Office | 0 | 72 | 49 | 642 | ND | 4 | N | Y | N |  |
| Page Office | 1 | 73 | 50 | 625 | ND | 4 | N | Y | N |  |
| White Office | 1 | 74 | 50 | 693 | ND | 5 | N | Y | N | Supply obstructed with manila envelope, DO |
| JRI Unit | 3 | 74 | 49 | 672 | ND | 5 | N | Y | N | Thermostat Fan-On |
| Phillips Office | 0 | 73 | 48 | 630 | ND | 3 | N | Y | N | DO |
| Phillips Unit | 1 | 73 | 48 | 590 | ND | 3 | N | Y | N |  |
| Aruda Office | 0 | 74 | 48 | 629 | ND | 4 | N | Y | N | DO |
| Garibotto | 1 | 75 | 46 | 749 | ND | 3 | N | Y | N | DO |
| Caledonia | 0 | 75 | 44 | 674 | ND | 4 | N | Y | N | DO, ~ 12:45 PM |
| Geary | 1 | 74 | 46 | 733 | ND | 4 | N | Y | Y | DO |
| Conference Room D | 0 | 74 | 46 | 689 | ND | 4 | N | Y | Y | DO, 2 WD CT reportedly from damaged AC unit, being repaired |
| Caledonia | 1 | 75 | 45 | 808 | ND | 4 | N | Y | N | ~2:30 PM |

Actions on Previous MDPH Recommendations

The following is a status report of action(s) taken on previous MDPH recommendations (in bold) based on reports from DCF officials, building management, maintenance personnel and BEH staff observations.

- In order to improve thermal comfort/temperature control it is highly recommended that DCF staff work in conjunction with building management and their HVAC vendor to examine the configuration of floor space and the placement of thermostats/sensors.  Consider adding additional zones, sensors and/or controls to improve comfort.

Action:  In an attempt to improve comfort, additional sensors were reportedly added and the system was re-balanced.

Continue with plans to install additional HVAC equipment in conference room D, an increase in the supply of fresh outside air to this area is recommended.

Action:  An additional HVAC unit was installed in conference room D.

Consult building management to determine function of vent outside the foster care review/adolescent unit area.  If vent is deactivated/unnecessary, consider sealing to prevent air infiltration.

Action:  At the time of the recent MDPH IAQ assessment, the function of the vent had not been identified or sealed.

Seal spaces around exterior doors in the foster care review/adolescent unit area with weather-stripping and/or a door sweep to prevent drafts and/or pest infiltration.

Action:  Mr. Kelley reported that building management was making plans to install weather-stripping beneath the doors.

Consider applying solar (tinted) film to windows as needed to reduce solar gain/excess heat.

Action:  One room had the solar film applied; according to Mr. Kelley several occupants reportedly declined the application.

Supplement airflow by using openable windows to control for comfort (with the exception of periods of high outdoor relative humidity to avoid condensation problems).  Care should be taken to ensure windows are properly closed at night and weekends to avoid pipe freezing and potential flooding (during winter months).

Action:  Occupants were reportedly told by management of their option to open windows to increase air circulation.

Encourage DCF staff to report any complaints concerning temperature control/preventive maintenance issues.

Action:  Mr. Kelley reported that DCF staff were encouraged to report temperature complaints.

Ensure leaks are repaired and replace water damaged ceiling tiles.  Examine the area above and around these areas for mold growth.  Disinfect areas of water leaks with an appropriate antimicrobial as needed.

Action:  Identification of leaks and repair is reportedly an ongoing process.  Repeated attempts have been made by building management via the use of private contractors to identify and repair leaks, with some success.  However, several problem areas are still under investigation due to periodic leaks during severe wind and weather patterns.  Water damaged ceiling tiles were noted in exterior corners of the building.  Although the ceiling tiles were stained, no visible mold growth was observed.  Staff are encouraged to report further damage and ongoing leaks to DCF/building management for corrective action.

Ensure plants have drip pans and avoid over-watering.  Examine drip pans periodically for mold growth and disinfect with an appropriate antimicrobial where necessary.

Action:  Advice concerning use/maintenance of plants/drip pans was reportedly communicated to DCF staff.

Relocate or place tile or rubber matting underneath water coolers in carpeted areas.  Clean and disinfect reservoirs as needed to prevent microbial growth.

Action:  In subsequent correspondence with Mr. Kelley, it was reported that mats were obtained for beneath water coolers.

Clean supply, return and restroom exhaust vents periodically of accumulated dust.

Action:  It was reported that vents are on a schedule to be cleaned twice a year.  Exhaust vents tend to accumulate more dust/debris than supply vents and should be cleaned on a more rigorous schedule, if needed.

Clean carpeting annually or semi-annually in soiled high traffic areas as per the recommendations of the Institute of Inspection, Cleaning and Restoration Certification (IICRC).

Action:  Carpets are reported to be on a schedule to be cleaned twice a year.

Discontinue the personal use of spray pesticides within the building.

Action:  DCF staff were reportedly advised to discourage personal use of spray pesticides.