INDOOR AIR QUALITY ASSESSMENT

Massachusetts Department of Environmental Protection

Southeast Regional Office

20 Riverside Drive

Lakeville, MA 02347

Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health

Indoor Air Quality Program

January 2009

# Background/Introduction

At the request of Mr. David Johnston, Southeast Regional Director for the Massachusetts Department of Environmental Protection (DEP), the Massachusetts Department of Public Health (MDPH), Bureau of Environmental Health (BEH) provided assistance and consultation regarding indoor air quality concerns at the Southeast Regional Office (SERO) located at 20 Riverside Drive, Lakeville, Massachusetts.  The request for assistance was prompted due to employee concerns of a possible connection between reported heart viruses in some building occupants and environmental conditions in the building, as well as general indoor air quality and comfort concerns.

The building was previously visited by BEH staff in May 1993, and a report detailing conditions observed at that time as well as recommendations for improving indoor air quality was issued (MDPH, 1993).  On October 7, 2008, Cory Holmes and James Tobin, Environmental Analysts/Inspectors within BEH’s Indoor Air Quality (IAQ) Program, conducted an assessment of the DEP SERO.  It was reported that several days prior to this most recent MDPH visit, the landlord/building management had hired LFR Environmental Engineering to conduct mold and bacteria testing in the building and were awaiting the report.

The DEP SERO occupies the entire second and the majority of the first floor of a two-story red brick office building built in 1993.  The Federal Bureau of Investigation (FBI) occupies the remaining section of the first floor.  The building consists of two wings that flank the main entrance/central foyer (Picture 1).  The space is made up of perimeter offices, work stations (cubicles), and common areas with wall-to-wall carpeting, tiled floors and dropped ceilings.  The building does not have openable windows and is entirely reliant on the heating, ventilation and air-conditioning (HVAC) system for air exchange.  The DEP has occupied the building since 1993.  Interior renovations including painting, new carpeting and thermostats has occurred over the past several years.

Methods

Air tests for carbon monoxide, carbon dioxide, temperature and relative humidity were conducted with the TSI, Q-Trak, IAQ Monitor, Model 7565/8554.  Air tests for airborne particle matter with a diameter less than 2.5 micrometers were taken with the TSI, DUSTTRAK™ Aerosol Monitor Model 8520.  Screening for total volatile organic compounds (TVOCs) was conducted using a MiniRAE 2000 Portable VOC Monitor, Model PGM 7600.  MDPH staff also performed visual inspection of building materials for water damage and/or microbial growth.  Moisture content of porous building materials (e.g., gypsum wallboard, ceiling tiles, carpeting) was measured with Delmhorst, BD-2000 Model, Moisture Detector with a Delmhorst Standard Probe.

Results

The DEP SERO has an employee population of approximately 135 and is visited by up to 25 members of the public daily.  The tests were taken during normal operations and results appear in Table 1.

Discussion

Ventilation

It can be seen from Table 1 that carbon dioxide levels were below 800 ppm (parts per million) in all areas surveyed, indicating adequate air exchange at the time of the assessment.  The HVAC system consists of nine rooftop air handling units (AHUs) (Picture 2), which draw in outside air through air intakes and distribute it to occupied areas via ceiling-mounted air diffusers (Picture 3).  Return air is drawn into a plenum above the ceiling tiles through passive grills commonly referred to as “egg-crates” and ducted back to the rooftop AHUs (Picture 4).  Occupants in several areas complained of “dead air” and/or lack of airflow coming from their vents.  Thermostats that control the HVAC system have fan settings of “on” and “automatic”.  The majority of thermostats were set to the fan “auto” setting (Picture 5).  The “automatic” setting on the thermostat activates the HVAC system at a preset temperature.  Once the preset temperature is reached, the HVAC system is deactivated, whereas the fan “on” setting provides continuous airflow, which is recommended by the MDPH.

Other interferences with airflow were observed in the form of modifications to HVAC components.  In several areas, supply diffusers were sealed with cardboard/paper and duct tape (Pictures 6 and 7).  This alteration can create an imbalance in the system, resulting in uneven heating/cooling conditions leading to occupant discomfort.  In one extreme case, an air diffuser had been removed from the ceiling tile system and the space was sealed, leaving the operating diffuser in the ceiling plenum (Pictures 8 and 9).  This is problematic for several reasons: 1) it can pressurize the ceiling plenum, forcing any accumulated dust, debris, fiberglass fibers, etc. into occupied areas; 2) the ceiling plenum is designed to be depressurized to provide exhaust ventilation; and 3) interference with the balance of the system.

Occupants also expressed concerns about the frequency of filter changes in AHUs.  The HVAC system at the DEP SERO has a two-tiered filtration system.  Outside air is drawn into the AHUs through wire mesh pre-filters mounted on the air intakes (Pictures 2 and 10).  Air is then drawn through a bank of pleated air filters located inside the unit.  The HVAC system is reportedly maintained by a private HVAC engineering firm, who are reportedly change filters four times a year.  BEH staff visited the roof to examine rooftop AHUs and observed stickers on the units recommending that filters be changed every three months (Picture 11).  The last filter change reportedly occurred in August 2008, with the next filter change scheduled for November 2008.  BEH staff opened the AHUs to check filters and found them to be relatively clean and correctly installed (Picture 12).

To maximize air exchange, the MDPH recommends that both supply and exhaust ventilation operate continuously during periods of occupancy.  In order to have proper ventilation with a mechanical ventilation system, the systems must be balanced subsequent to installation to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room.  It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).  The date of the last balancing of these systems was not available at the time of the assessment.

The Massachusetts Building Code requires that each room have a minimum ventilation rate of 20 cubic feet per minute (cfm) per occupant of fresh outside air or openable windows (SBBRS, 1997; BOCA, 1993).  The ventilation must be on at all times that the room is occupied.  Providing adequate fresh air ventilation with open windows and maintaining the temperature in the comfort range during the cold weather season is impractical.  Mechanical ventilation is usually required to provide adequate fresh air ventilation.

Carbon dioxide is not a problem in and of itself.  It is used as an indicator of the adequacy of the fresh air ventilation.  As carbon dioxide levels rise, it indicates that the ventilating system is malfunctioning or the design occupancy of the room is being exceeded.  When this happens, a buildup of common indoor air pollutants can occur, leading to discomfort or health complaints.  The Occupational Safety and Health Administration (OSHA) standard for carbon dioxide is 5,000 parts per million parts of air (ppm).  Workers may be exposed to this level for 40 hours/week, based on a time-weighted average (OSHA, 1997).

The MDPH uses a guideline of 800 ppm for publicly occupied buildings.  A guideline of 600 ppm or less is preferred in schools due to the fact that the majority of occupants are young and considered to be a more sensitive population in the evaluation of environmental health status.  Inadequate ventilation and/or elevated temperatures are major causes of complaints such as respiratory, eye, nose and throat irritation, lethargy and headaches.  For more information concerning carbon dioxide, please see Appendix A.

Temperature readings in the building ranged from 60o F to 73 o F, which were below or at the lower end of the MDPH recommended comfort guidelines in the majority of areas surveyed.  The MDPH recommends that indoor air temperatures be maintained in a range of 70o F to 78o F in order to provide for the comfort of building occupants.  In many cases concerning indoor air quality, fluctuations of temperature in occupied spaces are typically experienced, even in a building with an adequate fresh air supply.  As discussed earlier, airflow and temperature control complaints were expressed by occupants in several areas (as evidenced by blockage of vents).

The relative humidity measurements in the building ranged from 30 to 48 percent, which were below the MDPH comfort range in the majority of areas during the assessment.  The MDPH recommends a comfort range of 40 to 60 percent for indoor air relative humidity.  Relative humidity levels in the building would be expected to drop during the winter months due to heating.  The sensation of dryness and irritation is common in a low relative humidity environment.  Low relative humidity is a very common problem during the heating season in the northeast part of the United States.

Microbial/Moisture Concerns

Several areas had evidence of water penetration.  Water-damaged gypsum wallboard and peeling paint was observed below the skylight in the 2nd floor foyer (Picture 13).  Water stained ceiling tiles were also seen in a number of areas (Table 1/Pictures 14 through 16), which may indicate current or historic roof/plumbing leaks.  At the time of the assessment building management was working with their HVAC vendor to identify possible leaks around rooftop ventilation units, which was evidenced by water hoses with pressurized nozzles on the roof.

BEH staff removed ceiling tiles in a number of areas impacted by water penetration for examination.  All areas appeared dry at the time of the assessment and no visible mold growth and/or associated odors were observed/detected.  Missing/damaged pipe insulation was observed above water stained ceiling tiles in the IT/network office (Pictures 17 and 18), which could provide a source of condensation.

BEH staff also conducted moisture testing of carpeting, ceiling tiles and gypsum wallboard in areas that had visible water damage or had reportedly become wet due to previous leaks (Table 1).  In order for building materials to support mold growth, a source of water exposure is necessary.  Identification and elimination of water moistening building materials is necessary to control mold growth.  Materials with increased moisture content over normal concentrations may indicate the possible presence of mold growth.  All porous materials testing in these areas were found to have low (i.e., normal) moisture content at the time of the assessment.  Moisture content of materials measured is a real-time measurement of the conditions present at the time of the assessment.

The US Environmental Protection Agency and the American Conference of Governmental Industrial Hygienists (ACGIH) recommends that porous materials (carpeting, ceiling tiles, etc.) be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2001; ACGIH, 1989).  If porous materials are not dried within this time frame, mold growth may occur.  Water-damaged porous materials cannot be adequately cleaned to remove mold growth.  The application of a mildewcide to moldy porous materials is not recommended.

Plants were observed in several areas.  Plants, soil and drip pans can serve as sources of mold/bacterial growth.  Plants should be properly maintained, over-watering of plants should be avoided and drip pans should be inspected periodically for mold growth (Pictures 19 through 21).  Plants in one area were located on top of paper towels (Table 1/Picture 22).  Paper towels are a porous material that can provide a medium for mold growth, especially if wetted repeatedly.

Space between the sink countertop and backsplash were noted in kitchen/break area (Picture 23).  Improper drainage or sink overflow can lead to water penetration of countertop wood, the cabinet interior and areas behind cabinets.  Like other porous materials, if these materials become wet repeatedly they can provide a medium for mold growth.

Other IAQ Evaluations

Indoor air quality can be negatively influenced by the presence of respiratory irritants, such as products of combustion.  The process of combustion produces a number of pollutants.  Common combustion emissions include carbon monoxide, carbon dioxide, water vapor and smoke (fine airborne particle material).  Of these materials, exposure to carbon monoxide and particulate matter with a diameter of 2.5 micrometers (μm) or less (PM2.5) can produce immediate, acute health effects upon exposure.  To determine whether combustion products were present in the building, BEH staff obtained measurements for carbon monoxide and PM2.5.

Carbon Monoxide

Carbon monoxide is a by-product of incomplete combustion of organic matter (e.g., gasoline, wood and tobacco).  Exposure to carbon monoxide can produce immediate and acute health affects.  Several air quality standards have been established to address carbon monoxide and prevent symptoms from exposure to these substances.  The MDPH established a corrective action level concerning carbon monoxide in ice skating rinks that use fossil-fueled ice resurfacing equipment.  If an operator of an indoor ice rink measures a carbon monoxide level over 30 ppm, taken 20 minutes after resurfacing within a rink, that operator must take actions to reduce carbon monoxide levels (MDPH, 1997).

The American Society of Heating Refrigeration and Air-Conditioning Engineers (ASHRAE) has adopted the National Ambient Air Quality Standards (NAAQS) as one set of criteria for assessing indoor air quality and monitoring of fresh air introduced by HVAC systems (ASHRAE, 1989).  The NAAQS are standards established by the US EPA to protect the public health from six criteria pollutants, including carbon monoxide and particulate matter (US EPA, 2006).  As recommended by ASHRAE, pollutant levels of fresh air introduced to a building should not exceed the NAAQS levels (ASHRAE, 1989).  The NAAQS were adopted by reference in the Building Officials & Code Administrators (BOCA) National Mechanical Code of 1993 (BOCA, 1993), which is now an HVAC standard included in the Massachusetts State Building Code (SBBRS, 1997).  According to the NAAQS, carbon monoxide levels in outdoor air should not exceed 9 ppm in an eight-hour average (US EPA, 2006).

Carbon monoxide should not be present in a typical, indoor environment.  If it is present, indoor carbon monoxide levels should be less than or equal to outdoor levels.  On the day of assessment, outdoor carbon monoxide concentrations were non-detect (ND) to 3 ppm (Table 1).  No detectable levels of carbon monoxide were measured in the building at the time of the assessment (Table 1).

Particulate Matter (PM2.5)

The US EPA has established NAAQS limits for exposure to particulate matter.  Particulate matter is airborne solids that can be irritating to the eyes, nose and throat.  The NAAQS originally established exposure limits to particulate matter with a diameter of 10 μm or less (PM10).  According to the NAAQS, PM10 levels should not exceed 150 microgram per cubic meter (μg/m3) in a 24-hour average (US EPA, 2006).  These standards were adopted by both ASHRAE and BOCA.  Since the issuance of the ASHRAE standard and BOCA Code, US EPA established a more protective standard for fine airborne particles.  This more stringent PM2.5 standard requires outdoor air particle levels be maintained below 35 μg/m3 over a 24-hour average (US EPA, 2006).  Although both the ASHRAE standard and BOCA Code adopted the PM10 standard for evaluating air quality, MDPH uses the more protective PM2.5 standard for evaluating airborne particulate matter concentrations in the indoor environment.

Outdoor PM2.5 concentrations were measured at 2 μg/m3 (Table 1).  PM2.5 levels measured indoors ranged from 1 to 4 μg/m3 (Table 1).  Both indoor and outdoor PM2.5 levels were well below the NAAQS PM2.5 level of 35 μg/m3.  Frequently, indoor air levels of particulates (including PM2.5) can be at higher levels than those measured outdoors.  A number of mechanical devices and/or activities that occur in buildings can generate particulate during normal operations.  Sources of indoor airborne particulates may include but are not limited to particles generated during the operation of fan belts in the HVAC system, cooking in stoves and microwave ovens; use of photocopiers, fax machines and computer printing devices; operation of an ordinary vacuum cleaner and heavy foot traffic indoors.

Total Volatile Organic Compounds (TVOCs)

Indoor air concentrations can be greatly impacted by the use of products containing volatile organic compounds (VOCs).  VOCs are carbon-containing substances that have the ability to evaporate at room temperature.  Frequently, exposure to low levels of total VOCs (TVOCs) may produce eye, nose, throat and/or respiratory irritation in some sensitive individuals.  For example, chemicals evaporating from a paint can stored at room temperature would most likely contain VOCs.  In an effort to determine whether measurable levels of VOCs were present in the building, air monitoring for TVOCs was conducted.

Outdoor air samples were taken for comparison.  Outdoor TVOC concentrations ranged from ND to 0.2 ppm (Table 1).  Indoor TVOC concentrations were ND in all areas surveyed at the time of the assessment (Tables 1 and 2).  Although no measurable levels of VOCs were detected during the assessment, a number of VOC-containing materials were noted in the building.

Several offices and meeting rooms contained dry erase boards and related materials.  Materials such as dry erase markers and dry erase board cleaners may contain VOCs, such as methyl isobutyl ketone, n-butyl acetate and butyl-cellusolve (Sanford, 1999), which can be irritating to the eyes, nose and throat.  Containers of VOC-containing cleaning materials were observed to clean employee work areas (Picture 24).  These materials contain several VOCs (e.g., isopropyl alcohol and monoethanolamine) that can be irritating to the eyes, nose and throat (3M, 2000).

The second floor copy room is not equipped with local exhaust ventilation to help reduce excess heat and odors.  Photocopiers can produce VOCs, waste heat and ozone, particularly if the equipment is older and in frequent use.  Ozone is a respiratory irritant (Schmidt Etkin, 1992).

Other Conditions

Other conditions that can affect indoor air quality were observed during the assessment.  A number of supply diffusers, return grates, exhaust vents in restrooms and personal fans were observed to have accumulated dust/debris (Pictures 3, 25 and 26).  If exhaust vents are not functioning, backdrafting can occur, which can re-aerosolize accumulated dust particles.  Re-activated supply vents and fans can also aerosolize dust accumulated on vents/fan blades.

In a several areas, items were observed on the floor, windowsills, tabletops, counters, bookcases and desks (Pictures 27 and 28).  The large number of items on flat surfaces provides a source for dusts to accumulate and makes it difficult for custodial staff to clean.  Items should be relocated and/or be cleaned periodically to avoid excessive dust build up.

Finally, florescent light fixtures were missing covers in a number of areas throughout the building (Picture 29 and 30).  Fixtures should be equipped with access covers installed with bulbs fully secured in their sockets.  Breakage of glass can cause injuries and may release mercury and/or other hazardous compounds.

Conclusions/Recommendations

As indicated, the request for assistance was prompted due to employee concerns of a possible connection between heart viruses in occupants and environmental conditions in the building, as well as general indoor air quality and comfort complaints.  While potential indoor air quality problems have been identified in this office, these issues are not likely to be related to the incidence of heart conditions among DEP SERO staff.  Such air quality issues can, however, lead to complaints of poor airflow and comfort issues/symptoms (e.g., headaches, upper respiratory problems and allergies).  If concerns relative to heart viruses or other conditions continue, MDEP should request a confidential medical consultation from MDPH physician consultants at the Bureau of Environmental Health.

In view of the findings at the time of the visit, the following recommendations are made:

- Operate the HVAC system continuously in the fan “on” mode during periods of occupancy to maximize air exchange.

- Remove obstructions from air diffusers.  To improve thermal comfort/temperature control it is highly recommended that SERO staff work in conjunction with building management and their HVAC vendor to examine the configuration of floor space and the placement of thermostats/sensors/diffusers.

- Improve communication between building management/maintenance and DEP staff regarding HVAC maintenance and filter change frequency.

- Consider adopting a balancing schedule of every 5 years for all mechanical ventilation systems, as recommended by ventilation industrial standards (SMACNA, 1994).

- For buildings in New England, periods of low relative humidity during the winter are often unavoidable.  Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low.  To control for dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended.  Drinking water during the day can help ease some symptoms associated with a dry environment (e.g., throat and sinus irritations).

- Continue with plans to investigate roof/HVAC leaks, make repairs as needed.

- Remove/replace water damaged ceiling tiles.  Examine the areas above and around for mold growth.  Disinfect areas of water leaks with an appropriate antimicrobial.

- Make repairs to pipe insulation above ceiling tiles in IT/Network office.

- Avoid over watering of plants.  Ensure flat surfaces around plants are free of potting soil and other plant debris.  Examine drip pans periodically for mold growth and disinfect with an appropriate antimicrobial where necessary.  Do not place plants on porous materials (e.g., paper/cardboard).  Consider reducing number of plants in some areas.

- Seal areas around sinks to prevent water-damage to the interior of cabinets and adjacent wallboard.

- Relocate photocopiers or consider installing local exhaust ventilation in photocopier rooms.

- Clean air diffusers, exhaust/return vents and personal fans periodically of accumulated dust.

- Relocate or consider reducing the amount of materials stored on flat surfaces to allow for more thorough cleaning.  Clean items regularly with a wet cloth or sponge to prevent excessive dust build-up.

- Discontinue the use of VOC-containing cleaners.  Less irritating materials, (soap and water) may suffice to clean in these areas.

- Replace all covers for florescent light fixtures.

- Refer to resource manuals and other related indoor air quality documents for further building-wide evaluations and advice on maintaining public buildings.  Copies of these materials are located on the MDPH’s website: http://mass.gov/dph/iaq.

References

3M 2000.  Material Safety Data Sheet (MSDS Document No: 10-0157-7).  3M Brand Desk and Office Cleaner 573.  Minnesota Mining and Manufacturing Company.  St. Paul, Minnesota.

ACGIH.  1989.  Guidelines for the Assessment of Bioaerosols in the Indoor Environment.  American Conference of Governmental Industrial Hygienists, Cincinnati, OH.

ASHRAE.  1989.  ASHRAE Standard: Ventilation for Acceptable Indoor Air Quality.  Sections 5.11, 5.12.  American Society of Heating, Refrigerating and Air-Conditioning Engineers, Inc.  Atlanta, GA.

BOCA.  1993.  The BOCA National Mechanical Code/1993.  8th ed.   Building Officials and Code Administrators International, Inc., Country Club Hill, IL.

MDPH.  1993.  Indoor Air Quality Assessment.  Department of Environmental Protection, Southeast Regional Office, Lakeville, MA.  Massachusetts Department of Public Health, Bureau of Environmental Health Assessment, Boston, MA.  August, 1993.

MDPH.  1997.  Requirements to Maintain Air Quality in Indoor Skating Rinks (State Sanitary Code, Chapter XI).  105 CMR 675.000.  Massachusetts Department of Public Health, Boston, MA.

OSHA.  1997.  Limits for Air Contaminants.  Occupational Safety and Health Administration.  Code of Federal Regulations.  29 C.F.R 1910.1000 Table Z-1-A.

Sanford. 1999.  Material Safety Data Sheet (MSDS No: 198-17).  Expo( Dry Erase Markers Bullet, Chisel, and Ultra Fine Tip.  Sanford Corporation.  Bellwood, IL.

SBBRS.  1997.  Mechanical Ventilation.  State Board of Building Regulations and Standards.  Code of Massachusetts Regulations.  780 CMR 1209.0.

Schmidt Etkin, D.  1992.  Office Furnishings/Equipment & IAQ Health Impacts, Prevention & Mitigation.  Cutter Information Corporation, Indoor Air Quality Update, Arlington, MA.

SMACNA.  1994.  HVAC Systems Commissioning Manual.  1st ed.  Sheet Metal and Air Conditioning

US EPA.  2001.  “Mold Remediation in Schools and Commercial Buildings”.  Office of Air and Radiation, Indoor Environments Division, Washington, DC.  EPA 402-K-01-001.  March 2001.  Available at: http://www.epa.gov/mold/mold_remediation.html.

US EPA.  2006.  National Ambient Air Quality Standards (NAAQS).  US Environmental Protection Agency, Office of Air Quality Planning and Standards, Washington, DC.  http://www.epa.gov/air/criteria.html.

Picture 1

Exterior Configuration of DEP SERO, Note Two Wings off Central Foyer/Main Entrance

Picture 2

Rooftop Air Handling Units, Metal Mesh Pre-Filters Indicated by Arrow

Picture 3

Ceiling-Mounted Air Diffuser, Note Dust/Debris Accumulation

Picture 4

Ceiling-Mounted Return Grill “Egg-Crate”

Picture 5

Digital Thermostat, Note Fan is set to “Auto” Position (Center)

Picture 6

Supply Diffuser Sealed With Cardboard and Tape

Picture 7

Supply Diffuser Sealed With Paper and Duct Tape

Picture 8

Area Where Supply Diffuser was Removed and Replaced by Tile

Picture 9

Operating Supply Diffuser above Ceiling Tile System Pressurizing Ceiling Plenum

Picture 10

Metal Mesh Pre-Filters in Rooftop Air Handling Units

Picture 11

Sticker on AHU Indicating Manufacture’s Suggested Filter Changes of Every 3 Months

Picture 12

Bank of Pleated Filters in Rooftop AHUs

Picture 13

Water Damaged Gypsum Wallboard below Skylight in 2nd Floor Foyer

Picture 14

Water Damaged Ceiling Tiles

Picture 15

Water Damaged Ceiling Tiles

Picture 16

Water Damaged Ceiling Tiles in IT/Network Office

Picture 17

Missing Pipe Insulation over Water Damaged Ceiling Tiles in IT/Network Office,

Note Exposed Copper Piping

Picture 18

Missing Pipe Insulation over Water Damaged Ceiling Tiles in IT/Network Office,

Note Exposed Copper Piping

Picture 19

Plants on Work Station Divider, Note Potting Soil and Debris on Flat Surfaces

Picture 20

Drip Pan with Green Wet Material, Indicating Likely Mold Growth

Picture 21

Wet Drip Pan, With Accumulated Material

Picture 22

Plant on Wet Paper Towels

Picture 23

Space between Sink Backsplash and Countertop

Picture 24

VOC-Containing Cleaner, Note Warning at Bottom of Spray Can “May Cause Eye Irritation”

Picture 25

Accumulated Dust/Debris on Fan Cage/Blades

Picture 26

Accumulated Dust/Debris on Exhaust Vent

Picture 27

Accumulated Items in Work Station

Picture 28

Accumulated Items on Flat Surfaces

Picture 29

Missing Light Cover, Exposing Fluorescent Bulbs

Picture 30

Missing Light Cover, Exposing Fluorescent Bulbs

| Location/ Room | Occupants in Room | Temp (°F) | Relative Humidity (%) | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | PM2.5 (µg/m3) | TVOCs (ppm) | Windows Openable | Ventilation | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| Background |  | 53 | 55 | 359 | ND – 3 | 2 | ND – 0.1 |  |  |  | Moderate traffic/tractor trailers |
| 1104 – 1107 | 3 | 69 | 36 | 668 | ND | 3 | ND | N | Y | Y | Thermostat set to “Auto” Fan |
| 1108 – 1111 | 0 | 72 | 33 | 662 | ND | 4 | ND | N | Y | Y | Plants |
| 1112 – 1113 1126 – 1128 | 1 | 72 | 31 | 579 | ND | 3 | ND | N | Y | Y |  |
| 1115 – 1116 | 1 | 71 | 31 | 576 | ND | 3 | ND | N | Y | Y |  |
| 1117 | 0 | 72 | 31 | 579 | ND | 3 | ND | N | Y | Y | Broken light cover; DO |
| 1119 – 1120 | 0 | 72 | 31 | 572 | ND | 3 | ND | N | Y | Y |  |
| 1122 | 0 | 72 | 30 | 549 | ND | 2 | ND | N | Y | Y | Insects in light |
| 1123 – 1125 | 2 | 73 | 30 | 560 | ND | 3 | ND | N | Y | Y | DO; PF |
| 1130 | 0 | 71 | 30 | 584 | ND | 3 | ND | N | Y | Y | PC |
| 1202 | 2 | 66 | 33 | 590 | ND | 3 | ND | N | Y passive | Y | AC on wall |
| 1203 | 0 | 66 | 33 | 587 | ND | 3 | ND | N | Y | Y | WD CTs; missing/damaged insulation on water pipes above CTs |
| 1211 | 1 | 68 | 35 | 629 | ND | 2 | ND | N | Y | Y | DEM; 3M Cleaner |
| 1213/1217 | 2 | 68 | 34 | 585 | ND | 2 | ND | N | Y | Y | DEM |
| 1215 | 0 | 68 | 34 | 560 | ND | 2 | ND | N | Y | Y |  |
| 1221 Reception | 1 | 61 | 38 | 541 | ND | 2 | ND | N | Y | Y |  |
| 1222 | 1 | 66 | 37 | 527 | ND | 2 | ND | N | Y | Y | PC; computers; printers |
| 1227 | 1 | 67 | 37 | 478 | ND | 1 | ND | N | Y | Y |  |
| 2103 – 2105 | 1 | 68 | 33 | 546 | ND | 3 | ND | N | Y | Y |  |
| 2104 | 0 | 68 | 34 | 533 | ND | 2 | ND | N | Y | Y | DO |
| Copy Room | 0 | 69 | 33 | 556 | ND | 3 | ND | N | Y | Y | 2 WD CTs |
| 2106 | 0 | 68 | 32 | 526 | ND | 2 | ND | N | Y | Y | DO |
| 2106 | 0 | 70 | 32 | 534 | ND | 2 | ND | N | Y | Y | PF |
| 2107 – 2108 | 1 | 68 | 33 | 566 | ND | 3 | ND | N | Y | Y | Plants |
| 2109 | 0 | 68 | 33 | 551 | ND | 2 | ND | N | Y | Y | DO |
| 2110 – 2114 | 0 | 69 | 32 | 518 | ND | 2 | ND | N | Y | Y |  |
| 2111 | 0 | 68 | 32 | 546 | ND | 3 | ND | N | Y | Y | DO |
| Library | 0 | 70 | 31 | 506 | ND | 2 | ND | N | Y | Y | 3 WD CTs |
| 2115 – 2118 | 0 | 72 | 31 | 535 | ND | 3 | ND | N | Y | Y | 1 WD CT |
| 2119 – 2141 | 0 | 72 | 31 | 521 | ND | 2 | ND | N | Y | Y | Plants |
| 2120 | 0 | 72 | 30 | 560 | ND | 2 | ND | N | Y | N | PF |
| 2122 | 0 | 67 | 33 | 522 | ND | 2 | ND | N | Y | Y | WD CT; Accumulated dust on flat surfaces |
| 2123 | 1 | 70 | 32 | 519 | ND | 3 | ND | N | Y | Y |  |
| 2123 – 2126 | 1 | 69 | 32 | 521 | ND | 3 | ND | N | Y | Y |  |
| 2125 | 0 | 69 | 31 | 498 | ND | 2 | ND | N | Y | Y |  |
| 2127 – 2129 | 1 | 70 | 32 | 554 | ND | 2 | ND | N | Y | Y | Plants |
| 2128 | 1 | 70 | 33 | 566 | ND | 3 | ND | N | Y | Y | Plants; DO |
| 2130 | 0 | 70 | 32 | 492 | ND | 3 | ND | N | Y | Y | DO |
| 2131 – 2133 | 0 | 69 | 33 | 511 | ND | 2 | ND | N | Y | Y |  |
| 2132 | 1 | 69 | 32 | 542 | ND | 3 | ND | N | Y | Y | DO |
| 2134 | 0 | 69 | 32 | 494 | ND | 2 | ND | N | Y | Y | PF; DO |
| 2135 – 2136 | 0 | 69 | 34 | 503 | ND | 3 | ND | N | Y | Y |  |
| 2137 – 2139 | 3 | 70 | 32 | 524 | ND | 2 | ND | N | Y | Y |  |
| 2138 – 2140 | 1 | 71 | 31 | 553 | ND | 2 | ND | N | Y | Y |  |
| 2142 | 0 | 72 | 30 | 523 | ND | 2 | ND | N | Y | Y | DO |
| 2143 | 1 | 71 | 31 | 545 | ND | 3 | ND | N | Y | N | WD CT |
| 2144 | 0 | 71 | 31 | 546 | ND | 3 | ND | N | Y | Y | Plants; DO |
| 2145 | 0 | 71 | 30 | 536 | ND | 3 | ND | N | Y | N | DO |
| 2200 | 0 | 70 | 32 | 534 | ND | 3 | ND | N | Y | Y |  |
| 2201 | 0 | 72 | 32 | 504 | ND | 3 | ND | N | Y | Y | DO |
| 2204 – 2207 | 3 | 70 | 31 | 545 | ND | 3 | ND | N | Y | Y |  |
| 2208 – 2209; 2214 | 0 | 70 | 31 | 502 | ND | 3 | ND | N | Y | Y |  |
| 2215 | 0 | 69 | 31 | 501 | ND | 3 | ND | N | Y | Y | PF; DO |
| 2216 – 2219 | 1 | 70 | 31 | 524 | ND | 3 | ND | N | Y | Y | Plants |
| 2220 – 2221 | 2 | 70 | 31 | 536 | ND | 3 | ND | N | Y | Y |  |
| 2222 – 2223 | 3 | 70 | 32 | 559 | ND | 3 | ND | N | Y | Y |  |
| 2224 2235 2246 | 1 | 72 | 31 | 542 | ND | 4 | ND | N | Y | Y |  |
| 2228 | 0 | 69 | 30 | 467 | ND | 3 | ND | N | Y screened | Y |  |
| 2229 – 2230 | 0 | 69 | 30 | 498 | ND | 3 | ND | N | Y | Y | Plants on paper towels; Soil and debris on flat surfaces |
| 2231 | 0 | 72 | 31 | 512 | ND | 2 | ND | N | Y | N | PC |
| 2233 | 1 | 72 | 33 | 630 | ND | 3 | ND | N | Y | Y |  |
| 2236 – 2239 | 4 | 71 | 30 | 534 | ND | 2 | ND | N | Y | Y | Plants |
| 2241 | 0 | 71 | 32 | 572 | ND | 3 | ND | N | Y blocked | Y | 1 WD CT; plants |
| 2242 – 2246 | 2 | 71 | 31 | 514 | ND | 3 | ND | N | Y | Y | 2 WD CTs |
| 2247 | 0 | 72 | 31 | 466 | ND | 3 | ND | N | Y | Y |  |
| 2248 | 0 | 71 | 31 | 485 | ND | 4 | ND | N | N | N | Supply air diffuser removed and replaced with CT; 1 WD CT; DO |
| 2249 – 2251 | 0 | 71 | 30 | 523 | ND | 3 | ND | N | Y | Y | Plants |
| 2254 – 2255 | 3 | 71 | 30 | 567 | ND | 3 | ND | N | Y | Y | Supply diffuser in plenum above CTs; missing light cover |
| 2257 | 0 | 70 | 30 | 480 | ND | 3 | ND | N | Y | Y | Plants; 1 WD CT; DO |
| 2258 | 1 | 69 | 30 | 488 | ND | 3 | ND | N | Y | Y |  |
| 2260 | 0 | 72 | 30 | 493 | ND | 3 | ND | N | Y | Y |  |
| Conference Room 1st Floor | 0 | 60 | 48 | 661 | ND | 1 | ND | N | Y | Y dust | Missing light cover |
| Entrance Foyer | 5 | 67 | 35 | 602 | ND | 4 | ND | N | Y | Y | WD CTs-painted; Observed conditions above CTs: dry-no visible mold growth, sprinkler pipes |
| Kitchen | 1 | 68 | 36 | 512 | ND | 2 | ND | N | Y dust | Y | Space between sink and backsplash; microwave; toaster; coffee maker; refrigerator |