# Background

| Building: | Department of Revenue (DOR) |
| --- | --- |
| Address: | 100 Cambridge Street, Boston, MA |
| Assessment Requested by: | Joshua Martin, Deputy Director, Office of Facilities Management, Massachusetts DOR |
| Reason for Request: | Lease renewal indoor air quality (IAQ) status report |
| Date of Assessment: | January 11, 2017 |
| Massachusetts Department of Public Health/Bureau of Environmental Health (MDPH/BEH) Staff Conducting Assessment: | Ruth Alfasso, Environmental Engineer/Inspector, IAQ Program Cory Holmes, Environmental Analyst/Inspector, IAQ Program |
| Building Description: | These offices are located on the 4-8th floor of the Saltonstall Building, a 1960s era high-rise building in downtown Boston. |
| Building Population: | Approximately 300 employees on 4 floors |
| Windows: | Not openable |

# Methods

Please refer to the IAQ Manual for methods, sampling procedures, and interpretation of results (MDPH, 2015).

# IAQ Testing Results

The following is a summary of indoor air testing results (Table 1).

- Carbon dioxide levels were below 800 parts per million (ppm) in all but two areas assessed, indicating adequate fresh air in the space.

- Temperature was within the recommended range of 70°F to 78°F in all areas assessed.

- Relative humidity was below the recommended range of 40% to 60% in all areas assessed.

- Carbon monoxide levels were non-detectable in all indoor areas assessed.

- Fine particulate matter (PM2.5) concentrations measured were below the National Ambient Air Quality Standard (NAAQS) level of 35 μg/m3 in all areas assessed.

## Ventilation

A heating, ventilating, and air conditioning (HVAC) system has several functions. First, it provides heating and, if equipped, cooling. Second, it is a source of fresh air. Finally, an HVAC system will dilute and remove normally occurring indoor environmental pollutants by not only introducing fresh air, but also filtering the airstream and ejecting stale air to the outdoors via exhaust ventilation. Even if an HVAC system is operating as designed, point sources of respiratory irritation may exist and affect symptoms in sensitive individuals. The following analysis examines and identifies components of the HVAC system and likely sources of respiratory irritant/allergen exposure due to water damage, aerosolized dust, and/or chemicals found in the indoor environment.

Fresh air is provided by air handling units (AHUs). Air from the AHUs is filtered, heated/cooled, and delivered to rooms via ducted supply vents (Picture 1). Air is returned/exhausted through vents located around lights (Picture 2). In a few areas, vents were covered by paper, most likely to reduce drafts from the airstreams upon occupants (Picture 3). In order to operate properly, supply and exhaust vents should be unobstructed.   It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).

Along one side of the building, sunlight could be seen streaming in through the windows. Adjustable blinds should be used to control solar gain and assist with temperature control and reducing glare.

## Microbial/Moisture Concerns

Plants were observed in office areas (Table 1; Picture 4). Plants can be a source of pollen and mold, which can be respiratory irritants to some individuals. Plants should be properly maintained and equipped with drip pans to prevent water damage to porous materials. Plants should also be located away from air diffusers to prevent the aerosolization of dirt, pollen, and mold.

Small refrigerators and water dispensers were observed in carpeted areas (Table 1; Picture 5). These appliances may spill or leak and lead to carpet damage and microbial growth. It is recommended that these appliances be located in areas without carpeting or on waterproof mats. Carpet squares could also be replaced with tile in areas where water dispensers and refrigerators are located. Some of the refrigerators were crowded with items, had an odor of spoiled food or had evidence of spills (Picture 6). Refrigerators should be kept clean to prevent odors and microbial growth.

## Other IAQ Evaluations

Exposure to low levels of total volatile organic compounds (TVOCs) may produce eye, nose, throat, and/or respiratory irritation in some sensitive individuals. To determine if VOCs were present, BEH/IAQ staff examined rooms for products containing VOCs. BEH/IAQ staff noted hand sanitizers, cleaners, air freshener products, and dry erase materials in use within the building (Pictures 7 and 8; Table 1). All of these products have the potential to be irritants to the eyes, nose, throat, and respiratory system of sensitive individuals.

Cooking equipment, including toasters, microwave ovens and coffee machines were located in various parts of the office space. The kitchens on each floor are not enclosed and do not have any direct-vented exhaust, which increases the chance of food odors permeating office areas. For example, the odor of toast was observed in office areas on the 7th floor. Food areas and cooking equipment need to be kept clean to prevent odors and pests.

The offices were mostly carpeted. Carpets should be cleaned annually (or semi-annually in soiled/high traffic areas) in accordance with Institute of Inspection, Cleaning and Restoration Certification (IICRC) recommendations, (IICRC, 2012).

In some areas, stored materials and accumulated items make it more difficult for custodial staff to clean. Items should be stored neatly and moved periodically to allow for wet wiping and vacuuming of surfaces.

Personal fans were observed in a number of areas. Fan blades to some of these units had settled dust, which can be reaerosolized when the fan is activated. Some supply vents were also dusty (Picture 1).

# Conclusions/Recommendations

Based on observations at the time of assessment, the following is recommended:

- Operate supply and exhaust ventilation in all areas during occupied periods.

- Unblock vents that are covered by paper. To improve comfort, redirect airflow away from occupants if feasible or reconfigure workspace/move building occupant to reduce discomfort due to airflow.

- Have the HVAC system balanced every 5 years in accordance with SMACNA recommendations (SMACNA, 1994).

- Use blinds to reduce solar heating and glare.

- For buildings in New England, periods of low relative humidity during the winter are often unavoidable. Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low. To control for dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended. Avoid the use of feather dusters. Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

- Keep indoor plants in good condition, avoid overwatering, and avoid placing them on porous items such as carpets or paper. Also, keep plants out of the air stream of supply vents.

- Consider locating refrigerators and water dispensers in non-carpeted areas or place on a waterproof mat.

- Clean refrigerator spills promptly and clean refrigerators out regularly to avoid odors and microbial growth.

- Reduce use of products containing VOCs including eliminating air freshening products.

- Ensure cooking areas/equipment are kept clean to prevent odors and pests. Consider reducing the number of areas where food is stored and locating them away from occupied areas.

- Change filters on AHUs on a regular schedule at least twice a year.

- Clean carpeting in accordance with IICRC recommendations (IICRC, 2012).

- Reduce accumulated materials on flat surfaces and store in an organized manner to allow for thorough cleaning.

- Clean the blades of personal fans, supply, and exhaust vents periodically to avoid aerosolizing dusts.

- Refer to resource manual and other related IAQ documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings. These documents are available at: http://mass.gov/dph/iaq.

# References

IICRC. 2012. Institute of Inspection, Cleaning and Restoration Certification. Carpet Cleaning: FAQ. Retrieved from http://www.iicrc.org/consumers/care/carpet-cleaning.

MDPH. 2015. Massachusetts Department of Public Health. Indoor Air Quality Manual: Chapters I-III. Available at: http://www.mass.gov/eohhs/gov/departments/dph/programs/environmental-health/exposure-topics/iaq/iaq-manual/.

SMACNA. 1994. HVAC Systems Commissioning Manual. 1st ed. Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

Picture 1

Supply vent, note dust/debris

Picture 2

Light fixture with exhaust vents around it

Picture 3

Paper obstructing supply vent

Picture 4

Plants in an office, in need of maintenance; also note food

Picture 5

Water dispenser on carpet

Picture 6

Refrigerator with evidence of spills and stained gasket

Picture 7

Cleaning products

Picture 8

Reed diffuser

| Location | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | Temp (°F) | Relative Humidity (%) | PM2.5 (µg/m3) | Occupants in Room | Windows Openable | Ventilation | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| Background | 360 | 1.0 | 58 | 26 | 10 |  |  |  |  | Mostly sunny |
| Mezzanine |
| Mailroom | 532 | ND | 73 | 27 | 4 | 1 | N | Y | Y | CPs, DEM |
| 5th floor |
| 1-5 cubes | 674 | ND | 73 | 24 |  | 1 | N | Y | Y |  |
| 6-10 cubes | 654 | ND | 74 | 24 | 3 | 4 | N | Y | Y | PF |
| 14-17 cubes | 657 | ND | 74 | 24 | 3 | 3 | N | Y | Y |  |
| 26-29 cubes | 653 | ND | 74 | 24 | 3 | 1 | N | Y | Y |  |
| 32-33 cubes | 626 | ND | 74 | 24 | 3 | 0 | N | Y | Y |  |
| 36-38 cubes | 641 | ND | 74 | 32 | 3 | 1 | N | Y | Y | PF |
| 39-40 cubes | 675 | ND | 75 | 23 | 4 | 1 | N | Y | Y |  |
| 45-46A cubes | 631 | ND | 74 | 23 | 3 | 2 | N | Y | Y | PF |
| 47-48 cubes | 650 | ND | 74 | 24 | 3 | 2 | N | Y | Y | PF |
| 50-52 cubes | 638 | ND | 74 | 24 | 4 | 3 | N | Y | Y |  |
| 53-57 cubes | 653 | ND | 74 | 24 | 4 | 1 | N | Y | Y |  |
| 67-73 cubes | 704 | ND | 74 | 24 | 4 | 0 | N | Y | Y |  |
| 77-81 cubes | 711 | ND | 74 | 24 | 4 | 3 | N | Y | Y |  |
| 85-89 cubes | 651 | ND | 74 | 24 | 4 | 5 | N | Y | Y | PF |
| 100-101 cubes | 664 | ND | 73 | 24 | 4 | 2 | N | Y | Y |  |
| 103-105 cubes | 704 | ND | 74 | 24 | 4 | 3 | N | Y | Y |  |
| 117-119 cubes | 675 | ND | 74 | 24 | 4 | 0 | N | Y | Y |  |
| 5-01K | 634 | ND | 74 | 24 | 3 | 1 | N | Y | Y | DEM |
| 5-05M | 614 | ND | 74 | 23 | 4 | 0 | N | Y | Y | DEM, PF |
| 5-06A | 666 | ND | 73 | 24 | 4 | 0 | N | Y | Y |  |
| 5-09B | 669 | ND | 74 | 24 | 4 | 1 | N | Y | Y | Dusty vents |
| 5-14A | 706 | ND | 74 | 25 | 4 | 1 | N | Y | Y | DEM |
| 5-16M | 668 | ND | 74 | 25 | 5 | 1 | N | Y | Y |  |
| 5-19M | 660 | ND | 74 | 24 | 4 | 1 | N | Y | Y |  |
| 5-22M | 653 | ND | 74 | 24 | 4 | 0 | N | Y | Y |  |
| 5-23B | 677 | ND | 74 | 24 | 4 | 1 | N | Y | Y | Dusty vents |
| 6th floor |
| 2-4 cubes | 694 | ND | 72 | 28 | 1 | 0 | N | Y | Y |  |
| 5-8 cubes | 681 | ND | 73 | 25 | 1 | 2 | N | Y | Y |  |
| 12-18 cubes | 750 | ND | 75 | 25 | 2 | 4 | N | Y | Y | PF - dusty |
| 25-29 | 701 | ND | 75 | 24 | 2 | 5 | N | Y | Y |  |
| 30-33 cubes | 676 | ND | 75 | 24 | 2 | 4 | N | Y | Y |  |
| 36-37 cubes | 666 | ND | 74 | 24 | 2 | 1 | N | Y | Y |  |
| 42-43 cubes | 688 | ND | 75 | 23 | 3 | 2 | N | Y | Y | PF |
| 44-46 cubes | 668 | ND | 75 | 23 | 3 | 1 | N | Y | Y |  |
| 48-51 cubes | 677 | ND | 75 | 23 | 3 | 3 | N | Y | Y |  |
| 56-59 cubes | 675 | ND | 74 | 24 | 3 | 0 | N | Y | Y | PF |
| 70-73 cubes | 640 | ND | 74 | 24 | 3 | 1 | N | Y | Y |  |
| 78-83 cubes | 664 | ND | 74 | 24 | 3 | 3 | N | Y | Y |  |
| 85 cube | 658 | ND | 74 | 24 | 3 | 1 | N | Y | Y |  |
| 88-91 cubes | 664 | ND | 74 | 24 | 3 | 1 | N | Y | Y | PF |
| 97-99 cubes | 698 | ND | 74 | 24 | 4 | 2 | N | Y | Y | Dusty vents |
| 6-01A | 698 | ND | 74 | 26 | 1 | 1 | N | Y | Y |  |
| 6-01G | 671 | ND | 75 | 24 | 2 | 0 | N | Y | Y |  |
| 6-01H | 651 | ND | 74 | 23 | 2 | 0 | N | Y | Y | DEM |
| 6-01J | 672 | ND | 74 | 25 | 2 | 0 | N | Y | Y | PF (dusty), plant, mini humidifier |
| 6-01M | 705 | ND | 74 | 24 | 2 | 0 | N | Y | Y |  |
| 6-03A | 700 | ND | 73 | 27 | 2 | 1 | N | Y | Y | PF |
| 6-04A | 699 | ND | 72 | 27 | 2 | 0 | N | Y | Y |  |
| 6-04G | 672 | ND | 74 | 24 | 2 | 2 | N | Y | Y | PC, PF |
| 6-06M | 662 | ND | 75 | 23 | 3 | 1 | N | Y | Y | PF |
| 6-10M | 679 | ND | 75 | 23 | 3 | 1 | N | Y | Y | PF |
| 6-11A | 714 | ND | 74 | 24 | 3 | 4 | N | Y | Y |  |
| 6-16J | 699 | ND | 75 | 23 | 2 | 0 | N | Y | Y | DEM, dusty vents |
| 6-17A conference room | 728 | ND | 74 | 24 | 4 | 0 | N | Y | Y | PC, PF |
| 6-19E | 706 | ND | 74 | 25 | 3 | 1 | N | Y | Y |  |
| 6-19J conference room | 664 | ND | 74 | 23 | 3 | 0 | N | Y | Y | DEM |
| 6-22M | 677 | ND | 74 | 24 | 3 | 1 | N | Y | Y | DEM, plants |
| 6-23C | 671 | ND | 74 | 24 | 3 | 0 | N | Y | Y |  |
| 6-24N | 678 | ND | 74 | 25 | 3 | 2 | N | Y | Y |  |
| Lumb office | 673 | ND | 74 | 25 | 4 | 1 | N | Y | Y |  |
| Reception | 728 | ND | 70 | 30 | 3 | 0 | N | Y | Y |  |
| 7th floor |
| 2-3 cubes | 729 | ND | 73 | 25 | 5 | 0 | N | Y | Y | DEM |
| 4-5 cubes | 718 | ND | 74 | 25 | 5 | 1 | N | Y | Y | DEM, AI |
| 8 cubes | 711 | ND | 74 | 24 | 4 | 1 | N | Y | Y |  |
| 11-14 cubes | 734 | ND | 75 | 25 | 6 | 3 | N | Y | Y | Plants |
| 19-21 cubes | 729 | ND | 75 | 25 | 5 | 0 | N | Y | Y | Fridge and toaster |
| 22 cubes | 712 | ND | 74 | 25 | 4 | 0 | N | Y | Y | Fridge on carpet, toaster |
| 25, 33 cubes | 716 | ND | 75 | 24 | 4 | 0 | N | Y | Y |  |
| 26-29 cubes | 712 | ND | 75 | 24 | 5 | 2 | N | Y | Y | CP |
| 34-36 cubes | 728 | ND | 75 | 24 | 5 | 1 | N | Y | Y | Coffee |
| 41-43 cubes | 726 | ND | 74 | 24 | 4 | 0 | N | Y | Y |  |
| 45-48 cubes | 700 | ND | 74 | 24 | 5 | 3 | N | Y | Y |  |
| 51-52 cubes | 718 | ND | 74 | 24 | 4 | 0 | N | Y | Y | PF, CP, food |
| 53-54 cubes | 704 | ND | 73 | 25 | 4 | 2 | N | Y | Y |  |
| 55-57 cubes | 719 | ND | 73 | 25 | 5 | 2 | N | Y | Y | PFs, CP, food |
| 7-01G | 721 | ND | 75 | 24 | 4 | 0 | N | Y | Y | Plant |
| 7-01M conference room | 694 | ND | 73 | 24 | 5 | 0 | N | Y | Y | DEM |
| 7-02A | 730 | ND | 74 | 25 | 4 | 0 | N | Y | Y | DO, DEM, HS |
| 7-03A | 752 | ND | 74 | 25 | 4 | 1 | N | Y | Y |  |
| 7-04A | 681 | ND | 74 | 25 | 4 | 1 | N | Y | Y |  |
| 7-05 | 660 | ND | 74 | 25 | 5 | 0 | N | Y | Y | DEM, DO |
| 7-05M | 714 | ND | 74 | 25 | 4 | 1 | N | Y | Y | Boxes |
| 7-06M | 753 | ND | 74 | 25 | 5 | 1 | N | Y | Y | Solar gain, PF, plants |
| 7-08M | 719 | ND | 73 | 28 | 3 | 0 | N | Y | Y |  |
| 7-09A | 776 | ND | 74 | 25 | 5 | 1 | N | Y | Y | DEM, DO, AI |
| 7-09B | 741 | ND | 74 | 24 | 5 | 0 | N | Y | Y | AI |
| 7-09J | 735 | ND | 73 | 26 | 3 | 0 | N | Y | Y | HS |
| 7-09M | 681 | ND | 74 | 25 | 3 | 0 | N | Y | Y | Food |
| 7-10A | 710 | ND | 74 | 25 | 4 | 0 | N | Y | Y |  |
| 7-10B | 751 | ND | 74 | 25 | 5 | 1 | N | Y | Y | Vent dusty, PF, DO |
| 7-10H | 729 | ND | 74 | 25 | 6 | 0 | N | Y | Y | Plant |
| 7-10J | 742 | ND | 74 | 25 | 3 | 0 | N | Y | Y | Food, reed AF |
| 7-10M | 718 | ND | 74 | 26 | 4 | 1 | N | Y | Y | Dried flowers |
| 7-11A | 744 | ND | 73 | 25 | 4 | 0 | N | Y | Y | PF, boxes |
| 7-11J | 695 | ND | 74 | 24 | 3 | 0 | N | Y | Y |  |
| 7-11M | 665 | ND | 74 | 24 | 4 | 0 | N | Y | Y | DO, PF |
| 7-12A | 710 | ND | 73 | 25 | 4 | 0 | N | Y | Y | DO, CP, DEM |
| 7-12B | 731 | ND | 73 | 24 | 6 | 1 | N | Y | Y | DO, PF |
| 7-12J | 687 | ND | 75 | 24 | 4 | 0 | N | Y | Y | Plants (need water), food |
| 7-12M | 677 | ND | 75 | 24 | 4 | 1 | N | Y | Y | DO, PF |
| 7-12M | 706 | ND | 74 | 24 | 5 | 1 | N | Y | Y |  |
| 7-13A | 733 | ND | 73 | 25 | 5 | 2 | N | Y | Y | Items |
| 7-13B | 717 | ND | 73 | 25 | 5 | 0 | N | Y | Y | Food, PF |
| 7-13M | 629 | ND | 75 | 24 | 7 | 2 | N | Y | Y | HS |
| 7-14A | 725 | ND | 73 | 25 | 5 | 2 | N | Y | Y | Vent blocked, food odors |
| 7-14M | 702 | ND | 76 | 24 | 4 | 0 | N | Y | Y | Vent partly covered |
| 7-15A | 705 | ND | 73 | 25 | 4 | 0 | N | Y | Y | DO, DEM, dried flowers |
| 7-15M | 658 | ND | 76 | 23 | 4 | 0 | N | Y | Y | PF, DO |
| 7-16M | 689 | ND | 77 | 23 | 5 | 0 | N | Y | Y |  |
| 7-17A | 678 | ND | 73 | 24 | 4 | 0 | N | Y | Y | Boxes on floor |
| 7-17A | 744 | ND | 73 | 25 | 4 | 0 | N | Y | Y | PF, coffee |
| 7-17J kitchen | 698 | ND | 76 | 23 | 6 | 0 | N | Y | Y | No local exhaust, toast odor, fridge with spills, microwave and toaster |
| 7-17M | 671 | ND | 76 | 23 | 4 | 1 | N | Y | Y | Items, area rug, AI |
| 7-18M | 738 | ND | 76 | 23 | 4 | 0 | N | Y | Y | AI, books |
| 7-19A | 742 | ND | 73 | 25 | 5 | 1 | N | Y | Y | DO, AI, DEM |
| 7-19H | 664 | ND | 74 | 24 | 4 | 0 | N | Y | Y | Dusty vent, AP |
| 7-19J | 840 | ND | 75 | 23 | 5 | 0 | n | y | Y |  |
| 7-19M | 799 | ND | 75 | 23 | 4 | 1 | N | Y | Y | CP, DO |
| 7-20A | 695 | ND | 73 | 25 | 5 | 1 | N | Y | Y |  |
| 7-20J | 705 | ND | 75 | 23 | 4 | 1 | N | Y | Y | DO |
| 7-20M | 697 | ND | 75 | 23 | 4 | 1 | N | Y | Y | AI and books and papers, DO |
| 7-21M | 679 | ND | 75 | 23 | 4 | 1 | N | Y | Y | PF, plant, DO |
| 7-22M | 687 | ND | 75 | 23 | 4 | 1 | N | Y | Y | DO |
| 7-23B | 643 | ND | 74 | 24 | 4 | 0 | N | Y | Y | HS, DEM |
| 7-23C | 648 | ND | 74 | 24 | 4 | 0 | N | Y | Y |  |
| 7-23D | 697 | ND | 74 | 25 | 4 | 0 | N | Y | Y | CP/AF, boxes on floor |
| 7-23E | 674 | ND | 74 | 24 | 4 | 1 | N | Y | Y | Boxes |
| 7-23F | 678 | ND | 74 | 24 | 4 | 0 | N | Y | Y | Dusty PF |
| 7-23H | 670 | ND | 74 | 24 | 5 | 2 | N | Y | Y | Plants |
| 7-23J | 690 | ND | 74 | 24 | 4 | 1 | N | Y | Y | PF, DEM, DO |
| 7-23M | 659 | ND | 74 | 23 | 4 | 0 | N | Y | Y |  |
| 7th floor IT room | 931 | ND | 74 | 25 | 4 | 0 | N | Y |  |  |
| Copy area | 644 | ND | 74 | 24 | 4 | 0 | N | Y | Y | PC, fridge on carpet |
| Copy area | 685 | ND | 73 | 25 | 4 | 0 | N | Y | Y | WC on carpet |
| Large copier | 660 | ND | 73 | 25 | 5 | 0 | N | Y | Y |  |
| Reception | 735 | ND | 73 | 24 | 5 | 0 | N | Y | Y |  |
| 8th floor |
| 1-2 cubes | 669 | ND | 73 | 25 | 5 | 1 | N | Y | Y |  |
| 1-6 cubes | 741 | ND | 74 | 25 | 5 | 0 | N | Y | Y |  |
| 7-8 cubes | 730 | ND | 73 | 25 | 5 | 2 | N | Y | Y |  |
| 9-11 cubes | 705 | ND | 74 | 24 | 5 | 2 | N | Y | Y |  |
| 12-19 cubes | 699 | ND | 75 | 24 | 4 | 0 | N | Y | Y | Solar gain |
| 20-22 cubes | 651 | ND | 75 | 23 | 4 | 0 | N | Y | Y | Solar gain |
| 24-22 cubes | 652 | ND | 75 | 24 | 5 | 2 | N | Y | Y | Plants, solar gain |
| 27-28 cubes | 645 | ND | 74 | 24 | 5 | 0 | N | Y | Y |  |
| 29-30 cubes | 672 | ND | 74 | 24 | 5 | 1 | N | Y | Y |  |
| 33-38 cubes | 631 | ND | 74 | 24 | 5 | 1 | N | Y | Y | PF, food, big printer |
| 40-49 cubes | 650 | ND | 74 | 24 | 5 | 3 | N | Y | Y | Plants |
| 48 cubes | 668 | ND | 74 | 24 | 5 | 0 | N | Y | Y |  |
| 50 cubes | 650 | ND | 74 | 24 | 5 | 0 | N | Y | Y |  |
| 51-52 cubes | 668 | ND | 74 | 24 | 7 | 0 | N | Y | Y |  |
| 53-54 cubes | 673 | ND | 74 | 24 | 5 | 1 | N | Y | Y |  |
| 55 cubes | 646 | ND | 74 | 24 | 6 | 0 | N | Y | Y |  |
| 8-01A | 642 | ND | 73 | 24 | 5 | 0 | N | Y | Y |  |
| 8-01B Commissioners conference room | 644 | ND | 73 | 24 | 5 | 0 | N | Y | Y |  |
| 8-01H | 625 | ND | 74 | 24 | 5 | 1 | N | Y | Y | DEM |
| 8-01J | 686 | ND | 74 | 24 | 5 | 1 | N | Y | Y |  |
| 8-01M | 631 | ND | 73 | 24 | 5 | 0 | N | Y | Y | DEM |
| 8-03A | 660 | ND | 74 | 24 | 5 | 2 | N | Y | Y | CP |
| 8-05A | 738 | ND | 74 | 24 | 5 | 0 | N | Y | Y | Fake plant, DEM, AF, CP |
| 8-05A | 669 | ND | 74 | 25 | 5 | 1 | N | Y | Y | Plant |
| 8-05B | 686 | ND | 74 | 25 | 6 | 1 | N | Y | Y |  |
| 8-05F | 673 | ND | 74 | 25 | 5 | 1 | N | Y | Y |  |
| 8-05G | 665 | ND | 74 | 24 | 5 | 1 | N | Y | Y | DEM |
| 8-05H | 708 | ND | 74 | 25 | 5 | 1 | N | Y | Y | DEM |
| 8-05J | 641 | ND | 73 | 25 | 5 | 1 | N | Y | Y |  |
| 8-05M | 645 | ND | 73 | 25 | 4 | 1 | N | Y | Y | DEM |
| 8-06B | 662 | ND | 74 | 24 | 5 | 0 | N | Y | Y |  |
| 8-06M | 659 | ND | 73 | 25 | 5 | 1 | N | Y | Y | CP, DEM |
| 8-07A | 640 | ND | 74 | 25 | 5 | 0 | N | Y | Y | DEM |
| 8-07M | 648 | ND | 73 | 25 | 5 | 0 | N | Y | Y | Plants, solar gain, DEM |
| 8-09A | 637 | ND | 74 | 25 | 5 | 1 | N | Y | Y | AF – reeds, flowers |
| 8-09M | 651 | ND | 75 | 25 | 5 | 0 | N | Y | Y | Solar gain |
| 8-10B | 648 | ND | 74 | 26 | 5 | 0 | N | Y | Y |  |
| 8-11A | 678 | ND | 73 | 25 | 3 | 1 | N | Y | Y |  |
| 8-11B | 641 | ND | 74 | 24 | 5 | 0 | N | Y | Y |  |
| 812A | 681 | ND | 74 | 24 | 5 | 1 | N | Y | Y |  |
| 812B | 627 | ND | 74 | 24 | 6 | 0 | N | Y | Y |  |
| 8-12J | 636 | ND | 75 | 23 | 4 | 1 | N | Y | Y | DEM, perfume odor |
| 8-13J | 641 | ND | 75 | 24 | 5 | 0 | N | Y | Y |  |
| 815B | 627 | ND | 74 | 24 | 5 | 0 | N | Y | Y |  |
| 816B | 654 | ND | 74 | 24 | 5 | 1 | N | Y | Y |  |
| 817B copy | 654 | ND | 74 | 24 | 6 | 0 | N | Y | Y | Copy |
| 8-17M | 689 | ND | 74 | 24 | 5 | 1 | N | Y | Y | CP |
| 8-18A | 697 | ND | 74 | 25 | 5 | 1 | N | Y | Y | Area rug |
| 8-18B | 676 | ND | 74 | 24 | 6 | 1 | N | Y | Y | AF odor, CP |
| 8-19B conference | 627 | ND | 74 | 24 | 7 | 0 | N | Y | Y | DEM |
| 8-19D | 652 | ND | 74 | 24 | 5 | 1 | N | Y | Y | DEM |
| 8-19G | 635 | ND | 74 | 25 | 7 | 2 | N | Y | Y |  |
| 8-19H | 662 | ND | 74 | 24 | 5 | 1 | N | Y | Y | DEM |
| 8-19J Conference room | 651 | ND | 74 | 24 | 5 | 0 | N | Y | Y | DEM |
| 8-19M | 689 | ND | 74 | 24 | 5 | 2 | N | Y | Y | DEM |
| 8-20M | 658 | ND | 74 | 24 | 5 | 1 | N | Y | Y | DEM, solar |
| 8-23B | 645 | ND | 74 | 23 | 4 | 0 | N | Y | Y |  |
| 8-23D | 657 | ND | 74 | 24 | 5 | 0 | N | Y | Y | DEM, PF, papers |
| 8-23M | 680 | ND | 74 | 24 | 5 | 2 | N | Y | Y | DEM |
| Chief of staff | 668 | ND | 73 | 24 | 5 | 1 | N | Y | Y |  |
| Kitchen | 639 | ND | 74 | 23 | 5 | 0 | N | Y | Y | Fridge has odor, microwave and toaster |
| Reception | 620 | ND | 74 | 24 | 6 | 0 | N | Y | Y |  |

# Text boxes

INDOOR AIR QUALITY ASSESSMENT

Department of Revenue

100 Cambridge Street

Boston, MA

Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health

Indoor Air Quality Program

January 2017