INDOOR AIR QUALITY

POST-OCCUPANCY ASSESSMENT

Massachusetts Department of Revenue

100 TradeCenter, Suite 760

Woburn, MA

Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health

Indoor Air Quality Program

May 2011

# Background/Introduction

In response to a request from Gerald Covino, Project Manager, Division of Capital Asset Management (DCAM), the Massachusetts Department of Public Health (MDPH), Bureau of Environmental Health (BEH) conducted post-occupancy indoor air quality (IAQ) testing at the Department of Revenue (DOR), 100 TradeCenter, Suite 760, Woburn, Massachusetts.  This evaluation was conducted as part of enhanced efforts to assess the air quality of office space leased by Massachusetts state agencies pre and post occupancy.  On March 29, 2011, a visit to conduct an IAQ assessment was made by Sharon Lee, Environmental Analyst/Inspector and Ruth Alfasso, Environmental Engineer/Inspector for BEH’s IAQ Program.

The building is a one-story structure consisting of office space, open work areas and conference/meeting rooms.  DOR shares the building with several other tenants, including a wellness spa and a medical clinic; each office space has separate HVAC equipment and the DOR office is separated from other uses of the building by walls and a hallway.  Windows throughout the building are openable

# Methods

Air tests for carbon monoxide, carbon dioxide, temperature and relative humidity were taken with the TSI, Q-Trak, IAQ Monitor 7565.  Air tests for airborne particle matter with a diameter less than 2.5 micrometers were taken with the TSI, DUSTTRAK™ Aerosol Monitor Model 8520.  Screening for total volatile organic compounds was conducted using a MiniRAETM 2000 Photo Ionization Detector (PID).  BEH staff also performed visual inspection of building materials for water damage and/or microbial growth and other conditions that may potentially impact indoor air quality.

# Results

The DOR offices have a combined employee population of approximately 135.  Tests were taken during normal operations approximately four weeks after occupancy.  Results for the March 29, 2011 visit appear in Table 1 and are listed by occupants’ last name(s) or office numerical designation (where available).

# Discussion

## Ventilation

It can be seen from Table 1 that carbon dioxide levels were below 800 parts per million (ppm) in all but 2 of the 69 locations tested at the time of assessment, indicating good air exchange throughout the building.  It is important to note that a number of areas were empty or sparsely populated during this visit, which can greatly reduce carbon dioxide levels.  Carbon dioxide levels would be expected to be higher with full occupancy.

Fresh air for the DOR office space is provided by rooftop air-handling units (AHUs) (Picture 1).  Fresh air is drawn into the AHUs through a bank of air filters (Picture 2), heated or cooled and delivered to occupied areas via ducted air diffusers (Picture 3).  Return air is drawn into an above ceiling plenum and ducted back to the rooftop AHUs through exhaust vents.

The HVAC system is controlled by digital thermostats.  Thermostats examined had a fan switch with two settings, on and auto (Picture 4).  When the fan is set to on, the system provides a continuous source of air circulation and filtration.  The automatic setting on the thermostat activates the HVAC system at a preset temperature.  Once the preset temperature is reached, the HVAC system is deactivated.  Therefore, no mechanical ventilation is provided until the thermostat re-activates the system.  Some thermostats at the DOR were set to auto and others were set to on at the time of the post-occupancy assessment.  The MDPH typically recommends that thermostats be set to the fan on setting during occupied hours to provide continuous air circulation; however, since air exchange appears to be adequate in the building at this time, the current settings may be acceptable; further monitoring and adjustment of these settings by building occupants may be warranted as they settle in and usage patterns become better established.

In order to have proper ventilation with a mechanical supply and exhaust system, the systems must be balanced to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room.  It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).  It was reported that the system was balanced prior to occupancy in late February of 2011.

The Massachusetts Building Code requires a minimum ventilation rate of 20 cubic feet per minute (cfm) per occupant of fresh outside air or openable windows (SBBRS, 1997; BOCA, 1993).  The ventilation must be on at all times that the room is occupied.  Providing adequate fresh air ventilation with open windows and maintaining the temperature in the comfort range during the cold weather season is impractical.  Mechanical ventilation is usually required to provide adequate fresh air ventilation.

Carbon dioxide is not a problem in and of itself.  It is used as an indicator of the adequacy of the fresh air ventilation.  As carbon dioxide levels rise, it indicates that the ventilating system is malfunctioning or the design occupancy of the room is being exceeded.  When this happens, a buildup of common indoor air pollutants can occur, leading to discomfort or health complaints.  The Occupational Safety and Health Administration (OSHA) standard for carbon dioxide is 5,000 parts per million parts of air (ppm).  Workers may be exposed to this level for 40 hours/week, based on a time-weighted average (OSHA, 1997).

The MDPH uses a guideline of 800 ppm for publicly occupied buildings.  A guideline of 600 ppm or less is preferred in schools due to the fact that the majority of occupants are young and considered to be a more sensitive population in the evaluation of environmental health status.  Inadequate ventilation and/or elevated temperatures are major causes of complaints such as respiratory, eye, nose and throat irritation, lethargy and headaches.  For more information concerning carbon dioxide, please see Appendix A.

Indoor temperatures ranged from 70°F to 73°F (Table 1), which were within the MDPH recommended comfort range with one exception, an unoccupied conference room which had a temperature of 66°F.  The MDPH recommends that indoor air temperatures be maintained in a range of 70 oF to 78 oF in order to provide for the comfort of building occupants.  Since this is newly occupied space, DOR management and staff may want to work with building management to determine appropriate heating/cooling settings.  In many cases concerning indoor air quality, fluctuations of temperature in occupied spaces are typically experienced, even in a building with an adequate fresh air supply.  It was noted that areas along the southern wall may be affected by solar gain through windows, which is likely to increase temperature and may increase overall feelings of warmth in those spaces.  Use of blinds to modulate the amount of sunlight may improve comfort in these areas.

Relative humidity measurements ranged from 10 to 18 percent (Table 1), which were below the MDPH recommended comfort range.  The MDPH recommends a comfort range of 40 to 60 percent for indoor air relative humidity.  Several building occupants expressed that the building air felt dry.  The sensation of dryness and irritation is common in a low relative humidity environment.  Low relative humidity is a very common problem during the heating season in the northeast part of the United States.

## Microbial/Moisture Concerns

In order for building materials to support mold growth, a source of water exposure is necessary.  No evidence of building leaks and/or other moisture concerns were observed or reported.  It was noted however, that a few water dispensers were located on carpeted areas as was a refrigerator (Table 1); spills/condensation from these appliances can be a source of moisture in carpeting that can lead to water damage and mold growth.  When possible, these units should be located in tiled areas or placed on a waterproof mat.

## Other IAQ Evaluations

Indoor air quality can be negatively influenced by the presence of respiratory irritants, such as products of combustion.  The process of combustion produces a number of pollutants.  Common combustion emissions include carbon monoxide, carbon dioxide, water vapor, and smoke (fine airborne particle material).  Of these materials, exposure to carbon monoxide and particulate matter with a diameter of 2.5 micrometers (μm) or less (PM2.5) can produce immediate, acute health effects upon exposure.  To determine whether combustion products were present in the indoor environment, BEH staff obtained measurements for carbon monoxide and PM2.5.

### Carbon Monoxide

Carbon monoxide is a by-product of incomplete combustion of organic matter (e.g., gasoline, wood and tobacco).  Exposure to carbon monoxide can produce immediate and acute health affects.  Several air quality standards have been established to address carbon monoxide and prevent symptoms from exposure to these substances.  The MDPH established a corrective action level concerning carbon monoxide in ice skating rinks that use fossil-fueled ice resurfacing equipment.  If an operator of an indoor ice rink measures a carbon monoxide level over 30 ppm, taken 20 minutes after resurfacing within a rink, that operator must take actions to reduce carbon monoxide levels (MDPH, 1997).

The American Society of Heating Refrigeration and Air-Conditioning Engineers (ASHRAE) has adopted the National Ambient Air Quality Standards (NAAQS) as one set of criteria for assessing indoor air quality and monitoring of fresh air introduced by HVAC systems (ASHRAE, 1989).  The NAAQS are standards established by the US EPA to protect the public health from six criteria pollutants, including carbon monoxide and particulate matter (US EPA, 2006).  As recommended by ASHRAE, pollutant levels of fresh air introduced to a building should not exceed the NAAQS levels (ASHRAE, 1989).  The NAAQS were adopted by reference in the Building Officials & Code Administrators (BOCA) National Mechanical Code of 1993 (BOCA, 1993), which is now an HVAC standard included in the Massachusetts State Building Code (SBBRS, 1997).  According to the NAAQS, carbon monoxide levels in outdoor air should not exceed 9 ppm in an eight-hour average (US EPA, 2006).

Carbon monoxide should not be present in a typical, indoor environment.  If it is present, indoor carbon monoxide levels should be less than or equal to outdoor levels.  Outdoor carbon monoxide concentrations ranged from 1 to 2 ppm the day of the assessment (Table 1).  No measureable levels of carbon monoxide were detected in the building during the assessment (Table 1).

### Particulate Matter

The US EPA has established NAAQS limits for exposure to particulate matter.  Particulate matter is airborne solids that can be irritating to the eyes, nose and throat.  The NAAQS originally established exposure limits to particulate matter with a diameter of 10 μm or less (PM10).  According to the NAAQS, PM10 levels should not exceed 150 micrograms per cubic meter (μg/m3) in a 24-hour average (US EPA, 2006).  These standards were adopted by both ASHRAE and BOCA.  Since the issuance of the ASHRAE standard and BOCA Code, US EPA established a more protective standard for fine airborne particles.  This more stringent PM2.5 standard requires outdoor air particle levels be maintained below 35 μg/m3 over a 24-hour average (US EPA, 2006).  Although both the ASHRAE standard and BOCA Code adopted the PM10 standard for evaluating air quality, MDPH uses the more protective PM2.5 standard for evaluating airborne particulate matter concentrations in the indoor environment.

During the March 29, 2011 assessment, outdoor PM2.5 was measured at 4 μg/m3 (Table 1).  PM2.5 levels measured indoors ranged from 2 to 10 μg/m3 (Table 1), which were below the NAAQS PM2.5 level of 35 μg/m3.  Frequently, indoor air levels of particulates (including PM2.5) can be at higher levels than those measured outdoors.  A number of mechanical devices and/or activities that occur in buildings can generate particulate during normal operations.  Sources of indoor airborne particulates may include but are not limited to particles generated during the operation of fan belts in the HVAC system, use of stoves and/or microwave ovens in kitchen areas; use of photocopiers, fax machines and computer printing devices; operation of an ordinary vacuum cleaner and heavy foot traffic indoors.

### Volatile Organic Compounds

Indoor air concentrations can be greatly impacted by the use of products containing volatile organic compounds (VOCs) within the building.  VOCs are carbon-containing substances that have the ability to evaporate at room temperature.  Frequently, exposure to low levels of total volatile organic compounds (TVOCs) may produce eye, nose, throat and/or respiratory irritation in some sensitive individuals.  For example, chemicals evaporating from a paint can stored at room temperature would most likely contain VOCs.  In an effort to determine whether VOCs were present in the building, air monitoring for TVOCs was conducted.  Outdoor air samples taken for comparison were ND.  No measureable levels of TVOCs were detected in the building during the assessment.  TVOC concentrations were not recorded in specific areas and are not shown in Table 1.

# Conclusions/Recommendations

Overall, conditions in the building after build-out both before and after one month’s occupancy were adequate in terms of air exchange, temperature control and lack of evidence of moisture problem, water damage or other potential indoor air quality concerns.  In view of the findings at the time of the visit, the following recommendations are made:

- Consider setting all thermostats to the fan “on” position to operate the ventilation system continuously during business hours.

- DOR management/staff should work with building management to identify areas of uneven heating/cooling to determine appropriate heating/cooling settings.

- Change filters for air handling equipment as per the manufacturer’s instructions or more frequently if needed.

- For buildings in New England, periods of low relative humidity during the winter are often unavoidable.  Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low.  To control for dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended.  Avoid the use of feather dusters.  Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

- Consider adopting a balancing schedule of every 5 years for all mechanical ventilation systems, as recommended by ventilation industrial standards (SMACNA, 1994).

- Consider moving water dispensing equipment to areas with tiled floors instead of carpeting, or installing waterproof mats to prevent leaks from damaging carpet.

- Monitor interior areas for signs of water infiltration and/or plumbing leaks and report to building management for prompt remediation.

- Refer to resource manual and other related indoor air quality documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings.  These documents are available at: http://mass.gov/dph/iaq.

# References

ASHRAE.  1989.  Ventilation for Acceptable Indoor Air Quality.  American Society of Heating, Refrigeration and Air Conditioning Engineers.  ANSI/ASHRAE 62-1989.

BOCA.  1993.  The BOCA National Mechanical Code/1993.  8th ed.  Building Officials and Code Administrators International, Inc., Country Club Hill, IL.

MDPH.  1997.  Requirements to Maintain Air Quality in Indoor Skating Rinks (State Sanitary Code, Chapter XI).  105 CMR 675.000.  Massachusetts Department of Public Health, Boston, MA.

OSHA.  1997.  Limits for Air Contaminants.  Occupational Safety and Health Administration.  Code of Federal Regulations.  29 C.F.R 1910.1000 Table Z-1-A.

SBBRS.  1997.  Mechanical Ventilation.  State Board of Building Regulations and Standards.  Code of Massachusetts Regulations.  780 CMR 1209.0

SMACNA.  1994.  HVAC Systems Commissioning Manual.  1st ed.  Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

US EPA.  2006.  National Ambient Air Quality Standards (NAAQS).  US Environmental Protection Agency, Office of Air Quality Planning and Standards, Washington, DC.  http://www.epa.gov/air/criteria.html.

Picture 1

Rooftop Air Handling Unit

Picture 2

Example Air Filters in Air Handling Unit

Picture 3

Example Ceiling-Mounted Air Diffusers

Picture 4

Example Digital Thermostat

| - Location | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | Temp (°F) | Relative Humidity (%) | PM2.5 (µg/m3) | Occupants in Room | Windows Openable | Ventilation |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| Background (parking lot) | 391 | 1-2 | 50 | 15 | 4 | NA |  |  |  | Sunny, breezy |
| Conference room 2 | 726 | ND | 66 | 18 | 4 | 0 | N | Y | Y |  |
| Conference room 1 | 631 | ND | 70 | 12 | 3 | 0 | N | Y | Y |  |
| Deputy Director’s office | 643 | ND | 71 | 12 | 3 | 0 | Y | Y | N |  |
| 5 | 626 | ND | 71 | 12 | 4 | 0 | Y | Y | Y | Open plan cubicles |
| 19 | 629 | ND | 71 | 12 | 4 | 0 | Y | Y | Y |  |
| 24 | 639 | ND | 71 | 12 | 4 | 1 | Y | Y | Y |  |
| Gautier | 665 | ND | 71 | 12 | 4 | 2 | Y | Y | Y |  |
| 17 | 636 | ND | 70 | 12 | 4 | 1 | Y | Y | Y |  |
| 117 (interview) | 613 | ND | 70 | 11 | 3 | 0 | N | Y | N |  |
| 26 | 657 | ND | 71 | 13 | 4 | 0 | Y | Y | Y |  |
| Kelly | 732 | ND | 71 | 12 | 4 | 2 | Y | Y | Y |  |
| Kahlhaus | 672 | ND | 72 | 12 | 3 | 0 | Y | Y | Y | Many copy machines |
| 43 | 653 | ND | 72 | 12 | 4 | 0 | Y | Y | Y |  |
| 59 | 640 | ND | 72 | 12 | 4 | 4 | Y | Y | Y |  |
| 63 | 678 | ND | 72 | 12 | 4 | 3 | Y | Y | Y | Jammed copier being fixed |
| Gorzak | 644 | ND | 73 | 13 | 3 | 0 | Y | Y | Y |  |
| 65 | 706 | ND | 73 | 11 | 4 | 4 | Y | Y | Y |  |
| 77 | 689 | ND | 73 | 12 | 3 | 4 | Y | Y | Y |  |
| Darnelle | 695 | ND | 73 | 12 | 2 | 4 | Y | Y | Y | Occupant noted drafty feeling |
| Net | 670 | ND | 72 | 11 | 4 | 1 | Y | Y | Y |  |
| 71 | 653 | ND | 72 | 12 | 4 | 1 | Y | Y | Y |  |
| Office 116 | 632 | ND | 72 | 11 | 6 | 0 | N | Y | N |  |
| Office 127 | 687 | ND | 72 | 11 | 5 | 0 | N | Y | N |  |
| Office 128 | 644 | ND | 72 | 12 | 5 | 1 | N | Y | N |  |
| Office 129 | 677 | ND | 72 | 12 | 5 | 1 | N | Y | N |  |
| 83 | 654 | ND | 72 | 11 | 4 | 2 | Y | Y | Y |  |
| 87 | 636 | ND | 72 | 11 | 4 | 1 | Y | Y | Y |  |
| 89 | 635 | ND | 72 | 12 | 4 | 0 | Y | Y | Y |  |
| 101 | 626 | ND | 73 | 11 | 4 | 0 | Y | Y | Y |  |
| 108 | 646 | ND | 73 | 12 | 4 | 0 | Y | Y | Y |  |
| 107 | 643 | ND | 73 | 11 | 4 | 0 | Y | Y | Y |  |
| 110 | 656 | ND | 73 | 12 | 5 | 1 | Y | Y | Y | Solar gain (sunny side of office) |
| Adjacent to 110 | 717 | ND | 74 | 12 | 5 | 1 | Y | Y | Y | Solar gain |
| Office 125 | 617 | ND | 72 | 10 | 4 | 0 | N | Y | N |  |
| Office 126 | 649 | ND | 72 | 11 | 7 | 0 | N | Y | N |  |
| Office 127 | 650 | ND | 72 | 12 | 7 | 0 | N | Y | N |  |
| Office 128 | 694 | ND | 72 | 12 | 6 | 0 | N | Y | N |  |
| Interview 3 | 750 | ND | 71 | 14 | 5 | 0 | N | Y | N |  |
| Waiting room | 783 | ND | 71 | 13 | 5 | 1 | N | Y | Y |  |
| Interview 2 | 762 | ND | 72 | 13 | 5 | 0 | N | Y | N |  |
| Diaz/Aretusi | 922 | ND | 71 | 13 | 4 | 3 | N | Y | Y |  |
| 1-3 | 644 | ND | 71 | 12 | 5 | 0 | N | Y | Y | Water cooler/fridge on carpet |
| Reception (interior side) | 631 | ND | 71 | 12 | 4 | 2 | N | Y | Y | PC |
| 33 | 662 | ND | 72 | 12 | 5 | 0 | Y | Y | Y |  |
| 3/5 | 677 | ND | 72 | 12 | 4 | 0 | Y | Y | Y |  |
| Maline/51 | 739 | ND | 72 | 12 | 5 | 0 | Y | Y | Y |  |
| Bryant | 723 | ND | 72 | 13 | 4 | 0 | Y | Y | Y | PF, CP |
| Office 132 | 661 | ND | 72 | 12 | 4 | 0 | Y | Y | Y | DO |
| Office 133 | 634 | ND | 72 | 11 | 4 | 0 | Y | Y | Y | DO |
| Office 134 | 638 | ND | 71 | 11 | 5 | 0 | Y | Y | Y | DO |
| Office 135 | 690 | ND | 72 | 12 | 4 | 2 | Y | Y | Y | DO |
| 70/82/72/84 | 681 | ND | 72 | 11 | 5 | 0 | N | Y | Y | PF |
| 74/86 | 666 | ND | 72 | 11 | 4 | 1 | N | Y | Y | Water cooler on carpet |
| 90/Corneau | 680 | ND | 72 | 11 | 4 | 1 | N | Y | Y |  |
| 98/90/94 | 683 | ND | 72 | 12 | 5 | 3 | N | Y | Y |  |
| 93/91 | 663 | ND | 72 | 11 | 4 | 1 | N | Y | Y |  |
| 96/97/98 | 666 | ND | 72 | 11 | 4 | 0 | Y | Y | Y |  |
| 103/Cronin/Quintal | 643 | ND | 73 | 12 | 4 | 4 | Y | Y | Y |  |
| 83/85/87 | 704 | ND | 73 | 11 | 5 | 4 | N | Y | Y |  |
| 113/115/Cosela | 737 | ND | 73 | 12 | 6 | 2 | Y | Y | Y |  |
| 130 | 659 | ND | 73 | 11 | 6 | 1 | N | Y | Y | DO |
| 142 | 650 | ND | 73 | 11 | 8 | 1 | N | Y | Y |  |
| 141/131 | 707 | ND | 72 | 11 | 7 | 0 | N | Y | Y | DO |
| Staff lounge | 832 | ND | 72 | 14 | 6 | 9 | Y | Y | Y |  |
| Training 2 | 739 | ND | 72 | 13 | 7 | 0 | N | Y | Y | Fan-auto, DO |
| Imaging | 784 | ND | 72 | 13 | 8 | 1 | N | Y | Y | DO |
| File room | 693 | ND | 72 | 12 | 10 | 0 | N | Y | Y | DO |
| Training 4 | 749 | ND | 72 | 13 | 6 | 7 | N | Y | Y | DO |
| Conference 2 | 686 | ND | 72 | 11 | 6 | 4 | N | Y | Y | DO |