# Background

| Building: | Department of Transitional Assistance (DTA) |
| --- | --- |
| Address: | 310 State Street, Springfield, MA |
| Assessment Requested by: | Debra Thomas Department of Transitional Assistance |
| Reason for Request: | Reports of building occupant illness and concerns about general indoor air quality (IAQ) |
| Date of Assessment: | November 22, 2016 |
| Massachusetts Department of Public Health/Bureau of Environmental Health (MDPH/BEH) Staff Conducting Assessment: | Michael Feeney, Director, IAQ Program |
| Building Description: | Three-story brick building built in the 1920s. |
| Building Population: | Approximately 60 employees over the two floors |
| Windows: | Some openable |

# Methods

Please refer to the IAQ Manual for methods, sampling procedures, and interpretation of results (MDPH, 2015).

# IAQ Testing Results

The following is a summary of indoor air testing results (Table 1).

- Carbon dioxide levels were above 800 parts per million (ppm) in more than three quarters of the areas assessed, indicating less than adequate fresh air in the space. However, note that most readings were only slightly above 800 ppm.

- Temperature was within the recommended range of 70°F to 78°F in all areas assessed.

- Relative humidity was below the recommended range of 40% to 60% in all areas assessed.

- Carbon monoxide levels were non-detectable in all indoor areas assessed.

- Fine particulate matter (PM2.5) concentrations measured were below the National Ambient Air Quality Standard (NAAQS) level of 35 μg/m3 in all areas assessed.

## Ventilation

A heating, ventilating, and air conditioning (HVAC) system has several functions. First, it provides heating and, if equipped, cooling. Second, it is a source of fresh air. Finally, an HVAC system will dilute and remove normally occurring indoor environmental pollutants by not only introducing fresh air, but also filtering the airstream and ejecting stale air to the outdoors via exhaust ventilation. Even if an HVAC system is operating as designed, point sources of respiratory irritation may exist and affect symptoms in sensitive individuals. The following analysis examines and identifies components of the HVAC system and likely sources of respiratory irritant/allergen exposure due to water damage, aerosolized dust, and/or chemicals found in the indoor environment.

Fresh air is introduced by an air-handling unit (AHU) and distributed through ducted, ceiling vents throughout the building. The assessment results indicate that the ventilation system was limiting the amount of fresh air. The HVAC system is controlled by thermostats with a fan switch with two settings: “on” and “auto”. When the fan is set to “on”, the system provides a continuous source of air circulation and filtration. The automatic (“auto”) setting on the thermostat activates the HVAC system only when temperature needs adjustment to meet the pre-set temperature. Once the pre-set temperature is reached, the HVAC system is deactivated and no mechanical ventilation is provided until the thermostat re-activates the system. At the time of assessment, all thermostat fan settings were in the “auto” position (Picture 1). The MDPH typically recommends that thermostats be set to the fan “on” setting during occupied hours to provide continuous air circulation. The fan “auto” setting can lead to IAQ/comfort complaints due to lack of air exchange.

## Microbial/Moisture Concerns

DTA staff indicated that a radiator located in the stairwell had leaked several weeks prior to this assessment (Picture 4). When steam leaks occur, metallic particles suspended in the steam can become aerosolized, which can produce a pungent odor. In addition, steam can be a source of moisture to any porous building materials or accumulated dust and dirt inside the radiator cabinet, which can then become mold colonized. The leak was repaired prior to the BEH/IAQ visit. The radiator cabinet was found free of any discernable odor or other signs of microbial growth.

A few water-damaged ceiling tiles were observed in the storeroom and hallway. The conditions causing the damage (e.g., roof leaks) should be fixed, and the tiles should be replaced. Peeling paint from plaster walls indicate likely water penetration through window frames in some areas (Picture 2). A kitchen area had a water-damaged cabinet but did not have either mold colonization or musty odors.

Plants were observed in office areas (Picture 3). Plants can be a source of pollen and mold, which can be respiratory irritants to some individuals. Plants should be properly maintained and equipped with drip pans to prevent water damage to porous materials. Plants should also be located away from air diffusers to prevent the aerosolization of dirt, pollen, and mold.

Water dispensers were observed in carpeted areas. These appliances may spill or leak and lead to carpet damage and microbial growth. It is recommended that these appliances be located in areas without carpeting or on waterproof mats. Carpet squares could also be replaced with tile in areas where water dispensers and refrigerators are located. Some of the refrigerators were crowded with items or had evidence of spills/crumbs. Refrigerators should be kept clean to prevent odors and microbial growth.

## Other IAQ Evaluations

Exposure to low levels of total volatile organic compounds (TVOCs) may produce eye, nose, throat, and/or respiratory irritation in some sensitive individuals. To determine if VOCs were present, BEH/IAQ staff examined rooms for products containing VOCs and noted hand sanitizers, cleaners, and dry erase materials in use within the building. All of these products have the potential to be irritants to the eyes, nose, throat, and respiratory system of sensitive individuals. Photocopiers were also located next to occupied cubes; when heavily used, photocopiers can emit ozone, which is a respiratory irritant, and may also emit particulates and odors.

The offices were mostly carpeted. Carpets should be cleaned annually (or semi-annually in soiled/high traffic areas) in accordance with Institute of Inspection, Cleaning and Restoration Certification (IICRC) recommendations, (IICRC, 2012).

In some areas, stored materials and accumulated items make it more difficult for custodial staff to clean. One room had a large accumulation of food in plastic bags (Picture 5). Items should be stored neatly and moved periodically to allow for wet wiping and vacuuming of surfaces. In some places, workstation walls were set up against the original exterior or interior walls of the building, leaving narrow gaps. These areas can catch dirt and debris and become a source of odors, and harborage for pests. Ensure that these areas are cleaned regularly.

Personal fans were observed in a number of areas. Fan blades to some of these units had settled dust, which can be reaerosolized when the fan is activated.

# Conclusions/Recommendations

Based on observations at the time of assessment, the following is recommended:

- Operate supply and exhaust ventilation continuously in all areas during occupied periods.

- Have the HVAC system balanced every 5 years in accordance with SMACNA recommendations (SMACNA, 1994).

- Repair conditions leading to water-damaged ceiling tiles, and replace the tiles.

- Check closures and seals on windows to minimize water infiltration. Repair and repaint areas of peeling paint.

- Keep indoor plants in good condition, avoid overwatering, and avoid placing them on porous items such as carpets or paper. Also, keep plants out of the air stream of supply vents.

- Consider locating refrigerators and water dispensers in non-carpeted areas or place on a waterproof mat.

- Clean refrigerator spills promptly and clean refrigerators out regularly to avoid odors and microbial growth.

- Ensure cooking areas/equipment are kept clean to prevent odors and pests. Consider reducing the number of areas where food is stored and locating them away from occupied areas.

- For buildings in New England, periods of low relative humidity during the winter are often unavoidable. Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low. To control for dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended. Avoid the use of feather dusters. Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

- Consider moving photocopiers, particularly those that are heavily used, away from occupied areas.

- Minimize use of hand sanitizers and other products containing VOCs.

- Clean carpeting in accordance with IICRC recommendations (IICRC, 2012).

- Ensure hidden areas between workstations and walls get cleaned regularly.

- Reduce accumulated materials on flat surfaces and store in an organized manner to allow for thorough cleaning.

- Clean the blades of fans periodically to remove dust and debris.

- Refer to resource manual and other related IAQ documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings. These documents are available at: http://mass.gov/dph/iaq.

# References

IICRC. 2012. Institute of Inspection, Cleaning and Restoration Certification. Carpet Cleaning: FAQ. Retrieved from http://www.iicrc.org/consumers/care/carpet-cleaning.

MDPH. 2015. Massachusetts Department of Public Health. Indoor Air Quality Manual: Chapters I-III. Available at: http://www.mass.gov/eohhs/gov/departments/dph/programs/environmental-health/exposure-topics/iaq/iaq-manual/.

SMACNA. 1994. HVAC Systems Commissioning Manual. 1st ed. Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

Picture 1

Thermostat set on “AUTO” (arrow)

Picture 2

Peeling paint

Picture 3

Potted plant on carpet

Picture 4

Radiator in stairwell

Picture 5

Large accumulation of food in plastic bags

| Location | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | Temp (°F) | Relative Humidity (%) | PM2.5 (µg/m3) | Occupants in Room | Windows Openable | Ventilation | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| Background (outdoors) | 448 | ND | 38 | 48 | 5 |  |  |  |  |  |
| DTA conference room | 1011 | ND | 71 | 34 | 1 | 3 | N | Y | Y |  |
| 201 | 858 | ND | 72 | 27 | 1 | 1 | Y | Y | Y |  |
| 202 | 856 | ND | 72 | 27 | 2 | 1 | Y | Y | Y |  |
| 202 | 841 | ND | 73 | 25 | 2 | 0 | Y | Y | Y |  |
| 205 | 829 | ND | 74 | 24 | 2 | 0 | N | Y | Y | 2 water-damaged ceiling tiles |
| 206 | 779 | ND | 72 | 24 | 2 | 0 | Y | Y | Y |  |
| 214 | 758 | ND | 73 | 25 | 2 | 3 | Y | Y | Y |  |
| 216 | 875 | ND | 75 | 26 | 2 | 0 | Y | Y | Y | 6 water-damaged ceiling tiles |
| 218 | 831 | ND | 73 | 26 | 2 | 2 | Y | Y | Y |  |
| 220 | 819 | ND | 72 | 26 | 1 | 2 | N | Y | Y |  |
| 225 | 793 | ND | 74 | 24 | 2 | 2 | Y | Y | Y |  |
| 227 | 783 | ND | 74 | 25 | 2 | 1 | Y | Y | Y |  |
| 229 | 833 | ND | 73 | 26 | 1 | 4 | Y | Y | Y |  |
| 233 | 790 | ND | 73 | 25 | 2 | 2 | Y | Y | Y |  |
| 236 | 812 | ND | 73 | 26 | 1 | 2 | Y | Y | Y | Water cooler on carpet |
| 240 | 826 | ND | 73 | 25 | 2 | 3 | Y | Y | Y |  |
| 251 | 814 | ND | 73 | 25 | 2 | 2 | Y | Y | Y | Coke machine |
| Breakroom | 861 | ND | 73 | 24 | 3 | 0 | N | Y | Y |  |
| Reception | 803 | ND | 73 | 23 | 3 | 3 | Y | Y | Y | Plants |
| Waiting room | 876 | ND | 72 | 25 | 3 | 9 | Y | Y | Y |  |
| 105 | 797 | ND | 70 | 24 | 1 | 0 | Y | Y | N | Plastic bags |
| 106 | 828 | ND | 72 | 25 | 3 | 1 | N | Y | Y |  |
| 107 | 812 | ND | 72 | 24 | 2 | 0 | Y | Y | Y |  |
| 107 | 821 | ND | 71 | 24 | 3 | 0 | Y | Y | Y |  |
| 110 | 802 | ND | 73 | 25 | 2 | 0 | N | Y | Y |  |
| 113 | 865 | ND | 73 | 24 | 3 | 0 | Y | Y | Y |  |
| 116 | 895 | ND | 73 | 26 | 3 | 2 | Y | Y | Y |  |
| 119 | 901 | ND | 73 | 26 | 3 | 4 | Y | Y | Y |  |
| 120 | 889 | ND | 74 | 24 | 3 | 0 | N | Y | Y | Photocopier |
| 121 | 773 | ND | 73 | 25 | 2 | 3 | N | Y | Y | Plant |
| 129 | 822 | ND | 71 | 25 | 2 | 0 | Y | Y | Y |  |
| 135 | 811 | ND | 74 | 24 | 2 | 1 | Y | Y | Y | Plant |

# Text boxes

INDOOR AIR QUALITY ASSESSMENT

Department of Transitional Assistance

310 State Street

Springfield, MA

Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health

Indoor Air Quality Program

January 2017