INDOOR AIR QUALITY ASSESSMENT

Duxbury Middle School

71 Alden Street

Duxbury, Massachusetts  02332

Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health

Indoor Air Quality Program

December 2009

# Background/Introduction

In response to an anonymous request, the Massachusetts Department of Public Health (MDPH), Bureau of Environmental Health (BEH) provided assistance and consultation regarding indoor air quality concerns at Duxbury Middle School (DMS), 71 Alden Street, Duxbury, Massachusetts.  On October 26, 2009, Cory Holmes and James Tobin, Environmental Analysts/Inspectors in BEH’s Indoor Air Quality (IAQ) Program visited the DMS to conduct an assessment.  During the assessment, BEH staff were accompanied by Don Burgess, Facilities Manager, Duxbury Public Schools (DPS).

The DMS is a red, brick building built in 1961.  An addition was made in 1974.  The DMS is comprised of a two-story classroom wing and several single-story wings that form a courtyard.  The school contains general classroom, science classrooms, smaller educational classrooms for specialized instruction, a computer room, two gymnasiums, locker rooms, kitchen/cafeteria, library, auditorium and music/band rooms.  The majority of building components are original (floors, ceilings, mechanical ventilation components).  Windows are openable, however, many are reported to be in disrepair or inoperable.

Due to previous IAQ concerns, the DPS hired an environmental consultant, Envirotest Lab, Inc. (ELI), in January 2009 to conduct an evaluation of the DMS Guidance Department.  The ELI report recommended that: 1) all roof leaks be repaired; 2) all moisture damaged ceiling tiles be replaced; and 3) the water damaged sheetrock wall between the library and guidance department be replaced (ELI, 2009).

Methods

Air tests for carbon monoxide, carbon dioxide, temperature and relative humidity were conducted with the TSI, Q-Trak, IAQ Monitor, Model 7565.  Air tests for airborne particle matter with a diameter less than 2.5 micrometers were taken with the TSI, DUSTTRAK™ Aerosol Monitor Model 8520.  MDPH staff also performed visual inspection of building materials for water damage and/or microbial growth.  Moisture content of porous building materials was measured with a Delmhorst, BD-2000 Model, Moisture Detector equipped with a Delmhorst Standard Probe.

Results

The school houses approximately 800 students in grades 6 to 8 with approximately 80 staff members.  Tests were taken during normal school operations and results appear in Table 1.

Discussion

## Ventilation

It can be seen from Table 1 that carbon dioxide levels were above 800 parts per million (ppm) in 39 of 76 areas at the time of the assessment, which indicates poor air exchange in more than half of the areas surveyed, mainly due to deactivated/non-functional mechanical ventilation equipment.  It is also important to note that several classrooms had open windows and/or were empty/sparsely populated, which typically reduces carbon dioxide levels.  Carbon dioxide levels would be expected to be higher with full occupancy and/or windows closed.

Fresh air is supplied to most classrooms by unit ventilators (univent) systems (Pictures 1 through 3).  A univent draws air from the outdoors through a fresh air intake located on the exterior wall of the building or from rooftop vents (Pictures 4 and 5).  Return air from the classroom is drawn through an air intake located at the base of the unit (Figure 1).  Fresh and return air are mixed, filtered, heated and provided to classrooms through an air diffuser located in the top of the unit.  A number of univents appeared to be original equipment, approximately 40 to 50 years old.  Univents of this age are difficult to maintain because replacement parts are often unavailable.

Univents have control settings of ‘on or off’ and ‘low, medium or high’ (Picture 6).  Univents were found ‘off’ in many areas (Table 1/Picture 6); therefore, there was no means to provide mechanical ventilation to these classrooms at the time of the assessment.  In several cases, univent fresh air intakes were sealed on the exterior of the building with plywood or cardboard and duct tape (Pictures 7 and 8).  In order for univents to provide fresh air as designed, intakes/returns must remain free of obstructions.  Importantly, these units must remain ‘on’ and be allowed to operate while rooms are occupied.

Exhaust ventilation in classrooms is provided by wall or ceiling vents ducted to rooftop motors (Pictures 9 and 10).  Many exhaust vents were obstructed (Picture 11) and/or deactivated at the time of the assessment.  As with univents, in order to function properly, exhaust vents must be activated and allowed to operate while rooms are occupied.  Without adequate supply and exhaust ventilation, excess heat and environmental pollutants can build up and lead to indoor air/comfort complaints.

The heating, ventilating and air conditioning (HVAC) systems for interior rooms and common areas (e.g., gymnasium, locker rooms, auditorium) consist of rooftop or ceiling-mounted air-handling units (AHUs) (Pictures 12 and 13).  Fresh air is distributed via ceiling-mounted air diffusers (Picture 14) and ducted back to AHUs via ceiling or wall-mounted return vents (Pictures 15 and 16).  Several of these units had been deactivated or were inoperable at the time of the assessment; therefore, there was no means of mechanical air exchange in these areas, which was evidenced by the elevated carbon dioxide levels.  Of particular note was the lack of mechanical ventilation in interior rooms without windows (e.g., guidance suite, 418, 522, 518).  Since these areas cannot open windows they are entirely dependant on mechanical ventilation for air exchange.  At the time of the assessment, Mr. Burgess reported that he believed a fuse was out that controlled the unit.  In subsequent correspondence with Mr. Burgess, he reported that the fuse had been replaced and the AHU reactivated.

To maximize air exchange, the MDPH recommends that both supply and exhaust ventilation operate continuously during periods of school occupancy.  In order to have proper ventilation with a mechanical supply and exhaust system, the systems must be balanced to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room.  It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).  The date of the last balancing of these systems was not available at the time of the assessment.

The Massachusetts Building Code requires a minimum ventilation rate of 15 cubic feet per minute (cfm) per occupant of fresh outside air or have openable windows in each room (SBBRS, 1997; BOCA, 1993).  The ventilation must be on at all times that the room is occupied.  Providing adequate fresh air ventilation with open windows and maintaining the temperature in the comfort range during the cold weather season is impractical.  Mechanical ventilation is usually required to provide adequate fresh air ventilation.

Carbon dioxide is not a problem in and of itself.  It is used as an indicator of the adequacy of the fresh air ventilation.  As carbon dioxide levels rise, it indicates that the ventilating system is malfunctioning or the design occupancy of the room is being exceeded.  When this happens, a buildup of common indoor air pollutants can occur, leading to discomfort or health complaints.  The Occupational Safety and Health Administration (OSHA) standard for carbon dioxide is 5,000 parts per million parts of air (ppm).  Workers may be exposed to this level for 40 hours/week, based on a time-weighted average (OSHA, 1997).

The MDPH uses a guideline of 800 ppm for publicly occupied buildings.  A guideline of 600 ppm or less is preferred in schools due to the fact that the majority of occupants are young and considered to be a more sensitive population in the evaluation of environmental health status.  Inadequate ventilation and/or elevated temperatures are major causes of complaints such as respiratory, eye, nose and throat irritation, lethargy and headaches.  For more information concerning carbon dioxide, consult Appendix A.

## Temperature and Relative Humidity

Temperature measurements ranged from 66o F to 76o F, which were within the MDPH recommended comfort range in the majority of areas surveyed (Table 1).  The MDPH recommends that indoor air temperatures be maintained in a range of 70o F to 78o F in order to provide for the comfort of building occupants.  A number of occupants reported difficulty with temperature control.  In many cases concerning indoor air quality, fluctuations of temperature in occupied spaces are typically experienced, even in a building with an adequate fresh air supply.  In addition, it is difficult to control temperature and maintain comfort without operating the ventilation equipment as designed (e.g., univents/exhaust vents deactivated/obstructed).

The relative humidity measured in the building ranged from 30 to 46 percent, which was below the MDPH recommended comfort range in many of the areas surveyed (Table 1).  The MDPH recommends a comfort range of 40 to 60 percent for indoor air relative humidity.  Relative humidity levels in the building would be expected to drop during the winter months due to heating.  The sensation of dryness and irritation is common in a low relative humidity environment.  Low relative humidity is a very common problem during the heating season in the northeast part of the United States.

## Microbial/Moisture Concerns

In order for building materials to support mold growth, a source of water exposure is necessary (e.g., roof/plumbing leaks).  Identification and elimination of water moistening building materials is necessary to control mold growth.  Materials with increased moisture content over normal concentrations may indicate the possible presence of mold growth.  Numerous areas had water-damaged/missing ceiling tiles which can indicate leaks from either the roof or plumbing system (Pictures 17 through 19/Table 1).  Active leaks were evidenced by moistened ceiling tiles along the exterior wall in room 411.  Water-damaged ceiling tiles can provide a source of mold and should be replaced after a water leak is discovered and repaired.

BEH staff also conducted moisture testing of water-damaged wallboard in the upper library, which was found to have elevated moisture content.  Mr. Burgess reported that the library roof had been repaired over the summer of 2009.  Chronic leakage was observed in the form of water damaged ceiling tiles and peeling vinyl wallpaper (Pictures 19 through 21).  Although the leak has been repaired, the vinyl wall paper acts as a vapor barrier, trapping moisture behind it, causing it to peel, damaging wallboard beneath it and promoting mold growth.  At the time of the assessment, BEH staff recommended that the damaged wallpaper and moistened wallboard be removed using the US Environmental Protection Agency (US EPA) guidance “Mold Remediation in Schools and Commercial Buildings”.  In subsequent correspondence with Mr. Burgess, he reported that removal/replacement of the water damaged wallboard in the library was scheduled for the Veterans Day 2009 break.

It is important to note that moisture content of materials measured is a real-time measurement of the conditions present in the building at the time of the assessment.  Repeated water damage to porous building materials (e.g., wallboard, ceiling tiles, and carpeting) can result in microbial growth.  The US Environmental Protection Agency (US EPA) and the American Conference of Governmental Industrial Hygienists (ACGIH) recommend that porous materials be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2001; ACGIH, 1989).  If not dried within this time frame, mold growth may occur.  Once mold has colonized porous materials, they are difficult to clean and should be removed.

During the assessment, Mr. Burgess reported that several weeks previous to the assessment, mold growth was observed on a flexible cloth covered wall in room 212.  At the time of the assessment, the flexible wall had been removed and replaced with a solid, floor to ceiling, paneled wall (Pictures 22 and 23).  No current evidence of water damage or mold was observed during the MDPH assessment.

BEH staff examined the building exterior to identify breaches in the building envelope that could provide a source of water penetration.  Several potential sources were identified:

- Overgrown plants/trees/bushes against the building throughout the courtyard and around the perimeter of the building (Pictures 24 through 27)

- Plants growing in close proximity to fresh air intakes (Picture 27)

- Missing/damaged sealant between expansion joints and masonry (Picture 28);

- Missing/damaged sealant around univent air intakes (Picture 29);

- Damaged/corroded exterior metal doors (Pictures 30 and 31);

- Clinging plants on exterior brick (Picture 32); and,

- Severely damaged/missing exterior caulking around windows, which in some cases has resulted in moss growth both outside and inside window panes (Pictures 33 through 38).

The conditions listed above can undermine the integrity of the building envelope and create/provide a means of water entry by capillary action into the building through exterior walls, foundation concrete and masonry (Lstiburek & Brennan, 2001).  The freezing and thawing action of water during the winter months can create cracks and fissures in the foundation.  In addition, they can serve as pathways for insects, rodents and other pests into the building.  In subsequent correspondence with Mr. Burgess, he reported that windows were resealed in the interior courtyard.

Plants were noted in several classrooms.  Plants can be a source of pollen and mold, which can be respiratory irritants for some individuals.  Plants should be properly maintained and equipped with drip pans to prevent water damage to porous building materials, which can lead to mold growth.  Plants should also be located away from ventilation sources (e.g., air intakes, univent diffusers) to prevent the entrainment and/or aerosolization of dirt, pollen or mold.

## Other IAQ Evaluations

Indoor air quality can be negatively influenced by the presence of respiratory irritants, such as products of combustion.  The process of combustion produces a number of pollutants.  Common combustion emissions include carbon monoxide, carbon dioxide, water vapor and smoke (fine airborne particle material).  Of these materials, exposure to carbon monoxide and particulate matter with a diameter of 2.5 micrometers (μm) or less (PM2.5) can produce immediate, acute health effects upon exposure.  To determine whether combustion products were present in the school environment, BEH staff obtained measurements for carbon monoxide and PM2.5.

### Carbon Monoxide

Carbon monoxide is a by-product of incomplete combustion of organic matter (e.g., gasoline, wood and tobacco).  Exposure to carbon monoxide can produce immediate and acute health affects.  Several air quality standards have been established to address carbon monoxide and prevent symptoms from exposure to these substances.  The MDPH established a corrective action level concerning carbon monoxide in ice skating rinks that use fossil-fueled ice resurfacing equipment.  If an operator of an indoor ice rink measures a carbon monoxide level over 30 ppm, taken 20 minutes after resurfacing within a rink, that operator must take actions to reduce carbon monoxide levels (MDPH, 1997).

The American Society of Heating Refrigeration and Air-Conditioning Engineers (ASHRAE) has adopted the National Ambient Air Quality Standards (NAAQS) as one set of criteria for assessing indoor air quality and monitoring of fresh air introduced by HVAC systems (ASHRAE, 1989).  The NAAQS are standards established by the US EPA to protect the public health from six criteria pollutants, including carbon monoxide and particulate matter (US EPA, 2006).  As recommended by ASHRAE, pollutant levels of fresh air introduced to a building should not exceed the NAAQS levels (ASHRAE, 1989).  The NAAQS were adopted by reference in the Building Officials & Code Administrators (BOCA) National Mechanical Code of 1993 (BOCA, 1993), which is now an HVAC standard included in the Massachusetts State Building Code (SBBRS, 1997).  According to the NAAQS, carbon monoxide levels in outdoor air should not exceed 9 ppm in an eight-hour average (US EPA, 2006).

Carbon monoxide should not be present in a typical, indoor environment.  If it is present, indoor carbon monoxide levels should be less than or equal to outdoor levels.  On the day of assessment, outdoor carbon monoxide concentrations were non-detect (ND) (Table 1).  No measurable levels of carbon monoxide were detected inside the building (Table 1).

### Particulate Matter

The US EPA has established NAAQS limits for exposure to particulate matter.  Particulate matter is airborne solids that can be irritating to the eyes, nose and throat.  The NAAQS originally established exposure limits to particulate matter with a diameter of 10 μm or less (PM10).  According to the NAAQS, PM10 levels should not exceed 150 microgram per cubic meter (μg/m3) in a 24-hour average (US EPA, 2006).  These standards were adopted by both ASHRAE and BOCA.  Since the issuance of the ASHRAE standard and BOCA Code, US EPA established a more protective standard for fine airborne particles.  This more stringent PM2.5 standard requires outdoor air particle levels be maintained below 35 μg/m3 over a 24-hour average (US EPA, 2006).  Although both the ASHRAE standard and BOCA Code adopted the PM10 standard for evaluating air quality, MDPH uses the more protective PM2.5 standard for evaluating airborne particulate matter concentrations in the indoor environment.

Outdoor PM2.5 concentrations were measured at 7 μg/m3 (Table 1).  PM2.5 levels measured indoors ranged from 1 to 25 μg/m3 (Table 1), which were below the NAAQS PM2.5 level of 35 μg/m3.  Frequently, indoor air levels of particulates (including PM2.5) can be at higher levels than those measured outdoors.  A number of mechanical devices and/or activities that occur in schools can generate particulate during normal operations.  Sources of indoor airborne particulates may include but are not limited to particles generated during the operation of fan belts in the HVAC system, cooking in the cafeteria stoves and microwave ovens; use of photocopiers, fax machines and computer printing devices; operation of an ordinary vacuum cleaner and heavy foot traffic indoors.

### Volatile Organic Compounds

Indoor air quality can also be negatively influenced by the presence of materials containing volatile organic compounds (VOCs).  VOCs are carbon-containing substances that have the ability to evaporate at room temperature.  Frequently, exposure to low levels of total VOCs (TVOCs) may produce eye, nose, throat and/or respiratory irritation in some sensitive individuals.  For example, chemicals evaporating from a paint can stored at room temperature would most likely contain VOCs.  In an effort to identify materials that can potentially increase indoor VOC concentrations, BEH staff examined classrooms and common areas for products containing these respiratory irritants.

The majority of classrooms contained dry erase boards and related materials.  Materials such as dry erase markers and dry erase board cleaners may contain VOCs, such as methyl isobutyl ketone, n-butyl acetate and butyl-cellusolve (Sanford, 1999), which can be irritating to the eyes, nose and throat.  One classroom had a number of cans of spray paint in a sink cabinet accessible to students (Picture 39).  Spray paints contain VOCs that can be irritating and are flammable as well, therefore, should be located in an area inaccessible to students.

Several areas that contain photocopiers and laminators are not equipped with local mechanical exhaust ventilation to help reduce excess heat and odors (Table 1).  Lamination machines melt plastic and give off odors and VOCs.  VOCs and ozone can be produced by photocopiers, particularly if the equipment is older and in frequent use.  Ozone is a respiratory irritant (Schmidt Etkin, 1992).

Plug in air deodorizers and other scented materials (i.e., reed/oil diffusers) were observed in some areas (Table 1/Pictures 40 and 41).  Air deodorizers can contain chemicals that can be irritating to the eyes, nose and throat of sensitive individuals.  Furthermore, deodorizing agents do not remove materials causing odors, but rather mask odors that may be present in the area.

In an effort to reduce noise from sliding desks/chairs, tennis balls had been sliced open and placed on the base of the legs (Table 1).  Tennis balls are made of a number of materials that are a source of respiratory irritants.  Constant wearing of tennis balls can produce fibers and cause VOCs to off-gas.  Tennis balls are made with a natural rubber latex bladder, which becomes abraded when used as a chair leg pad.  Use of tennis balls in this manner may introduce latex dust into the school environment.  Some individuals are highly allergic to latex (e.g., spina bifida patients) (SBAA, 2001).  It is recommended that the use of materials containing latex be limited in buildings to reduce the likelihood of symptoms in sensitive individuals (NIOSH, 1997).

### Other Conditions

Other conditions that can affect indoor air quality were observed during the assessment.  In several classrooms, items were observed on the floor, windowsills, tabletops, counters, bookcases and desks.  The large number of items stored in classrooms provides a source for dusts to accumulate.  These items (e.g., papers, folders, boxes) make it difficult for custodial staff to clean.  Items should be relocated and/or be cleaned periodically to avoid excessive dust build up.  In addition, these materials can accumulate on flat surfaces (e.g., desktops, shelving and carpets) in occupied areas and subsequently be re-aerosolized causing further irritation.  Accumulated dusts/debris and cobwebs were seen in classrooms and other areas throughout the school (Table 1).

A number of air diffusers, exhaust/return vents and personal fans (Picture 14 through 16 and 42) were observed to have accumulated dust.  If exhaust vents are not functioning, backdrafting can occur, which can re-aerosolize accumulated dust particles.  Re-activated univents and fans can also aerosolize dust accumulated on vents/fan blades.

Filters are reportedly changed once per year, which may be less frequent than recommended by the manufacturer.  It has been the experience of BEH IAQ staff that most schools change filters 2 to 4 times per year, usually during school vacations.  Changing filters can enhance the univents efficient removal of particles from the airstream.

An accumulation of chalk dust and dry erase particulate was observed in some classrooms (Picture 43).  When windows are opened or univents are operating, these materials can become airborne.  Once aerosolized, they can act as irritants to eyes and the respiratory system.

The unused shower area of the boy’s locker room was being used for storage.  The shower room has drains are equipped with traps.  Without regular water input, the traps for these drains can dry out which can lead to sewer gas odors penetrating the room through unsealed traps.  Sewer gas odors can be irritating to the eyes, nose, and throat.

Finally, piles of wood dust and debris were observed on wood cutting machines and flat surfaces in the wood shop.  It appeared that the room contains a local exhaust system dedicated to collecting dust from equipment, however, at the time of the assessment a shop-vac was set up to draw wood dust to exhaust out of an exterior door (Pictures 44 and 45), which can lead to security issues.

During the assessment, BEH staff found damaged insulation material that likely contained asbestos.  The presence of this material and the recommendation to encapsulate it by a licensed asbestos remediation firm was documented in a letter released subsequent to the MDPH inspection (Appendix B).

# Recommendations

The conditions related to indoor air quality problems at the DMS raise a number of issues.  The general building conditions, maintenance, work hygiene practices and the condition of HVAC equipment, if considered individually, present conditions that could degrade indoor air quality.  When combined, these conditions can serve to further degrade indoor air quality.  Some of these conditions can be remedied by actions of building occupants.  Other remediation efforts will require alteration to the building structure and equipment.  It is important to note that DPS has reportedly hired an architectural firm to complete a building-wide feasibility study of the DMS addressing current and future needs of the building.  [Note: DPS has reportedly submitted a statement of interest to the Massachusetts School Building Authority (MSBA) as a first step to address future needs.]

For these reasons, a two-phase approach is required for remediation.  The first consists of short-term measures to improve air quality and the second consists of long-term measures that will require planning and resources to adequately address the overall indoor air quality concerns.

The following short-term measures should be considered for implementation:

- Examine each univent and AHU for function.  Consider consulting an HVAC engineer concerning the calibration of univent fresh air control dampers throughout the school.

- Operate all ventilation systems throughout the building (e.g., gymnasium, locker rooms, cafeteria, classrooms) continuously during periods of school occupancy.  To increase airflow in classrooms, set univent controls to “high”.

- Inspect exhaust motors and belts for proper function.  Repair and replace as necessary.

- Remove all blockages from univents and exhaust vents to ensure adequate airflow.

- Close classroom doors to maximize air exchange.

- Increase filter changes for HVAC equipment (e.g., univents, AHUs and ACs).  Filter changes for HVAC equipment should be changed as per the manufacturer’s instructions or more frequently if needed.  Vacuum interior of units prior to activation to prevent the aerosolization of dirt, dust and particulates.  Ensure filters fit flush in their racks with no spaces in between allowing bypass of unfiltered air into the unit.

- Use openable windows in conjunction with classroom univents and exhaust vents to increase air exchange.  Care should be taken to ensure windows are properly closed at night and weekends to avoid the freezing of pipes and potential flooding.

- Consider adopting a balancing schedule of every 5 years for all mechanical ventilation systems, as recommended by ventilation industrial standards (SMACNA, 1994).

- For buildings in New England, periods of low relative humidity during the winter are often unavoidable.  Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low.  To control for dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended.  Avoid the use of feather dusters.  Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

- Ensure roof/window/plumbing leaks are repaired and remove/replace any remaining water-stained ceiling tiles.

- Move plants along the exterior of univent air intakes approximately 5-feet to prevent entrainment of pollen, moisture or mold.

- Remove clinging plants from exterior walls.

- Remove moss growth from window sills, clean and disinfect.

- Seal window panes and frames to prevent water penetration drafts and pest entry.

- Seal spaces in masonry/joints and univent fresh air intakes.

- Contact a masonry firm or general contractor to repair holes/breaches in exterior walls to prevent water penetration, drafts and pest entry.

- Make repairs to exterior doors to seal holes.

- Relocate or consider reducing the amount of materials stored in classrooms to allow for more thorough cleaning of classrooms.  Clean items regularly with a wet cloth or sponge to prevent excessive dust build-up.

- Clean personal fans, univent air diffusers, return vents and exhaust vents periodically of accumulated dust.

- Clean chalkboards and dry erase board trays regularly to avoid the build-up of particulates.

- Consider providing local exhaust ventilation for photocopiers and laminations machines, or relocate to an area with mechanical ventilation.

- Restore operation of the local wood dust collection system in the wood shop, make repairs as needed.  Ensure that excess wood dust is cleaned after completion of projects.

- Ensure flammable products (e.g., spray paints) are stored in proper cabinets inaccessible to students.

- Cap abandoned plumbing fixtures in locker rooms (sinks, showers, water fountains) or ensure water is poured into the drains every other day (or as needed) to maintain the integrity of the traps.

- Refrain from using air fresheners and deodorizers to prevent exposure to VOCs.

- For more advice on mold please consult the document “Mold Remediation in Schools and Commercial Buildings” published by the US Environmental Protection Agency (US EPA, 2001).  Copies of this document can be downloaded from the US EPA website at: http://www.epa.gov/iaq/molds/mold_remediation.html.

- Consider adopting the US EPA (2000) document, “Tools for Schools”, as an instrument for maintaining a good indoor air quality environment in the building.  This document is available at: http://www.epa.gov/iaq/schools/index.html.

- Refer to resource manual and other related indoor air quality documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings.  These documents are available at: http://www.state.ma.us/dph/MDPH/iaq/iaqhome.htm.

The following long-term measures should be considered:

- Contact an HVAC engineering firm for an assessment of the ventilation system’s control system (e.g., controls, air intake louvers, thermostats).  Based on the age, physical deterioration and availability of parts for ventilation components, such an evaluation is necessary to determine the operability and feasibility of repairing/replacing the equipment.

- Consider having exterior walls re-pointed and waterproofed to prevent water intrusion.  This measure should include a full building envelope evaluation.

- Consider replacing window systems to prevent air infiltration and water penetration.

- Replace damaged exterior doors.

- Consideration should be made for a full roof replacement to prevent chronic leaks.

- Consider creating a centralized location of heat/odor producing office equipment (e.g., photocopiers/lamination machines) equipped with local exhaust ventilation.

# References

ACGIH.  1989.  Guidelines for the Assessment of Bioaerosols in the Indoor Environment.  American Conference of Governmental Industrial Hygienists, Cincinnati, OH.

ASHRAE.  1989.  Ventilation for Acceptable Indoor Air Quality.  American Society of Heating, Refrigeration and Air Conditioning Engineers. ANSI/ASHRAE 62-1989

BOCA.  1993.  The BOCA National Mechanical Code/1993.  8th ed.   Building Officials and Code Administrators International, Inc., Country Club Hill, IL.

ELI.  2009.  Environmental Measurements, Duxbury Middle School Guidance Department, Envirotest Lab, Inc.  Dated January 20, 2009.

Lstiburek, J. & Brennan, T.  2001.  Read This Before You Design, Build or Renovate.  Building Science Corporation, Westford, MA.  U.S. Department of Housing and Urban Development, Region I, Boston, MA

MDPH.  1997.  Requirements to Maintain Air Quality in Indoor Skating Rinks (State Sanitary Code, Chapter XI).  105 CMR 675.000.  Massachusetts Department of Public Health, Boston, MA.

NIOSH.  1997.  NIOSH Alert Preventing Allergic Reactions to Natural Rubber latex in the Workplace.  National Institute for Occupational Safety and Health, Atlanta, GA.

OSHA.  1997.  Limits for Air Contaminants.  Occupational Safety and Health Administration.  Code of Federal Regulations.  29 C.F.R 1910.1000 Table Z-1-A.

Sanford.  1999.  Material Safety Data Sheet (MSDS No: 198-17).  Expo( Dry Erase Markers Bullet, Chisel, and Ultra Fine Tip.  Sanford Corporation.  Bellwood, IL.

SBBRS.  1997.  Mechanical Ventilation.  State Board of Building Regulations and Standards.  Code of Massachusetts Regulations.  780 CMR 1209.0

Schmidt Etkin, D.  1992.  Office Furnishings/Equipment & IAQ Health Impacts, Prevention & Mitigation.  Cutter Information Corporation, Indoor Air Quality Update, Arlington, MA.

SMACNA.  1994.  HVAC Systems Commissioning Manual.  1st ed.  Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

US EPA.  2000.  Tools for Schools.  Office of Air and Radiation, Office of Radiation and Indoor Air, Indoor Environments Division (6609J). EPA 402-K-95-001, Second Edition.  http://www.epa.gov/iaq/schools/tools4s2.html

US EPA.  2001.  Mold Remediation in Schools and Commercial Buildings. US Environmental Protection Agency, Office of Air and Radiation, Indoor Environments Division, Washington, D.C.  EPA 402-K-01-001.  March 2001.

US EPA.  2006.  National Ambient Air Quality Standards (NAAQS).  US Environmental Protection Agency, Office of Air Quality Planning and Standards, Washington, DC.  http://www.epa.gov/air/criteria.html.

Picture 1

1960’s Vintage Univent

Picture 2

1970’s Vintage Univent

Picture 3

Ceiling-Mounted Univent

Picture 4

Univent Fresh Air Intake

Picture 5

Univent Fresh Air Intakes Covered with Metal Hoods

Picture 6

Univent Control Switches, Note Unit Switched to the “Off” Position

Picture 7

Univent Fresh Air Intake (in courtyard) Sealed With Plywood

Picture 8

Univent Fresh Air Intake (along front of building) Sealed With Cardboard and Duct Tape

Picture 9

Ceiling-Mounted Exhaust Vent

Picture 10

Wall-Mounted Exhaust Vent

Picture 11

Exhaust Vent Obstructed by Classroom Furniture

Picture 12

Rooftop AHUs

Picture 13

Ceiling-Mounted AHU in Gym

Picture 14

Ceiling-Mounted Supply Diffuser, Note Accumulated Dust/Debris

Picture 15

Ceiling-Mounted Return Vent, Note Accumulated Dust/Debris

Picture 16

Wall-Mounted Return Vent, Note Accumulated Dust/Debris

Picture 17

Water Damaged Ceiling Tiles in Classroom

Picture 18

Water Damaged Ceiling Tiles

Picture 19

Water Damaged Ceiling Tiles, Wallboard and Peeling Vinyl Wall Paper in the Upper Library

Picture 20

Water Damaged Wallboard and Peeling Vinyl Wall Paper in the Upper Library

Picture 21

Close-Up of Water Damaged Wallboard in Upper Library

Picture 22

“New” Floor to Ceiling Paneled Wall in Classroom 212

Picture 23

“New” Floor to Ceiling Paneled Wall in Classroom 212

Picture 24

Overgrown Plants/Shrubs/Trees against Exterior Walls in Courtyard

Picture 25

Overgrown Plants/Shrubs/Trees against Exterior Walls in Courtyard

Picture 26

Over Grown Shrubs/Plants against Exterior Wall

Picture 27

Overgrown Shrubs against Exterior Wall in Courtyard, Note Fresh Air Intake for Univent

Picture 28

Missing Damaged Sealant in Expansion Joint, Pen Inserted by BEH to Show Depth

Picture 29

Missing Damaged Sealant around Univent Air Intake

Picture 30

Damaged/Corroded Metal Exterior Doors

Picture 31

Close-Up of Damaged/Corroded Metal Exterior Doors

Picture 32

Clinging Plants on Exterior Brick

Picture 33

Loose Caulking on Exterior Window Sill

Picture 34

Severely Damaged/Missing Caulking around Exterior Windows

Picture 35

Severely Damaged/Missing Caulking around Exterior Windows

Picture 36

Severely Damaged/Missing Caulking around Exterior Window Frame

Picture 37

Moss Growth Inside Window Pane

Picture 38

Moss Growth Inside and Outside of Window Pane

Picture 39

Multiple Cans of Spray Paint in Classroom Cabinet under Sink

Picture 40

Plug-in Air Deodorizer

Picture 41

Reed/Oil Deodorizer

Picture 42

Personal Fan in Classroom with Accumulated Dust/Debris on Fan Blades

Picture 43

Accumulated Chalk Dust

Picture 44

Shop-Vac in Wood Shop with Exhaust Hose in Open Exterior Door

Picture 45

Exhaust Hose from Shop-Vac (in Wood Shop) in Open Exterior Door

| Location/ Room | Occupants in Room | Temp (°F) | Relative Humidity (%) | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | PM2.5 (µg/m3) | Windows Openable | Ventilation | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| background |  | 53 | 46 | 364 | ND | 7 |  |  |  | Cool, sunny |
| 320 | 2 | 75 | 32 | 807 | ND | 6 | Y Open | Y | Y | 22 occupants gone ~5 mins, 2 WD CTs, DO, TB, PF |
| 321 | 22 | 75 | 33 | 702 | ND | 3 | Y Open | Y | Y | Heat complaints, DO |
| 322 | 1 | 73 | 37 | 735 | ND | 4 | Y | Y | Y | 22 occupants gone ~15 mins, 5 WD CTs |
| Prep Room |  |  |  |  | ND | 2 | N | Y | Y | 3 WD CT |
| 324 | 24 | 75 | 37 | 853 | ND | 2 | Y | Y | Y | DO, 3 WD CT, 4 Damaged CT |
| 315 | 22 | 75 | 40 | 1073 | ND | 6 | Y | Y | Y off | 8 WD CT, TB, DO, cobwebs/acuum dust debris corners |
| 314 | 18 | 76 | 40 | 1231 | ND | 6 | Y | Y | Y off | Exhaust off, TB, WD CTs |
| 312 | 26 | 75 | 36 | 885 | ND | 4 | Y | Y | Y | TB, 3 WD CT, PF, DO, exhaust-dust/debris |
| 311 | 0 | 76 | 36 | 751 | ND | 4 | Y | Y | Y | DO, 4 WD CT |
| 412 | 0 | 71 | 32 | 452 | ND | 1 | Y | Y | Y | Classroom unoccupied, divider wall removed/replaced due to mold growth, tile mastic around floor tiles |
| 411 | 4 | 71 | 38 | 784 | ND | 3 | Y | Y off | Y off | UV and exhaust off, WD CT-High moisture (damp) active leak near windows |
| 410 | 0 | 71 | 35 | 584 | ND | 3 | N | Y | Y | Dusty CTs around supply vent |
| Library Upper |  |  |  |  | ND |  |  | Y | Y | WD CTs previous roof leak-reportedly repaired summer 09, WD peeling vinyl wallpaper, moistened wallboard beneath wallpaper under WD CTs |
| 418 | 0 | 71 | 38 | 784 | ND | 3 | Y | Y off | Y off | Supply and exhaust off, 8 WD CTs-dry/low moisture, rusty metal ceiling rails |
| Teacher’s Lounge | 9 | 73 | 36 | 754 | ND | 6 | N | Y off | Y off | Supply and exhaust off, dust-ceiling |
| Guidance Main | 3 | 73 | 37 | 758 | ND | 5 | N | Y off | Y off | Supply and exhaust off |
| Guidance Conf Room | 8 | 73 | 42 | 1154 | ND | 6 | N | Y off | Y off | Supply and exhaust off, DEM odors |
| Guidance Corbin Office | 0 | 73 | 39 | 845 | ND | 5 | N | Y off | Y off | Supply and exhaust off |
| 99 | 18 | 72 | 40 | 1128 | ND | 4 | Y | Y | Y off | Exhaust off, TB |
| 101 | 2 | 70 | 36 | 700 | ND | 3 | Y | Y | Y | DO, plants |
| 103 | 0 | 70 | 40 | 943 | ND | 5 | Y | Y off | Y | Supply off, occupants at lunch, plug-in air freshener |
| 105 | 27 | 71 | 42 | 1074 | ND | 5 | Y Open | Y | Y | Window broken-open/duct tape, PF, items on UV |
| 107 | 27 | 71 | 46 | 1280 | ND | 3 | Y | Y | Y | TB, DO |
| 109 | 0 | 71 | 46 | 1746 | ND | 3 | Y | Y | Y | Occupants at lunch, exhaust blocked with poster, mastic around floor tiles, exposed pipe insulation near UV possible asbestos-recommended encapsulation |
| 201 | 1 | 73 | 36 | 985 | ND | 6 | Y | Y off | Y off | UV and exhaust off, UV reportedly deactivated due to noise |
| 202 | 0 | 74 | 42 | 1213 | ND | 25 | Y | Y off | Y off/weak | UV off, exhaust off/weak, DO |
| Auditorium | 0 | 71 | 35 | 430 | ND | 2 | N | Y | Y |  |
| 422 | 1 | 74 | 30 | 632 | ND | 3 | Y | Y | Y | Stored items on UV; DEM; DO |
| 323 | 1 | 73 | 32 | 662 | ND | 4 | Y | Y | Y | Exhaust near door to prep room; DEM |
| 325 | 25 | 73 | 33 | 819 | ND | 4 | Y 1 open | Y | Y | DO |
| 313 | 23 | 73 | 37 | 954 | ND | 5 | Y | Y | Y | Exhaust near door to prep room; AT; DEM; DO; TB |
| 312/313 prep | 0 | 73 | 35 | 849 | ND | 4 | N | Y | Y |  |
| 409 | 0 | 71 | 30 | 548 | ND | 3 | N | Y |  | Debris/dust on vents; DEM; 2 DO; PF |
| 414 | 6 | 74 | 34 | 585 | ND | 3 | Y | Y off | Y | DEM; DO; Exterior door |
| 413 | 24 | 72 | 34 | 772 | ND | 3 | Y | YV on | Y | Stored items on UV; WD CTs above UV; DEM; DO; Exterior door – bees nest |
| Library |  | 66 | 46 | 685 | ND | 4 |  | Y |  | WD along windows; PC with no exhaust; vinyl wallpaper |
| 416 | 0 | 70 | 40 | 694 | ND | 4 | N | Y | N | WD CTs; 2 DO; PF; DEM |
| 522 | 0 | 76 | 33 | 684 | ND | 4 | N | Y off | Y off dust | Ventilation off; Computer lab; PF; DO |
| Guidance Main | 3 | 73 | 33 | 732 | ND | 6 | N | Y |  | PC; microwave |
| Guidance Limmer | 0 | 73 | 34 | 752 | ND | 5 | N | Y | N | DO |
| Guidance Epstein | 0 | 73 | 38 | 1082 | ND | 5 | N | Y | N | DO |
| Guidance Closed Door | 0 | 73 | 35 | 717 | ND | 4 | N | Y | N |  |
| 100 | 0 | 71 | 32 | 517 | ND | 3 | Y | Y | N | CPs; DEM |
| 102 | 0 | 73 | 33 | 717 | ND | 4 | Y | Y | Y weak | Plants; DEM; DO; PF |
| 104 | 0 | 73 | 37 | 1284 | ND | 6 | Y | Y off | Y weak blocked by board | Bags on top of UV; DEM; PF |
| 106 | 6 | 73 | 38 | 1039 | ND | 6 | Y | N | N | PC; PF; microwave; refrigerator |
| 108 | 18 | 73 | 32 | 794 | ND | 4 | Y 1 open | Y off | Y weak |  |
| 200 | 4 | 71 | 39 | 875 | ND | 3 | Y | Y off | Y in bathrooms | 2 bathrooms with exhaust vents, switch on wall; WD CTs; DEM; DO; microwave |
| 204 | 0 | 72 | 39 | 918 | ND | 5 | Y | Y off | Y weak | DEM; DO |
| 203 | 0 | 72 | 38 | 978 | ND | 5 | Y | Y off | Y off | DEM |
| 205 | 17 | 73 | 38 | 1084 | ND | 5 | Y 1 open | Y off | Y |  |
| 206 | 18 | 73 | 43 | 1258 | ND | 7 | Y | Y off | Y weak | PF |
| 207 | 20 | 73 | 40 | 1474 | ND | 7 | Y | Y off | Y | PF; DEM odor |
| 208 | 0 | 72 | 35 | 920 | ND | 7 | Y | Y off | Y weak | DO |
| 209 | 0 | 72 | 36 | 862 | ND | 5 | Y | Y off | Y blocked | Plants on UV; PF; DEM; DO |
| 210 | 1 | 72 | 35 | 892 | ND | 4 | Y | Y off | Y weak | DEM |
| 520 | 1 | 74 | 33 | 694 | ND | 5 | N | Y off | Y off | Ventilation off; DO |
| 415 | 1 | 75 | 31 | 678 | ND | 5 | N | Y off | Y off | Ventilation off |
| Print Room | 1 | 75 | 31 | 675 | ND | 14 | N | Y off | Y off | Ventilation off; debris/dust on ceiling around vents; PC in use; laminator; DO |
| 518 | 1 | 74 | 30 | 584 | ND | 9 | N | Y off | Y off | Ventilation off; CD; PF; WD CTs; DO |
| General Music | 16 | 71 | 41 | 959 | ND | 6 | N | Y off | Y off | Ventilation off; WD CTs; DEM |
| 514 | 1 | 71 | 30 | 488 | ND | 4 | Y 1 open | Y off | Y off | CPs; DEM; TB |
| 512 | 0 | 72 | 42 | 1288 | ND | 9 | Y | Y off | Y off | 22 occupants gone 1 minute; AD; CPs; DO; microwave; refrigerator; stove |
| 512 therapy OT/PT | 0 | 71 | 43 | 1402 | ND | 8 | Y | Y off | Y off |  |
| Band Office | 0 | 71 | 40 | 1138 | ND | 7 | N | Y off | Y off |  |
| Band Practice room 1 | 0 | 71 | 41 | 1242 | ND | 5 | N | Y off | Y off |  |
| Band Practice room 2 | 0 | 71 | 42 | 1220 | ND | 5 | N | Y off | Y off |  |
| Band Room | 0 | 71 | 40 | 1132 | ND | 8 | Y | Y | Y | WD CTs; DEM; space around exterior door |
| Wood Shop | 0 | 70 | 36 | 751 | ND | 7 | Y | Y | Y | Sawdust on equipment, floor and surfaces; portable shop vacuum in use as exhaust; TB; saw exposed |
| Server Room | 0 | 72 | 41 | 858 | ND | 10 | N | Y |  | Network server; beanbag seats |
| Kiln Room |  |  |  |  |  |  |  |  | Y | Kiln has dedicated local exhaust |
| 136 Art Room | 0 | 72 | 32 | 432 | ND | 2 | Y | Y | Y | Space around exterior door |
| 145 Art Room | 20 | 72 | 38 | 849 | ND | 5 | Y | Y | Y | Aqua; PF; DO |
| 175 | 0 | 72 | 31 | 469 | ND | 5 | Y 1 open | Y | Y | DO |
| Boys Locker Room | 0 | 71 | 32 | 481 | ND | 4 | N | Y | Y | Showers used as storage |
| Lower Gym | 20 | 68 | 31 | 420 | ND | 3 | N | Y | Y | 2 of 4 exterior doors open |
| Small Gym | 13 | 69 | 37 | 548 | ND | 4 | N | Y | Y |  |
| Gym | 0 | 70 | 30 | 428 | ND | 2 | N | Y | Y |  |
| Café | 0 | 70 | 46 | 1368 | ND | 9 | Y | 2 UVs off | Y |  |