# Background

| Building: | Executive Office of Health and Human Services (EOHHS) Service Center |
| --- | --- |
| Address: | 300 Howard Street, Framingham, MA |
| Assessment Requested by: | Deborah Coleman, Facilities Director, EOHHS |
| Reason for Request: | Concerns about allergies/health and indoor air quality (IAQ) |
| Date of Assessment: | January 12, 2017 |
| Massachusetts Department of Public Health/Bureau of Environmental Health (MDPH/BEH) Staff Conducting Assessment: | Ruth Alfasso, Environmental Engineer/Inspector, IAQ Program |
| Date of Building Construction: | Pre-1900s |
| Building/Site Description: | DCF is located on the second story, of a former manufacturing plant that has been completely renovated into state offices. |
| Building Population: | Approximately 200 employees on two floors with members of the public visiting daily |
| Windows: | Openable in some areas, but generally not opened |

# Methods

Please refer to the IAQ Manual for methods, sampling procedures, and interpretation of results (MDPH, 2015).

# IAQ Testing Results

Note that this building has been visited by the IAQ program on several occasions since the EOHHS service center occupied these offices in 2015; reports from these visits can be found on the IAQ webpage at http://www.mass.gov/eohhs/gov/departments/dph/programs/environmental-health/exposure-topics/iaq/iaq-rpts/.

This visit concentrated on several areas of concern on the second floor occupied by the Department of Children and Families (DCF) and a few areas on the first floor occupied by the Department of Transitional Assistance (DTA) rather than the entire office building.

The following is a summary of indoor air testing results (Table 1).

- Carbon dioxide levels were below 800 parts per million (ppm) in all but one area assessed, indicating adequate fresh air in the space.

- Temperature was within the recommended range of 70°F to 78°F in all areas assessed.

- Relative humidity was within or close to the lower end of the recommended range of 40% to 60% in all areas assessed.

- Carbon monoxide levels were non-detectable in all indoor areas assessed.

- Fine particulate matter (PM2.5) concentrations measured were below the National Ambient Air Quality Standard (NAAQS) level of 35 μg/m3 in all areas assessed.

## Ventilation

A heating, ventilating, and air conditioning (HVAC) system has several functions. First, it provides heating and, if equipped, cooling. Second, it is a source of fresh air. Finally, an HVAC system will dilute and remove normally occurring indoor environmental pollutants by not only introducing fresh air, but also filtering the airstream and ejecting stale air to the outdoors via exhaust ventilation. Even if an HVAC system is operating as designed, point sources of respiratory irritation may exist and affect symptoms in sensitive individuals. The following analysis examines and identifies components of the HVAC system and likely sources of respiratory irritant/allergen exposure due to water damage, aerosolized dust, and/or chemicals found in the indoor environment.

Fresh air is provided by air handling units (AHUs) located on the roof. Air from the AHUs is filtered, heated/cooled, and delivered to rooms via ducted supply vents (Picture 1). Air is returned/exhausted through ducted return vents (Picture 2). It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).

Along one side of the building, sunlight could be seen streaming in through the windows (Picture 3). Adjustable blinds should be used to control solar gain within the occupied space and assist with temperature control as well as reducing glare.

## Microbial/Moisture Concerns

Water-damaged and some obviously wet ceiling tiles were observed in many places on the second floor (Table 1; Pictures 1, 4 and 5). These indicate that the roof has leaked, which has been an ongoing problem since the offices were occupied. Examination of the roof revealed that parts of the roof have subsided below the level of the roof drains which allows water to pool (Picture 6) and eventually penetrate through seams or holes in the roof. Holes in the roof should be repaired as they are discovered, and consideration should be given to a more thorough repair of the roof, including slope and drains. All leaks should be reported to building management as soon as they are discovered, and water-damaged ceiling tiles should be removed and replaced. If areas have chronic leaks, temporary use of special ceiling tile inserts that can capture and direct water via a hose into a container to reduce the chance of water damage to building materials and furnishings. The containers need to be monitored and emptied at least daily.

Plants were observed in office areas (Table 1; Picture 7). Plants can be a source of pollen and mold, which can be respiratory irritants to some individuals. Plants should be properly maintained and equipped with drip pans to prevent water damage to porous materials. Plants should also be located away from air diffusers to prevent the aerosolization of dirt, pollen, and mold.

Small refrigerators and water dispensers were observed in carpeted areas (Table 1). These appliances may spill or leak and lead to carpet damage and microbial growth. It is recommended that these appliances be located in areas without carpeting or on waterproof mats; in many cases carpet squares had been replaced with tile in the area of water dispensers. Refrigerators should be kept clean to prevent odors and microbial growth.

## Other IAQ Evaluations

Exposure to low levels of total volatile organic compounds (TVOCs) may produce eye, nose, throat, and/or respiratory irritation in some sensitive individuals. BEH/IAQ staff examined rooms for products containing VOCs. BEH/IAQ staff noted hand sanitizers, cleaners, air freshener products, and dry erase materials in use within the building (Pictures 8 and 9; Table 1). All of these products have the potential to be irritants to the eyes, nose, throat, and respiratory system of sensitive individuals.

Items were observed on many windowsills in the office, including some that are subject to direct sunlight (Picture 3). Items containing plastic, cardboard, or inks/paints may release odors and VOCs when heated; these items should not be placed in direct sunlight.

Cooking equipment, including toasters, microwave ovens and coffee machines were located in various parts of the office space. Food areas and cooking equipment need to be kept clean to prevent odors and pests.

Mousetraps were observed in several areas, although staff reported that rodents were not currently an issue in this office. Rodent infestation can result in indoor air quality related symptoms due to materials in their wastes. Mouse urine contains a protein that is a known sensitizer (US EPA, 1992). A sensitizer is a material that can produce symptoms (e.g., running nose or skin rashes) in sensitive individuals after repeated exposure. To eliminate exposure to allergens, rodents must be removed from the building. Please note that removal, even after cleaning, may not provide immediate relief since allergens can exist in the interior for several months after rodents are eliminated (Burge, 1995). Once the infestation is eliminated, a combination of cleaning and increased ventilation and filtration should serve to reduce allergens associated with rodents.

In some areas, stored materials and accumulated items make it more difficult for custodial staff to clean. Items for clients, such as clothing and toys, were stored in the open in some areas (Picture 10) which can allow for dusts to accumulate, create harborage for pests, or allow for hidden water damage when leaks occur. Items should be stored neatly, preferably on shelves or in closable bins, and moved periodically to allow for wet wiping and vacuuming of surfaces.

In some areas, decorative items were observed hanging from the ceiling tile system. Hanging items from the ceiling tiles can create dust and allow debris from above the tiles into occupied spaces.

Personal fans were observed in a number of areas (Table 1; Picture 11). Fan blades to some of these units had settled dust, which can be reaerosolized when the fan is activated.

The rooftop AHU for Section 4 on the second floor was opened and examined. The filter was soiled and in need of changing (Picture 11). It could not be determined at what frequency the filters were currently being changed. Filters in the AHUs should be changed no less frequently than twice a year; if filters are significantly soiled when they are changed, the frequency should be increased. A log of when filters are changed should be kept for reference and to ensure these goals are met. Filters should be of a pleated type with a Minimum Efficiency Reporting Value (MERV) of 8 or better, and should fit flush into the AHU cabinets without gaps.

The offices were mostly carpeted. Carpets should be cleaned annually (or semi-annually in soiled/high traffic areas) in accordance with Institute of Inspection, Cleaning and Restoration Certification (IICRC) recommendations, (IICRC, 2012).

# Conclusions/Recommendations

Based on observations at the time of assessment, the following is recommended:

- Operate supply and exhaust ventilation in all areas during occupied periods.

- Have the HVAC system balanced every 5 years in accordance with SMACNA recommendations (SMACNA, 1994).

- Ensure filters are changed in all AHU a minimum of twice a year, more frequently if filters are significantly soiled between changes. A log should be kept of filter changes to ensure this occurs. Filters with a MERV value of 8 or higher that properly fit the AHUs should be used.

- Use blinds to reduce solar heating and glare. Avoid storing items on windowsills that may emit odors and VOCs when heated.

- For buildings in New England, periods of low relative humidity during the winter are often unavoidable. Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low. To control for dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended. Avoid the use of feather dusters. Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

- Use a reporting system to ensure that water-damaged and wet ceiling tiles and other leaks are reported promptly and removed/repaired.

- Avoid storing materials in areas with chronic leaks. Consider the use of ceiling-tile replacements to catch leaks and drain them through a hose to a container of an appropriate volume. If used, the container must be monitored and emptied daily and kept clean to avoid odors.

- Have the roof patched as needed. Consideration undertaking a complete overhaul of the roof including ensuring roof drains can function properly.

- Keep indoor plants in good condition, avoid overwatering, and avoid placing them on porous items such as carpets or paper. Also, keep plants out of the air stream of supply vents.

- Consider locating refrigerators and water dispensers in non-carpeted areas or place on a waterproof mat. Clean refrigerator spills promptly and clean refrigerators out regularly to avoid odors and microbial growth.

- Reduce use of products containing VOCs including eliminating air freshening products.

- Ensure cooking areas/equipment are kept clean to prevent odors and pests. Consider reducing the number of areas where food is stored and locating them away from occupied areas.

- Use the principles of Integrated Pest Management (IPM) and the services of a licensed pest control operator to remove rodents and reduce the potential for pest infestation. Ensure that any area where rodents may have been is thoroughly cleaned to remove allergens.

- Reduce accumulated materials on flat surfaces and move periodically to allow for thorough cleaning.

- Store items for clients such as clothing and toys in an organized manner, preferably in closed totes or on shelves to prevent dust accumulation and reduce harborage for pests.

- Avoid hanging items from the ceiling tiles to avoid create dust and allowing debris from above the ceiling tiles into occupied spaces.

- Clean the blades of personal fans, supply, and exhaust vents periodically to avoid aerosolizing dusts.

- Clean carpeting in accordance with IICRC recommendations (IICRC, 2012).

- Refer to resource manual and other related IAQ documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings. These documents are available at: http://mass.gov/dph/iaq.

# References

Burge, H.A. 1995. Bioaerosols. Lewis Publishing Company, Boca Raton, FL.

IICRC. 2012. Institute of Inspection, Cleaning and Restoration Certification. Carpet Cleaning: FAQ. Retrieved from http://www.iicrc.org/consumers/care/carpet-cleaning.

MDPH. 2015. Massachusetts Department of Public Health. Indoor Air Quality Manual: Chapters I-III. Available at: http://www.mass.gov/eohhs/gov/departments/dph/programs/environmental-health/exposure-topics/iaq/iaq-manual/.

SMACNA. 1994. HVAC Systems Commissioning Manual. 1st ed. Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

US EPA. 1992. Indoor Biological Pollutants. US Environmental Protection Agency, Environmental Criteria and Assessment Office, Office of Health and Environmental Assessment, research Triangle Park, NC. EPA 600/8-91/202. January 1992.

Picture 1

Supply vent, note water-damaged ceiling tiles

Picture 2

Return vent

Picture 3

Sunlight through window, note plastic items on windowsill

Picture 4

Wet, bulging ceiling tile

Picture 5

Water-damaged and missing ceiling tiles

Picture 6

Water pooling on the roof due to poor slope to roof drains

Picture 7

Plants on a windowsill

Picture 8

Plug-in air freshener

Picture 9

Air freshener/cleaner

Picture 10

Toys stored on the floor in piles

Picture 11

Soiled AHU filter

Picture 12

Dusty personal fan

| Location | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | Temp (°F) | Relative Humidity (%) | PM2.5 (µg/m3) | Occupants in Room | Windows Openable | Ventilation | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| Background | 362 | 1.0 | 62 | 55 | 13 |  |  |  |  | Warm and humid |
| Second Floor, DCF areas |
| Kitchen | 702 | ND | 70 | 51 | 6 | 1 | Y | N | Y | Refrigerator, toaster, microwave, NC |
| Half wall office next to kitchen | 676 | ND | 70 | 45 | 7 | 2 | N | Y | Y |  |
| 2311 cubes | 880 | ND | 70 | 46 | 7 | 1 | N | Y | Y |  |
| 2297 half wall office | 730 | ND | 70 | 45 | 6 | 1 | N | Y | Y |  |
| 2309 | 646 | ND | 71 | 45 | 6 | 2 | N | Y | Y |  |
| Half wall office | 692 | ND | 71 | 44 | 7 | 1 | N | Y | Y |  |
| 2306 | 700 | ND | 71 | 44 | 6 | 2 | N | Y | Y |  |
| 2294 half wall office | 800 | ND | 72 | 43 | 6 | 1 | N | Y | Y |  |
| 2304 | 668 | ND | 72 | 43 | 5 | 1 | N | Y | Y | Plants |
| 2293 half wall office | 621 | ND | 73 | 41 | 4 | 0 | N | Y | Y | PF, HS |
| 2303 cubes | 714 | ND | 73 | 41 | 4 | 0 | N | Y | Y | PC in hall |
| 2204 office | 633 | ND | 73 | 40 | 7 | 0 | N | Y | Y | DO, PF, HS |
| 2203 office | 568 | ND | 71 | 40 | 7 | 0 | N | Y | Y | DEM |
| 2315 cubes | 515 | ND | 72 | 41 | 7 | 1 | N | Y | Y |  |
| 2202 office | 601 | ND | 72 | 40 | 6 | 0 | N | Y | Y |  |
| 2261 cubes | 646 | ND | 72 | 43 | 3 | 3 | N | Y | Y | PF, heater, CP/AF, HS |
| 2269-2272 cubes | 642 | ND | 72 | 41 | 7 | 1 | N | Y | Y | AI, WD CT (reported previous week), decorative items |
| 2276 cubes | 626 | ND | 73 | 41 | 7 | 2 | N | Y | Y | WD CT (2) |
| 2281 cubes | 626 | ND | 73 | 40 | 7 | 3 | N | Y | Y | Sunlight, decorative items, WD CT, HS |
| 3386 cubes | 625 | ND | 73 | 40 | 8 | 2 | N | Y | Y | WD CT |
| Goldman half-wall office | 685 | ND | 74 | 40 | 8 | 1 | N | Y | Y | WD carpet in hall (old stain) |
| Ramos half-wall office | 670 | ND | 74 | 40 | 7 | 0 | N | Y | Y | Food |
| 2302 half wall office | 681 | ND | 74 | 39 | 7 | 0 | N | Y | Y | PF |
| 2292 cubes | 647 | ND | 74 | 40 | 7 | 1 | N | Y | Y | Plant |
| 2213 storage |  |  |  |  |  |  | N | Y |  | NC, storage items, WD CT (no items underneath) |
| 2206 janitor closet |  |  |  |  |  |  | N | Y | N | NC, no exhaust, CP, mops |
| 2212 (IT) |  |  |  |  |  |  | N | Y | N | Computers |
| Storage |  |  |  |  |  |  | N | Y | Y | Boxes on floor |
| Women’s restroom |  |  |  |  |  |  |  | Y | Y | Exhaust is small, dusty, operating |
| Men’s Restroom |  |  |  |  |  |  |  | Y | Y | Exhaust is small, operating |
| Second floor, Section 5 |
| 2221 files |  |  |  |  |  |  |  |  |  | WD and missing CT, NC |
| 2220 kitchen | 493 | ND | 72 | 39 | 7 | 0 | N | Y | Y | NC, WD CT, toaster and fridge, vending had leaked in the past |
| Cubes next to kitchen | 603 | ND | 74 | 38 | 7 | 3 | N | Y | Y | Clothing and items |
| 2222 office | 522 | ND | 74 | 36 | 8 | 0 | N | Y | Y | Plant, coffee |
| 2223 office | 549 | ND | 73 | 36 | 7 | 0 | N | Y | Y | Heater |
| 2225 | 540 | ND | 73 | 37 | 10 | 0 | N | Y | Y | 4 WD CT, water stain on wall |
| 2226 | 508 | ND | 73 | 36 | 7 | 0 | N | Y | Y | WD CT, fridge on carpet, HS |
| 2227 office | 495 | ND | 74 | 37 | 8 | 0 | N | Y | Y | Plug-in AF |
| 2228 office | 506 | ND | 73 | 38 | 7 | 0 | N | Y | Y | AI on floor |
| 2230 office | 550 | ND | 73 | 38 | 7 | 3 | N | Y | Y | DEM, plants, fridge on carpet |
| 2231 office | 647 | ND | 73 | 38 | 7 | 0 | N | Y | Y | Coffee |
| Open storage area |  |  |  |  |  |  |  | Y | Y | Messy, clothes and items stored openly |
| 2345 cubes | 528 | ND | 73 | 38 | 7 | 1 | N | Y | Y |  |
| 2340 cubes | 527 | ND | 73 | 37 | 7 | 2 | N | Y | Y | Plants, toys |
| Cubes | 517 | ND | 73 | 37 | 7 | 2 | N | Y | Y | Decorations |
| 2353 cube | 552 | ND | 74 | 39 | 8 | 1 | N | Y | Y | DEM, items on windowsill, HS |
| Stairwell |  |  |  |  |  |  |  |  |  | Odor in stairwell, handle warm to the touch |
| 2360 cube | 556 | ND | 74 | 39 | 7 | 2 | N | Y | Y | DEM, food |
| cubes | 562 | ND | 74 | 39 | 7 | 9 | N | Y | Y | WD CT, sunlight, plants and items on windowsill |
| 2279 cubes | 555 | ND | 74 | 39 | 7 | 1 | N | Y | Y |  |
| Cubes | 561 | ND | 75 | 39 | 8 | 3 | N | Y | Y | DEM, CP |
| 2223 | 595 | ND | 75 | 39 | 7 | 0 | N | Y | Y |  |
| 2251 kitchen | 528 | ND | 75 | 38 | 7 | 0 | N | Y | Y | NC, fridge and microwave |
| 2396 | 621 | ND | 75 | 37 | 7 | 4 | N | Y | Y | Items on windowsill |
| Cubes | 645 | ND | 75 | 35 | 7 | 2 | N | Y | Y | CP, clothing |
| 2415 | 680 | ND | 75 | 35 | 7 | 1 | N | Y | Y | Items hanging from ceiling, PF, HS |
| 2259 office | 642 | ND | 75 | 35 | 7 | 0 | N | Y | Y | Food, plants, PF |
| 2254 | 652 | ND | 74 | 35 | 7 | 0 | N | Y | Y | Upholstered items |
| 2255 conference | 657 | ND | 74 | 36 | 7 | 0 | N | Y | Y | Old vault boarded up, no wallboard, reports of drafts |
| 2257 office | 717 | ND | 74 | 36 | 7 | 0 | N | Y | N | DO |
| 2401 cubes | 705 | ND | 74 | 36 | 7 | 5 | n | y | y | Plants |
| First Floor DTA areas |
| 1152 and area | 747 | ND | 74 | 34 | 6 | 0 | N | Y | Y | Area of leak one year ago, wallboard all replaced 12-18 inches above ground |
| 1154 office | 695 | ND | 74 | 33 | 6 | 0 | N | Y | Y | Plants, HS, PF |
| 1157 office | 751 | ND | 74 | 34 | 6 | 1 | N | Y | N |  |
| Cube area | 669 | ND | 74 | 32 | 6 | 2 | N | Y | Y | HS, DEM |

# Text boxes

INDOOR AIR QUALITY ASSESSMENT

EOHHS Service Center

300 Howard Street

Framingham, Massachusetts

Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health

Indoor Air Quality Program

January 2017