Ted Hoefler			RE: HAVERHILL - Metropolitan

Ogden Martin Systems of Haverhill, Inc.		Boston/Northeast Region

100 Recovery Way					310 CMR 7.08(2) - Municipal Waste Combustors

Haverhill, MA 01835					Application No. MBR-98-ECP-007

Transmittal No. 201602										EMISSION CONTROL PLAN

FINAL APPROVAL

Dear Mr. Hoefler:

The Metropolitan Boston/Northeast Region of the Department of Environmental Protection (the “Department”), Bureau of Waste Prevention, has reviewed your Municipal Waste Combustor (MWC) Emission Control Plan (ECP) submittal.  This ECP submittal details how emission limitations and compliance schedules for the control of certain designated pollutants according to 310 CMR 7.08(2) – Municipal Waste Combustors (MWCs), will be implemented for equipment located at the Ogden Martin Systems of Haverhill (OMSH) facility located at 100 Recovery Way, Haverhill, Massachusetts.  This application bears the signature of Mr. Gary Crane as the designated legally responsible official for OMSH.

LEGAL AUTHORITY

On December 19, 1995, EPA adopted New Source Performance Standards (NSPS) for new MWCs (40 CFR 60 Subpart Eb), and Emission Guidelines (EG) for existing MWCs (40 CFR 60 Subpart Cb). The emission guidelines were amended by EPA on October 24, 1997. The NSPS apply to facilities that commenced construction after September 20, 1994, and the EG apply to facilities that commenced construction on or prior to September 20, 1994.  Both the NSPS and the EG apply to large MWC units, that is, those combusting greater than 250 tons per day of municipal solid waste (MSW).  Because OMSH was constructed prior to September 20, 1994, and your two combustion units burn greater than 250 tons per day of MSW, your facility is subject to 40 CFR 60 Subpart Cb “Emission Guidelines” and 310 CMR 7.08(2).  In addition, the Department has imposed further requirements, including materials separation requirements, a requirement for electronic filing of compliance data, cumulative impact requirements, and lowered the emission limitation for mercury from the Federal limit of 0.080 milligrams per dry standard cubic meter (mg/dscm) to 0.028 mg/dscm.  With the exception of the emission limitation for mercury, the Commonwealth has adopted Emission Limits identical to the Federal EG into regulation under 310 CMR 7.08(2), “Municipal Waste Combustors” as contained in 310 CMR 7.00 “Air Pollution Control Regulations” adopted by the Department pursuant to the Massachusetts General Laws, Chapter 111, Sections 142 A-M.

The MWC Regulation requires any person who owns, leases, operates or controls a large municipal waste combustor unit to comply with 310 CMR 7.08(2) in its entirety. The MWC ECP was submitted in accordance with Regulation 310 CMR 7.08(2)(j).

The purpose of 310 CMR 7.08(2) is to provide emission limitations and compliance schedules for the control of certain designated pollutants emitted from Municipal Waste Combustors, in accordance with the requirements contained in sections 111(d) and 129 of the Clean Air Act.  310 CMR 7.08(2) establishes requirements for the following:

Operating Practices (Carbon Monoxide (CO), Flue Gas Temperature, Load Level)

Metals (Mercury (Hg), Lead (Pb), Cadmium (Cd))

Particulate Matter (PM)

Opacity

Organics (Dioxin/Furan)

Acid Gases (Sulfur Dioxide (SO2), Hydrogen Chloride (HCl))

Nitrogen Oxides (NOx)

Fugitive Ash Emissions

Applicable requirements and limitations contained in 310 CMR 7.08(2) shall not supersede, relax or eliminate any more stringent conditions or requirements (e.g. emission limitation(s), testing, record keeping, reporting, or monitoring requirements) established by regulation or contained in a facility's previously issued source specific plan approval(s) or emission control plan(s). Furthermore, the facility must amend its operating permit application to include the approved emission control plan.

Based upon the above, the Department has determined that the referenced ECP Application is administratively and technically complete and that the proposed modifications are in conformance with current air pollution control engineering practices and hereby grants Final ECP Approval for the proposed modifications of your municipal waste combustor units, with the conditions listed below.

EQUIPMENT DESCRIPTION

The following emission units (Table 1) are subject to and regulated by this ECP approval:

| Table 1+ |  |  |  |
| --- | --- | --- | --- |
| EMISSION UNIT (EU#) | DESCRIPTION OF EMISSION UNIT | EU DESIGN CAPACITY | PROPOSED POLLUTION CONTROL DEVICE (PCD) |
| EU 1 | Mass Burn Incinerator/Water Wall Boiler | 381.56 MMBtu/hr Heat Input 225,000 lbs/hr of steam @ 865 psig/830 degrees F | Two (2) No. 2 Fuel Oil Fired 55 MMBtu/hr Auxiliary Burners [AB] (PCD 1) |
|  |  |  | Selective Non-Catalytic Reduction with Aqueous Ammonia Injection [SNCR] (PCD 2) |
|  |  |  | Powdered Activated Carbon Injection System [PACI] (PCD 3) |
|  |  |  | Spray Drier Absorber with Lime Slurry Injection [SDA] (PCD 4) |
|  |  |  | Pulse Jet , 13 Module, Fabric Filter/Baghouse [FF/BH] (PCD 5) |
| EU 2 | Mass Burn Incinerator/Water Wall Boiler | 381.56 MMBtu/hr Heat Input 225,000 lbs/hr of steam @ 865 psig/830 degrees F | Two (2 ) No. 2 Fuel Oil Fired 55 MMBtu/hr AB (PCD 6) |
|  |  |  | SNCR (PCD 7) |
|  |  |  | PACI (PCD 8) |
|  |  |  | SDA (PCD 9) |
|  |  |  | FF/BH (PCD 10) |
| EU 3 | Ash Handling and Fugitive Emissions | 112,500 SCFM @ 68 degrees F | Five (5) roof mounted ventilation fans, each fan capable of handling 22,500 SCFM @ 68 degrees F; each fan is equipped with a high efficiency particulate filter (PCD 11, 12, 13, 14 and 15) |
|  |  |  | Enclosed Buildings and Conveyors |

+	Legend to Abbreviated Terms within Table 1:

EU# = Emission Unit Number

PCD# = Pollution Control Device

F = Fahrenheit

MMBtu/hr = million British thermal units per hour

lbs/hr = pounds per hour

psig = pounds per square inch gauge

ACFM = Actual Cubic Feet per Minute

APPLICABLE  REQUIREMENTS

A. EMISSION LIMITS AND RESTRICTIONS

The facility is subject to the emission limits/restrictions as contained in Table 2 below:

| Table 2 + |  |  |  |  |
| --- | --- | --- | --- | --- |
| EU# | RESTRICTION/OPERATING PRACTICES | POLLUTANT | EMISSION LIMIT/STANDARD | APPLICABLE REGULATION AND/OR APPROVAL NUMBER |
| EU 1, EU 2 | Unit Load < 110% of maximum demonstrated load, calculated in 4-hour block arithmetic averages, measured during the most recent dioxin/furan compliance test in which compliance is achieved 3 PM control device inlet temperature < 17C (30F) above maximum demonstrated PM control device inlet temperature, calculated in 4-hour block arithmetic averages, measured during the most recent dioxin/furan compliance test in which compliance is achieved 3 | PM | < 27 mg/dscm at 7% O2 dry basis 1 | 310 CMR 7.08(2)(f)2 |
|  |  | Opacity | < 10% (6 minute average) | 310 CMR 7.08(2)(f)2 |
|  |  | Cd | < 0.040 mg/dscm at 7% O2 dry basis | 310 CMR 7.08(2)(f)2 |
|  |  | Pb | < 0.440 mg/dscm at 7% O2 dry basis | 310 CMR 7.08(2)(f)2 |
|  |  | Hg | < 0.028 mg/dscm at 7% O2 dry basis | 310 CMR 7.08(2)(f)2 |
|  |  | SO2 | < 29 ppm by volume at 7% O2 dry basis or 75% reduction by weight or volume, whichever is less stringent. Compliance is based on a 24-hour geometric mean. | 310 CMR 7.08(2)(f)2 |
|  |  | HCl | < 29 ppm by volume at 7% O2 dry basis or 95% reduction by weight or volume, whichever is less stringent. | 310 CMR 7.08(2)(f)2 |
|  |  | Dioxan/Furan | < 30 ng/dscm at 7% O2 dry basis with FF | 310 CMR 7.08(2)(f)2 |
|  |  | CO | < 100 ppm by volume at 7% O2 dry basis at combustor outlet . Compliance is based on a 4-hour block average. | 310 CMR 7.08(2)(f)1.a.i. |
|  |  | NOx | < 205 ppm by volume at 7% O2 dry basis (24-hour daily arithmetic average) | 310 CMR 7.08(2)(f)3 |
| EU 3 |  | Fugitive Ash | Visible emissions < 9 minutes per 3 hour period 2 | 310 CMR 7.08(2)(f)5 |

Table 2 Notes:

1	No person shall cause, suffer, allow, or permit emissions from any incinerator of any particles that have a dimension greater than 100 microns. (Be referred to 310 CMR 7.06(2))

2	No person subject to 310 CMR 7.08(2) shall cause, suffer, allow or permit the discharge into the atmosphere of any visible emissions of combustion ash from an ash conveying system (including transfer points) in excess of 5 percent of the observation period (nine minutes per three hour period). This emission limit does not cover visible emissions discharged inside buildings or enclosures of ash conveying systems; however the emission limit does apply to visible emissions discharged to the atmosphere from buildings or enclosures of ash conveying systems. This subsection does not apply during maintenance and repair of ash conveying systems. Maintenance and repair of the ash conveying systems must be done in accordance with best management practices.

3	No person subject to 310 CMR 7.08(2) shall:

- cause, suffer, allow or permit a municipal waste combustor unit to operate at a load level (based on steam load) greater than 110 percent of the maximum demonstrated municipal waste combustor unit load calculated in 4-hour block arithmetic averages, measured during the most recent dioxin/furan compliance test in which compliance is achieved; and

- cause, suffer, allow or permit a municipal waste combustor unit to operate at a temperature, measured at the PM control device inlet, exceeding 17 C (30 F) above the maximum demonstrated PM control device temperature, calculated in 4-hr block arithmetic averages, measured during the most recent dioxin/furan compliance test in which compliance is achieved.

Table 2, Note 3 continued:

During any nine month dioxin/furan compliance test and the 2 weeks preceding each nine month dioxin/furan  compliance test, municipal waste combustor unit load limit and PM control device temperature limitations are not applicable.

Municipal waste combustor unit load limit and PM control device temperature limitations may be waived, if prior approval is granted by the Department, for the purposes of evaluating system performance, testing new technology or control technologies, diagnostic testing, or related activities for the purpose of improving facility performance provided that there is an improvement in controlling air pollution, or advancing the state-of-the-art for controlling facility emissions.

Emission limits apply at all times except during periods of start-up, shutdown or malfunction as defined in 40 CFR Part 60.58b.

+	Legend to Abbreviated Terms within Table 2:

EU# = Emission Unit Number

mg/dscm = milligram per dry standard cubic meter

ng/dscm = nanogram per dry standard cubic meter

ppm = parts per million

Cd = Cadmium

Pb = Lead

Hg = Mercury

NH3 = Ammonia

NOx = Nitrogen Oxides

CO = Carbon Monoxide

PM = Particulate Matter

HCl = Hydrogen Chloride

SO2 = Sulfur Dioxide

O2 = Oxygen

% = percent

C = Degrees Centigrade

F = Degrees Fahrenheit

< = less than or equal to

B. COMPLIANCE DEMONSTRATION

Any person subject to 310 CMR 7.08(2) that is subject to 310 CMR 7.00 and 310 CMR 19.00 shall be in compliance with, or on a Department approved compliance schedule to meet, all provisions of 310 CMR 7.00 and 310 CMR 19.00 and any plan approval, order, notice of noncompliance or permit issued thereunder. The facility is subject to the monitoring/testing, record keeping, and reporting requirements as contained in Tables 3, 4 and 5 below and 310 CMR 7.08, as well as the applicable requirements contained in Table 2:

| Table 3 + |  |
| --- | --- |
| EU# | MONITORING/TESTING REQUIREMENTS |
| EU 1, EU 2 | In accordance with 310 CMR 7.08(2)(g), complete initial performance test for dioxin/furan and mercury (Hg) within 180 days after the final compliance date of December 19, 2000. |
|  | Following the date of the initial performance test for dioxin/furan, the facility shall conduct compliance tests for dioxin/furan emissions according to one of the schedules specified below, as required by 310 CMR 7.08(2)(g)1.a. and b.: a. conduct compliance test for dioxin/furan emissions on all municipal waste combustor unit(s) on a nine month basis, or b. for municipal waste combustor unit(s) where all compliance tests for all unit(s) over a 27 month period indicate that dioxin/furan emissions are less than or equal to 7 nanograms per dry standard cubic meter total mass (ng/dscm), corrected to 7 percent oxygen, the facility may elect to conduct compliance tests for one unit every nine months. At a minimum, a compliance test for dioxin/furan emissions shall be conducted every nine months following the previous compliance test for one unit at the municipal waste combustor plant. Every nine months a different unit at the municipal waste combustor plant shall be tested, and the units at the plant shall be tested in sequence (e.g., unit 1, unit 2, unit 3, as applicable). The facility may continue to conduct compliance testing on only one unit per nine month basis so long as the dioxin/furan emissions remain less than or equal to 7 ng/dscm @ 7% O2. If any nine month compliance test indicates dioxin/furan emissions greater than the specified limit, compliance tests shall thereafter be conducted on all units at the plant every nine months until and unless all nine month compliance test for all units at the plant over a 27 month period indicate dioxin/furan emissions less than or equal to the 7 ng/dscm @ 7% O2. |
|  | In accordance with 310 CMR 7.08(2)(g)1.d., for municipal waste combustor units where carbon injection (or equivalent) is used to comply with the dioxin/furan emission limits specified in section 310 CMR 7.08(2)(f)2. or the dioxin/furan emission limit specified in 310 CMR 7.08(2)(g)1.b, measure and calculate the carbon (or equivalent) usage rate following the procedures specified in 40 CFR 60.58b(m) effective December 19, 1995 and as amended October 24, 1997. |
|  | In accordance with 310 CMR 7.08(2)(g)2., following the date of the initial performance test for Hg, compliance testing for Hg shall be conducted on all municipal waste combustor unit(s)on a quarterly basis. Compliance with the emissions limit specified in 310 CMR 7.08(2)(f) 2. Shall be based on the average of four quarterly compliance tests per rolling twelve months but shall not exceed 0.080 mg/dscm in any quarterly test. If compliance with the Hg emission limit has been achieved in each quarter for eight consecutive quarters, the facility may elect to perform compliance testing on a nine month basis. Any municipal waste combustor unit(s) which cannot achieve compliance with the emission limitation in 310 CMR 7.08(2)(f) 2. During the nine month compliance test shall resume quarterly compliance testing as specified above. |
|  | In accordance with 310 CMR 7.08(2)(g)3., for municipal waste combustor unit(s) which employ a carbon injection (or equivalent) Hg emission control system, conduct optimization tests. These tests will determine the optimum feed rate for the Hg emissions control apparatus by determining the carbon (or equivalent) feed rate at which the emissions of Hg are equal to or less than the applicable limit at 310 CMR 7.08(2)(f) 2. The optimization test shall be conducted as follows: a. The optimization tests shall be performed during the initial performance test, after a change in carbon (or equivalent), upon request by the Department, upon request by the facility or annually if required under 310 CMR 7.08(2)(g)4. b. If there are identical municipal waste combustor units at the municipal waste combustor plant, then optimization tests may be performed on one unit, and the resulting parameters applied to the other unit(s) which are identical to that unit at that plant. c. Within 30 calendar days of the conclusion of any optimization test, the facility shall submit to the Department for approval a proposed optimized carbon (or equivalent) feed rate which minimizes Hg emissions. An approvable feed rate is the feed rate such that a higher feed rate achieves insignificant additional reductions in Hg emissions compared to the amount of carbon (or equivalent) added. The carbon (or equivalent) feed rate approved by the Department shall be used to operate the carbon injection (or equivalent) Hg control system until the next optimization test is performed and the feed rate approved. |
|  | In accordance with 310 CMR 7.08(2)(g)6., the facility shall conduct compliance testing for all designated pollutants every nine months for each municipal waste combustor unit(s). Compliance testing for dioxin/furan and Hg shall be as specified in 310 CMR 7.08(2)(g)1. and 2. |
|  | In accordance with 310 CMR 7.08(2)(g)5.a. and b., Continuous Emissions Monitoring Systems (CEMS) which monitor NOx, SO2, and operating practices parameters (e.g., CO, unit load and PM control device inlet temperature) shall obtain at a minimum valid continuous emissions monitoring system data for 75% of the hours per day, 75% of the days per month, and 90% of the hours per quarter that the municipal waste combustor unit is combusting municipal solid waste. CO CEMS installed and operated in accordance with Performance Specification 4 of 40 CFR Part 60, Appendix B, will satisfy the requirements in 310 CMR 7.08(2)(g). |
| EU3 | Monitor visible emissions associated with ash handling and fugitive operations to insure compliance with visible emission standards as specified in Table 2. |

| Table 4 + |  |
| --- | --- |
| EU# | RECORD KEEPING REQUIREMENTS |
| EU 1, EU 2 | In accordance with 310 CMR 7.08(2)(h)9., the results of the initial performance tests and all nine month compliance tests conducted to determine compliance with the PM, opacity, Cd, Pb, Hg, dioxin/furan, HCl, and fugitive ash emission limits shall be recorded along with supporting calculations and submitted to the Department within 90 days after the test. In addition, the results of the quarterly Hg compliance tests shall also be recorded and submitted to the Department within 30 days after the test. |
|  | For the initial dioxin/furan performance test and all subsequent dioxin/furan compliance tests recorded under 7.08(2)(h), the maximum demonstrated municipal waste combustor load level and maximum PM control device inlet temperature (for each PM control device) shall be recorded along with supporting calculations, as required by 310 CMR 7.08(2)(h)10. |
|  | As required by 310 CMR 7.08(2)(h)4., for municipal waste combustor unit(s) that apply carbon (or equivalent) for Hg or dioxin/furan control, maintain the following records: a. The average carbon (or equivalent) mass feed rate (in lbs/hr) estimated as required under 40 CFR 60.58b(m)(1)(i) effective December 19, 1995 and as amended October 24, 1997, during the initial Hg performance test and all subsequent compliance tests, with supporting calculations. b. The average carbon (or equivalent) mass feed rate (in lbs/hr) estimated for each hour of operation as required under 40 CFR 60.58b(m)(1)(ii) effective December 19, 1995 and as amended October 24, 1997, during the initial dioxin/furan performance test and all subsequent nine month compliance tests, with supporting calculations. c. The average carbon (or equivalent) mass feed rate (in lbs/hr) estimated for each hour of operation as required under 40 CFR 60.58b(m)(3)(ii) effective December 19, 1995 and as amended October 24, 1997, with supporting calculations. d. The total carbon (or equivalent) usage for each calendar quarter estimated as specified under 40 CFR 60.58b(m)(3) effective December 19, 1995 and as amended October 24, 1997, with supporting calculations. e. The carbon (or equivalent) injection system operating parameter data for the parameter(s) that are the primary indicator(s) of carbon (or equivalent) feed rate. |
|  | As required by 310 CMR 7.08(2)(h)13., for municipal waste combustor units that apply carbon (or equivalent) for Hg or dioxin/furan control: a. Identification of the calendar dates when the average carbon (or equivalent) mass feed rates recorded under 310 CMR 7.08(2)(h)4.c. were less than either of the hourly carbon feed rates estimated during compliance tests for Hg or dioxin/furan emissions and recorded under paragraphs 310 CMR 7.08(2)(h) 4. a. or b., respectively, with reasons for such feed rates and a description of corrective actions taken. b. Identification of the calendar dates when the carbon injection (or equivalent) system operating parameter(s) that are the primary indicator(s) of carbon mass feed rate (or equivalent) recorded under 310 CMR 7.08(2)(h) 4. e., are below the level(s) estimated during the compliance tests as specified in 40 CFR 60.58b(m)(1)(i) and 60.58b(m)(1)(ii)effective December 19, 1995 and as amended October 24, 1997, with reasons for such occurrences and a description of corrective actions taken. |
|  | In accordance with 310 CMR 7.08(2)(h)2., record the emission concentrations and parameters measured using continuous emissions monitoring systems. The measurements specified below shall be recorded and shall be available for submittal to the Department or for onsite review by an inspector: a. All 6-minute average opacity levels as specified under 40 CFR 60.58b(c) effective December 19, 1995 and as amended October 24, 1997, including the highest level measured. b. All 1-hour average SO2 emission concentrations as specified under 40 CFR 60.58b(e) effective December 19, 1995 and as amended October 24, 1997. c. All 1-hour average NOx emission concentrations as specified under 40 CFR 60.58b(h) effective December 19, 1995 and as amended October 24, 1997. d. All 1-hour average CO emission concentrations, municipal waste combustor unit load measurements, and PM control device inlet temperatures as specified under 40 CFR 60.58b(i) effective December 19, 1995 and as amended October 24, 1997. e. All 24-hour daily geometric average SO2 emission concentrations and all 24-hour daily geometric average percent reductions in SO2 emissions as applicable, as specified under 40 CFR 60.58b(e) effective December 19, 1995 and as amended October 24, 1997 including the highest level recorded. f. All 24-hour daily arithmetic average NOx emission concentrations as specified under 40 CFR 60.58b(h) effective December 19, 1995 and as amended October 24, 1997, including the highest level recorded. g. All 4-hour block average CO emission concentrations, as applicable, as specified under 40 CFR 60.58b(i) effective December 19, 1995 and as amended October 24, 1997, including the highest level recorded. h. All 4-hour block arithmetic average municipal waste combustor unit load levels (steam flow) and PM control device inlet temperature as specified under 40 CFR 60.58b(I) effective December 19, 1995 and as amended October 24, 1997, including the highest level recorded. |
|  | As required by 310 CMR 7.08(2)(h)3., record the calendar dates when any of the average emissions concentrations or percent reductions, or operating parameters recorded under section 7.08(2)(h) 2., exceed the applicable limits, with detailed specific reasons for such exceedances and a description of corrective actions taken. |
|  | As required by 310 CMR 7.08(2)(h)5., record the calendar dates and time periods for which the minimum number of hours of any of the data specified below have not been obtained including reasons for not obtaining sufficient data and a description of corrective actions taken: a. SO2 emissions data. b. NOx emissions data. c. CO emissions data. d. Municipal waste combustor unit load data, including PM control device inlet temperature data. |
|  | As required by 310 CMR 7.08(2)(h)6., record each occurrence that SO2 emissions data, NOx emissions data, or operational data (e.g. CO emissions, unit load, and PM control device temperature) have been excluded from the calculation of average emission concentrations or parameters, along with detailed and specific reasons for excluding the data. |
|  | As required by 310 CMR 7.08(2)(h)7., record the results of daily drift tests and quarterly accuracy determinations for SO2, NOx, and CO continuous emission monitoring systems, as required under 40 CFR, Part 60, Appendix F, Procedure 1. |
|  | As required by 310 CMR 7.08(2)(h)8., record each occurrence of a start-up, shut-down or malfunction, including the specific reasons for each occurrence, date, time, and unit involved. Average emissions concentrations or percent reductions, or operating parameters recorded under section 7.08(2)(h) 2., shall be recorded during start-up, shut-down or malfunction. |
|  | In accordance with 310 CMR 7.08(2)(h)11., maintain records showing the names of the municipal waste combustor chief facility operator, shift supervisors, and control room operators who are certified by ASME (Operator Certification and Provisional Certification), including the dates of initial and renewal certifications and documentation of current certification. Records showing the names of the municipal waste combustor chief facility operator, shift supervisors, and control room operators who have completed the EPA municipal waste combustor operator training course if required. |
|  | In accordance with 310 CMR 7.08(2)(h)12., maintain the records showing the names of the persons who have completed a review of the operating manual as required by section 7.08(2)(f) 6. d. including the date of the initial review and subsequent annual reviews. |
|  | As required by 310 CMR 7.08(2)(h)1., maintain the calendar date of each record. |
|  | The facility shall maintain records of the information specified in this section, as applicable, for each municipal waste combustor unit. All records shall be retained at the facility for at least 5 years, in accordance with 310 CMR 7.08(2)(h) and shall be made available to Department personnel upon request. |
| EU 3 | Maintain records of the compliance status of visible emissions associated with ash handling and fugitive operations. |

| Table 5 + |  |
| --- | --- |
| EU# | REPORTING REQUIREMENTS |
| EU 1, EU 2 | As required by 310 CMR 7.08(2)(i), the facility shall submit an initial performance report as well as an annual report of the information specified in 310 CMR 7.08(2)(i) 1., as applicable. The facility which elects to follow the compliance testing schedule specified in 310 CMR 7.08(2)(g) 1.b., shall follow the procedures specified in section 310 CMR 7.08(2)(i) 1. for reporting the selection of this schedule. Annual Reporting Requirementsa – The information specified in (a.) through (g.) below shall be reported: a. 310 CMR 7.08(2)(h) 2.a., e. through h. for the highest emission levels recorded. b. 310 CMR 7.08(2)(h) 4.a. and b. c. 310 CMR 7.08(2)(h) 5. – 6. d. 310 CMR 7.08(2)(h) 8. – 10. e. Summary of a. through d. for the previous year. f. The performance evaluation of the continuous emission monitoring system using the applicable performance specifications in Appendix B of 40 CFR, Part 60. g. A notification of intent to begin the reduced dioxin/furan compliance testing schedule specified in section 310 CMR 7.08(2)(g) 1. b. during the following calendar year. |
|  | The facility shall submit a semiannual report that includes the information specified in 310 CMR 7.08(2)(i) 2. For any recorded pollutant or parameter that does not comply with the emission limits as set forth in 310 CMR 7.08(2). Semi-Annual Reporting Requirementsb - The information specified in a. through e. below shall be reported: a. 310 CMR 7.08(2)(h) 2.a., e. through h. for each date recorded in 310 CMR 7.08(2)(h)3. b. 310 CMR 7.08(2)(h) 3. c. 310 CMR 7.08(2)(h) 4.c. d. 310 CMR 7.08(2)(h) 9.c e. 310 CMR 7.08(2)(h) 13. |
|  | As required by 310 CMR 7.08(2)(i), in meeting the reporting requirements of 310 CMR 7.08(2)(i)1. And 310 CMR 7.08(2)(i)2., the facility shall report the information in a format determined by the Department that is designed to be understandable and informative to the public. The information shall be submitted in written format and electronic format. |

a	Annual reports shall be submitted to this Office  no later than February 15 of each year following the calendar year in which the data was collected.

b	Semiannual reports shall be submitted according to the schedule specified: (1) If data reported in accordance with section 310 CMR 7.08(2)(i)2 were collected during the first calendar half, then the report shall be submitted on or before August 1 following the first calendar half; (2) If data reported in section 310 CMR 7.08(2)(i)2 were collected during the second calendar half, then the report shall be submitted on or before February 15 following the second calendar half.

c	Include only the reports which document emission levels that were above the applicable requirements and the corrective actions taken.

+	Legend to Abbreviated Terms within Tables 3, 4 and 5:

EU# = Emission Unit Number

mg/dscm = milligram per dry standard cubic meter

ng/dscm = nanogram per dry standard cubic meter

Cd = Cadmium

Pb = Lead

Hg = Mercury

NOx = Nitrogen Oxides

CO = Carbon Monoxide

PM = Particulate Matter

HCl = Hydrogen Chloride

SO2 = Sulfur Dioxide

O2 = Oxygen

% = percent

Unit load is based on steam flow

## COMPLIANCE  SCHEDULE

As required by 310 CMR 7.08(2)(k), the subject municipal waste combustor unit(s) shall be in full compliance with the applicable requirements of 310 CMR 7.08(2):

| TABLE 6 |  |
| --- | --- |
| Activity | Date |
| All contracts involving required air pollution control systems and required process modifications will be awarded by: | May 18, 1999 |
| Completion of on-site construction or installation of air pollution control equipment or process modifications will be achieved by: | November 19, 2000 |
| Compliance will be achieved by: | December 19, 2000 |

The OMSH facility shall submit documentation that each above activity has been completed to this Office within 7 days of the compliance date for each activity identified in Table 6 above.

### SPECIAL CONDITIONS FOR ECP

- The OMSH facility shall comply with the requirements contained in Tables 2, 3, 4, and 5 on and after December 19, 2000.

- The OMSH facility shall not combust sewage sludge in any of the municipal waste combustor units.

- The OMSH facility shall conduct an optimization/minimization testing program over a period of one year regarding the operation of the SNCR system at the facility to insure that the emission of ammonia (ammonia slip) is minimized while insuring adequate NOx controls. OMSH shall submit a protocol for the testing program to the Department at least 30 days before the initiation of the testing program. Such testing shall be witnessed by a representative of the Department. A test report shall be submitted to the Department within 90 days of the completion of the ammonia optimization/minimization testing program. Based on the results of the optimization/minimization testing program, the Department shall include in the ECP a term to limit ammonia emissions. This term may be an emission limit, a process parameter, or other provision that insures that emissions of ammonia are minimized. Inclusion of this term to limit ammonia emissions into the ECP will be deemed a modification to the ECP under 310 CMR 7.08(2). The term to limit ammonia emissions will be specifically set forth as a “state only” enforceable requirement in the ECP.

- The OMSH facility may use untreated landfill leachate as a source of process water for the air pollution control system.

GENERAL CONDITIONS FOR ECP

## SITE ASSIGNMENT

In accordance with 310 CMR 7.08(2)(a), no person shall, suffer, allow, or permit the construction, substantial reconstruction, alteration or operation of a municipal waste combustor unit on a site which has not received a site assignment in accordance with M.G.L. c.111, s.150A.

## COMPLIANCE AND PERFORMANCE TESTING

As required by 310 CMR 7.08(2)(g), the facility shall comply with the provisions of 40 CFR 60.58b, "Compliance and performance testing", effective December 19, 1995 and as amended October 24, 1997, the provisions of which are hereby incorporated by reference. Compliance with the applicable requirements as set forth in 310 CMR 7.08(2)(f) and Section B of this ECP, shall be determined in accordance with 40 CFR 60.58b, except as provided under 310 CMR 7.08(2)(g)1., 2., 3., 4., 5., and 6, and as specified within this ECP. The initial performance test must be completed within 180 days after the final compliance date.

## OPERATOR TRAINING AND CERTIFICATION

In accordance with 310 CMR 7.08(2)(f)6., the facility shall implement the following municipal waste combustor operator training and certification requirements:

a.	shall obtain and maintain an Operator Certificate issued by the American Society of Mechanical Engineers (ASME).

b.	shall not allow the municipal waste combustor unit to be operated at any time unless one of the following persons is on duty: A chief facility operator or a shift supervisor who has obtained an Operator Certificate. (A Provisional Certificate is acceptable provided the supervisor is scheduled to obtain an Operator Certificate in accordance with section (f) below). If one of the persons listed above must leave the municipal waste combustor plant during his or her operating shift, a provisionally certified control room operator who is onsite at the municipal waste combustor plant may fulfill these requirements.

c.	shall have all chief facility operators, shift supervisors, and control room operators who have not obtained an Operator Certificate from ASME complete the National Technical Information Service - "EPA Municipal Waste Combustor Operating Course."

d.	shall establish a training program to review the operating manual with each person who has responsibilities affecting the operation of an affected municipal waste combustor unit, including, but not limited to, chief facility operators, shift supervisors, control room operators, ash handlers, maintenance personnel, and crane/load handlers. The operating manual shall address at a minimum the following:

i.	A summary of all applicable requirements in this regulation;

ii.	Basic combustion theory applicable to a municipal waste combustor unit;

iii.	Procedures for receiving, handling, and feeding municipal solid waste;

iv.	Municipal waste combustor unit startup, shutdown, and malfunction procedures;

v.	Procedures for maintaining proper combustion air supply levels;

vi.	Procedures for operating the municipal waste combustor unit within the requirements established under this regulation;

vii.	Procedures for responding to periodic upset or off-specification  conditions;

viii.	Procedures for minimizing PM carryover;

ix.	Procedures for handling ash;

x.	Procedures for monitoring municipal waste combustor unit emissions; and

xi.	Reporting and recordkeeping procedures.

e.	shall make available to the Department for inspection upon request all the operating manuals and records of training.

f.	shall be in compliance with all training and certification requirements specified in 310 CMR 7.08(2)(f)6. by six months after the date of start up or August 21, 1999, whichever is later.

## ADDITIONAL REQUIREMENTS

In accordance with 310 CMR 7.08(2)(j)5., additional requirements may be included in the emission control plan approval if the Department determines that the emissions from a municipal waste combustor plant's unit(s) alone or cumulatively with other municipal waste combustor plant's unit(s) cause or contribute to a condition of air pollution or a violation of any other regulation. Such requirements include but are not limited to emissions limits on air contaminants, and additional stack testing or emission monitoring requirements.

The Department may modify the emission control plan at any time if the Department determines that a municipal waste combustor plant's unit(s) alone or cumulatively with other municipal waste combustor plant's unit(s) cause or contribute to a condition of air pollution or a violation of any other regulation.

Cumulative Impact: The Department has assessed the cumulative impact of other municipal waste combustors  within the vicinity of the OMSH MWC facility. The analysis indicated that the OMSH MWC facility would  not alone or cumulatively with any other MWC facility cause or contribute to a condition of air pollution.

MODIFICATION TO THE ECP

In accordance with 310 CMR 7.08(2)(j)7., if the Department proposes to modify a municipal waste combustor plant's emission control plan approval,  the Department shall publish a notice of public comment in accordance with M.G.L. c. 30A detailing the proposed modification.  The Department shall allow for a 30 day public comment period following the published notice. The Department will modify the emission control plan approval after the close of the public comment period.

Error! Bookmark not defined.GENERAL LEGAL RESPONSIBILITY

OMSH shall maintain continuous compliance at all times with the terms of this emission control plan approval.  This approval may be suspended, modified, or revoked by the Department if at any time the facility is violating any applicable Regulation(s) or conditions of this approval letter.

The application material submitted and this approval letter together constitute the approved emission control plan.  Where there is a conflict between the submitted information and this approval letter, this letter shall rule.

Should any nuisance condition(s) occur as a result of the operation of this facility, then OMSH shall immediately take appropriate steps to abate said nuisance conditions.

## MASSACHUSETTS ENVIRONMENTAL POLICY ACT

The Department has determined that the filing of an Environmental Notification Form (ENF) with the Secretary of Environmental Affairs, for air quality control purposes, was not required prior to this action by the Department.  Notwithstanding this determination, the Massachusetts Environmental Policy Act (MEPA) and Regulation 301 CMR 11.00 Section 11.03, provide certain "Fail Safe Provisions" which allow the Secretary to require the filing of an ENF and/or Environmental Impact Report at a later time.

Please be advised that this Final Approval does not negate the responsibility of OMSH to comply with this or any other applicable federal, state, or local regulations now or in the future.  Nor does this Final Approval imply compliance with any applicable federal, state or local regulations now or in the future.

Should you have questions concerning this matter or regarding the terms or conditions of this Final Approval, please do not hesitate to contact Edward J. Braczyk, in the Metropolitan Boston/Northeast Regional Office, 205a Lowell Street, Wilmington, Massachusetts 01887.

Very truly yours,

Edward J. Braczyk					James E. Belsky

Environmental Engineer					Permit Chief

Bureau of Waste Prevention

cc:	City Hall, City of Haverhill, Haverhill, MA 01830

Fire Headquarters, City of Haverhill, 4 Summer St., Haverhill, MA 01830

Board of Health, City Hall, Haverhill, MA 01830

Metropolitan Area Planning Council, 60 Temple Place, Boston, MA 02111

John Courcier, USEPA - Region 1

Tom Parks, DEP-NERO

Maureen Hancock, DEP-NERO

Michael Castro, DEP-Boston