July 2, 2002

Wheelabrator Millbury, Inc.					Re:  CR – Millbury

331 Southwest Cutoff Road					310 CMR 7.08(2) Municipal Waste

Millbury, MA 01527						Combustors

Approval Modified ECP TR #W003303

Attn:  Alfred Confalone, General Manager

Dear Mr. Confalone:

Wheelabrator Millbury Inc. (WMI) operates a waste-to-energy facility, which is owned by Wheelabrator Environmental Systems, Inc. (the "Permittee"). The Department of Environmental Protection (the “Department”), Bureau of Waste Prevention, Permitting Section has reviewed the proposed modifications to the Municipal Waste Combustor (MWC) Emission Control Plan (ECP) for the Wheelabrator Millbury Inc, 331 Southwest Cutoff Road, Millbury,  Massachusetts  (the "facility").  A Notice to approve the modifications to the ECP and the holding of a public hearing was published in the local newspapers on May 30, 2002 and a 30-day public comment period was provided. The hearing was held on July 1, 2002. No written or oral comments were received during the notice period or hearing.  DEP hereby APPROVES the ECP modifications as noted herein.

This Modified ECP submittal details how emission limitations and compliance schedules for the control of certain designated pollutants according to 310 CMR 7.08(2)-MWC, will be implemented for equipment located at the facility. The modification to this ECP was submitted under the seal and signature of David Raymond, P.E. Number 40655. The modification includes a limited waiver from the mercury limit as allowed under 310 CMR 7.08(2) g.4. and a change in the emission control equipment from the current electrostatic precipitators to new fabric filter collectors.

# LEGAL AUTHORITY

On December 19, 1995, EPA adopted New Source Performance Standards (NSPS) for new MWCs (40 CFR 60 Subpart Eb), and Emission Guidelines (EG) for existing MWCs (40 CFR 60 Subpart Cb).  The emission guidelines were amended by EPA on October 24, 1997.  The NSPS apply to facilities that commenced construction after September 20, 1994, and the EG apply to facilities that commenced construction on or prior to September 20, 1994.  Both the NSPS and the EG apply to large MWC units, that is, those combusting greater than 250 tons per day of municipal solid waste (MSW).  Because Wheelabrator Millbury, Inc. was constructed prior to September 20, 1994, and the combustion unit(s) burn greater than 250 tons per day of MSW, the facility is subject to 40 CFR 60 Subpart Cb “Emission Guidelines” and 310 CMR 7.08(2).

In addition, the Department has imposed further requirements and lowered the emission limitation for mercury from the Federal limit of 0.080 milligrams per dry standard cubic meter (mg/dscm) to 0.028 mg/dscm.  With the exception of the emission limitation for mercury, the Commonwealth has adopted Emission Limits identical to the Federal EG into regulation under 310 CMR 7.08(2), “Municipal Waste Combustors” as contained in 310 CMR 7.00 “Air Pollution Control Regulations” adopted by the Department pursuant to the Massachusetts General Laws, Chapter 111, Sections 142 A-M.

The MWC Regulation requires any person who owns, leases, operates or controls a large municipal waste combustor unit to comply with 310 CMR 7.08(2) in its entirety. The facility’s original MWC ECP was approved by the Department on September 23, 1999 in accordance with Regulation 310 CMR 7.08(2)(j).

The purpose of 310 CMR 7.08(2) is to establish emission limitations and compliance schedules for the control of certain designated pollutants emitted from Municipal Waste Combustors, in accordance with the requirements contained in sections 111(d) and 129 of the Clean Air Act.  310 CMR 7.08(2) establishes requirements for the following:

Operating Practices (Carbon Monoxide (CO), Flue Gas Temperature, Load Level)

Metals (Mercury (Hg), Lead (Pb), Cadmium (Cd))

Particulate Matter (PM)

Opacity

Organics (Dioxin/Furan)

Acid Gases (Sulfur Dioxide (SO2), Hydrogen Chloride (HCl))

Nitrogen Oxides (NOx)

Fugitive Ash Emissions

Applicable requirements and limitations contained in 310 CMR 7.08(2) shall not supersede, relax or eliminate any more stringent conditions or requirements (e.g. emission limitation(s), testing, record keeping, reporting, or monitoring requirements) established by regulation or contained in a facility's previously issued source specific plan approval(s) or emission control plan(s). The facility must also amend its operating permit application to include the approved modified emission control plan. Regulation 310 CMR 7.08(2)g.4. sets forth the conditions and procedures for a limited waiver from the mercury limit.  This modified ECP supersedes in entirety the original ECP dated September 23, 1999 and the ECP Final Approval dated April 5, 2000.

This approval is an action of the Department.  If you are aggrieved by this action, you may request an adjudicatory hearing.  A request for a hearing must be made in writing and postmarked within twenty-one (21) days of the date of issuance of this Approval. Under 310 CMR 1.01(6)(b), the request must state clearly and concisely the facts which are the grounds for the request, and the relief sought.  Additionally, the request must state why the Approval is not consistent with applicable laws and regulations.

The hearing request along with a valid check payable to Commonwealth of Massachusetts in the amount of one hundred dollars ($100.00) must be mailed to: Commonwealth of Massachusetts, Department of Environmental Protection, P.O. Box 4062, 	Boston, MA  02211.  The request will be dismissed if the filing fee is not paid, unless the appellant is exempt or granted a waiver.  The filing fee is not required if the appellant is a city of town (or municipal agency) county, or district of the Commonwealth of Massachusetts, or a municipal housing authority.

The Department may waive the adjudicatory hearing-filing fee for a person who shows that paying the fee will create an undue financial hardship.  A person seeking a waiver must file, together with the hearing request as provided above, an affidavit setting forth the facts believed to support the claim of undue financial hardship.

Yours truly,

Date signed July 2, 2002

Date:_________					Thomas P. Cusson

TPC/GWR/le						Section Chief,

Bureau of Waste

Cc:	Millbury Board of Health

Millbury Fire Department

John Courcier, USEPA-Region I

Marylin Levenson, DEP – Boston

Don Squires, DEP - Boston

/tmp/in/input.doc

Wheelabrator Millbury, Inc.

Modified ECP Approval - Tr #W003303

Table of Contents

Section	Page

LEGAL AUTHORITY	1

I.	PROJECT SUMMARY	5

II.	OVERVIEW	6

1.	FABRIC FILTER	6

2.	RELOCATION OF SNCR SYSTEM COMPONENTS	7

3.	CONTINUOUS EMISSIONS MONITORING SYSTEM MODIFICTIONS	7

4.	ASH HANDLING AND FUGITIVE EMISSIONS CONTROLS	7

5.	CARBON SYSTEM OPTIMIZATION	7

6.	MODIFICATION TO FANS	7

III.	EMISSION UNIT EQUIPMENT DESCRIPTION	8

Table 1 - ECP Emission Unit Equipment Description	8

IV.	EMISSION LIMITS	8

V.	COMPLIANCE DEMONSTRATION	9

Table 2 - Emission Limit, Standard or Restrictions in Operating Practices	10

VI.	MONITORING and TESTING REQUIREMENTS	11

Table 3 – Monitoring and Testing Requirements	11

VII.	RECORD KEEPING REQUIREMENTS	13

Table 4 –Record-Keeping Requirements	13

VIII.	REPORTING REQUIREMENTS	16

Table 5 –Reporting Requirements	16

IX.	COMPLIANCE SCHEDULE	16

X.	SPECIAL CONDITIONS FOR MODIFIED ECP	17

XI.	GENERAL CONDITIONS FOR ECP	17

XII.   ADDITIONAL REQUIREMENTS	19

XIII.    MODIFICATION TO THE ECP	19

XIV.	GENERAL RESPONSIBILITY	19

XV.	 MASSACHUSETTS ENVIRONMENTAL POLICY ACT	20

# I.	PROJECT SUMMARY

A.	The proposed project is for the replacement of existing air emissions control equipment with an improved technology at the facility. The facility currently consists of two boilers each equipped with a spray dryer absorber (SDA), an electrostatic precipitator (ESP), an SNCR de-NOx system, a powdered activated carbon injection system and auxiliary gas burners to control air emissions.  The proposed replacement air emissions control equipment, fabric filters, are being installed to more consistently and reliably meet emission limit requirements adopted pursuant to the Clean Air Act Amendments of 1990 and the Massachusetts Regulations (310 CMR 7.08 (2)).

B.	The 40 CFR 60 Subpart Cb Emission Guidelines established by the United States Environmental Protection Agency (EPA) in response to the Clean Air Act Amendments of 1990 have required existing municipal waste combustion facilities, such as the WMI Facility, to install upgraded air emissions control systems.  In response to these requirements, WMI has recently added the new air emissions control equipment consisting of a selective non-catalytic reduction (SNCR) system and a powdered activated carbon injection system (PACIS).  To further improve plant emissions, fabric filters are being proposed to replace the existing electrostatic precipitators.

C.	The emissions control project will be a multi-year effort involving permitting, equipment purchase and construction.  The design and permitting processes have been initiated by WMI and a construction schedule established to ensure project completion by December 2003.  The construction will be phased to minimize disruption of services to the 36 area communities and other customers that use the facility.

D.	The project is being implemented to reduce air emissions from the existing combustion process.  The fabric filters (FF) selected for this project are the Wheelabrator Air Pollution Control (WAPC) Jet III type, which is a standard and well-proven design similar to many that are currently operating successfully at similar facilities throughout the US.  The fabric filters are being installed to ensure that the facility can consistently meet the mercury emission limits contained in the Massachusetts regulations (310 CMR 7.08 (2) (f) 2.).

E.	No modifications are being proposed that would affect the combustion parameters or combustion process of the existing facility, and there will be no changes (increases or decreases) to the facility’s capacity or throughput.  The proposed changes will not extend the life of the facility.

F.	The changes to the ash handling system are minimal and only include the substitution of new enclosed conveyors for the fabric filters and removal of ash conveyors associated with the ESP.  Fly ash collected in the fabric filter hoppers will be conveyed via enclosed screw conveyors and drag conveyors to a tie-in point on the existing SDA collecting conveyors.  This is similar to the present method of handling fly ash. From there ash will be directed to the ash conditioning and load-out systems as is presently done.

G.	Minor changes to the storm water management system will take place to allow for additional collection of contact storm water.  These changes will include additional curbing around the proposed new fabric filters and for a small area of added paving.	Wash down water and storm water from the vicinity of the new fabric filters areas will be collected in a system of u-drains and sumps, and used as slurry dilution water in the SDAs, or stored in the contact water storage tank for ash quench make-up.  This water collection system will include trenches and sumps, associated pump(s) and piping.

H.	Several existing plant components require relocation to provide space on the site for the construction of the new emissions control equipment.  These include ESP area cable trays and piping, the underground natural gas supply, a portion of the storm water system, the urea storage tank and circulation module for the SNCR system and replacement of the CEMS sample lines for the SDA inlets.  The existing induced draft fans will also need to be modified to accommodate the added flue gas system resistance of the proposed fabric filters.

I.	There will be no changes (increases or decreases) to the capacity of the facility resulting from this project and WMI is not proposing to modify any of the emission limits.  As a result of changing from ESP to FF, the emission limits for dioxin/furan will be reduced from 60 ng/dscm to 30 ng/dscm corrected to 7% oxygen (dry basis) per 310 CMR 7.08.  No other emission limits will change.

J.	A project schedule is included as Figure 1.

# II.	OVERVIEW

A.	The primary components of the proposed air emissions control project include the decommissioning of the existing Electrostatic precipitators (ESPs) and the installation of the following new components:

- Fabric Filters (FFs) for control of particulate, metals and organics (dioxins/furans).

- Modifications to the ash handling system to accommodate the new fabric filters.

- Minor modifications to the water collection system to allow for the collection, storage and reuse of water including storm water collected from the new fabric filter areas.

- Screen walls and enclosures of the areas which contain new emissions control equipment and ash handling equipment.  Enclosures will be similar to those with existing ESPs.

B.	Several other pieces of ancillary equipment are included in the proposed project to support the operation of the major components.  These include new air compressors to generate pulse air for the fabric filters, relocating the urea tank for the existing SNCR system and various controls and instrumentation for proper operation of the equipment, relocating underground natural gas supply lines and a portion of the underground storm water sewer.  Additionally, because of the higher system resistance requirements of the fabric filters, the existing induced draft (ID) fans will be modified to handle the post-modification flue gas conditions.  Electrical system modifications including transformed and motor control addition will be provided as necessary to support the new equipment.

C.	A discussion of each of the proposed components/modifications follows.

# 1.	FABRIC FILTER

Wheelabrator Air Pollution Control (WAPC) will supply the WAPC Jet III Emission Control Equipment, model number (2) x (8) 1817/192 Jet III.  Each emission control train will include an eight (8)-compartment pulse jet fabric filter collector.  The fabric filters will serve to collect particulate matter and reaction products in the flue gas leaving the SDAs.  Cleaning of the bags will be accomplished by bursts of compressed air.  Each compartment will contain 306 bags each approximately 6” in diameter and 192” in length.  The specified maximum gross air-to-cloth ratio (all compartments in service) will be 3.21:1 with a specified maximum net air-to-cloth ratio (one module off-line) of 3.67:1.

# 2.	RELOCATION OF SNCR SYSTEM COMPONENTS

Emissions of NOx are controlled using SNCR.  The SNCR process involves the injection of an aqueous solution containing a urea-based reagent into the furnace. The components of the SNCR system being relocated are the urea reagent tank and circulation skid since they are physically in the way of the proposed new system (Unit #1).  System downtime will be minimized by relocating the module during a scheduled outage or in one shift after the new area has been completely prepared.

# 3.	CONTINUOUS EMISSIONS MONITORING SYSTEM MODIFICTIONS

There exist continuous monitoring systems (CEMS) at the facility; two independent systems, one per unit.  The CEMS are the dry extractive type and include instruments to monitor the following parameters;

FF Outlet - Nitrogen Oxides (NOx), Sulfur Dioxide (SO2), Oxygen (O2 as diluent), and Opacity (in-situ).

SDA Inlet - Oxygen (O2 as diluent), Carbon Monoxide (CO) and Sulfur Dioxide (SO2).

Modified outlet duct arrangements may require relocation of the existing opacity monitors. Consequently new opacity monitors will be installed in accordance with the requirements of 40 CFR 60 Appendix B, Performance Specification 1.  The new opacity monitors will be certified within 180 days after startup of each fabric filter collector.  The CEMS modifications will consist of new heated sample umbilical lines at both SDA inlets.

# 4.	ASH HANDLING AND FUGITIVE EMISSIONS CONTROLS

In order to manage the ash residue from the new equipment, the project will include modifications to the ash handling system.  Drag conveyors from the existing ESP/SDA will be modified and a system of screw conveyors and drag conveyors will be installed to transport the ash from the fabric filter hoppers to a modified (shortened) SDA drag conveyor.  The SDA drag conveyor leads to the existing ash conditioning system. Enclosures or wind walls will be installed to surround the base of the new FFs to minimize the potential for fugitive dust emissions and to provide weather protection for the components.  The enclosures will extend from grade up to the hopper level enclosing the base of the FF structures.  The walls will extend to a height of approximately 209-feet, and will be constructed of a material similar to the existing siding, with a color compatible with that of the existing facility façade.

# 5.	CARBON SYSTEM OPTIMIZATION

Following completion of construction and tie-in for the fabric filters, new carbon optimization tests will take place.  The carbon feed rate will be adjusted following the completion of the test.  It is expected that the feed rate will be reduced to 10-15 lbs/hour.  The vendor guarantees that the facility will be able to meet the emission limits at a carbon use rate of 15 lbs/hr.

# 6.	MODIFICATION TO FANS

The induced draft fans will be modified by having the blades re-tipped or having rotors and bearings replaced.  The modification will not require the fan speed to change and therefore, no additional noise is expected to be generated.

# III.	EMISSION UNIT EQUIPMENT DESCRIPTION

The following emission units (Table 1) are subject to and regulated by this ECP approval:

| # Table 1 - ECP Emission Unit Equipment Description |  |  |  |
| --- | --- | --- | --- |
| Emission Unit # | Description of Emission Unit | EU Design Capacity | Pollution Control Device |
| EU#1 | Babcock & Wilcox Mass Burn Incinerator | 323 MMBTU/hr* 195,000 #/hr of steam @ 900 psig/830F | Fabric Filter Collector, Spray Dryer Absorber, Selective Non-catalytic Reduction system and Powdered Activated Carbon Injection System |
| EU#2 | Babcock & Wilcox Mass Burn Incinerator | 323 MMBTU/hr* 195,000 #/hr of steam @ 900 psig/830F | Fabric Filter Collector, Spray Dryer Absorber, Selective Non-catalytic Reduction system and Powdered Activated Carbon Injection System |
| EU#3 | Ash Handling and Fugitive Emissions | #1 - 4500 ACFM** #2 – 10,000 ACFM** | Enclosed Buildings and Conveyors #1 – Zurn Wet Dust Collector DX03-12 #2 – Tri-Mer Model 100-H Whirl Wet Collector |

*Represents million British thermal units per hour

** Represents actual cubic feet per minute

# IV.	EMISSION LIMITS

1.	The Permittee shall comply with the emission limits, standard or restrictions as specified in Table 2 and in Section IV. EMISSION LIMITS.  Limits apply at all times except during periods of start-up, shutdown, or malfunction as defined in 40 CFR Part 60.58b.

2	No person subject to 310 CMR 7.08(2) shall:

a)	cause, suffer, allow or permit a municipal waste combustor unit to operate at a load

level (based on steam flow) greater than 110 percent of the maximum demonstrated municipal waste combustor unit load calculated in 4-hour block arithmetic averages, measured during the most recent dioxin/furan compliance test in which compliance is achieved; and

b)	cause, suffer, allow or permit a municipal waste combustor unit to operate at a temperature, measured at the PM control device inlet, exceeding 17 C (30 F) above the maximum demonstrated PM control device temperature, calculated in 4-hr block arithmetic averages, measured during the most recent dioxin/furan compliance test in which compliance is achieved.

3.	During any nine-month dioxin/furan compliance test and the 2 weeks preceding each nine-month dioxin/furan compliance test, municipal waste combustor unit load limit and PM control device temperature limitations are not applicable.

4.	Municipal waste combustor unit load limit and PM control device temperature limitations may be waived, if prior approval is granted by the Department, for the purposes of evaluating system performance, testing new technology or control technologies, diagnostic testing, or related activities for the purpose of improving facility performance provided that there is an improvement in controlling air pollution, or advancing the state-of-the-art for controlling facility emissions.

5.	During the limited mercury waiver period, which shall expire on December 31, 2003 the Permittee, shall comply with a mercury emission limit of 0.065 mg/dscm at 7% O2 dry basis based on the average of four quarterly compliance tests per rolling 12-months.

# V.	COMPLIANCE DEMONSTRATION

Any person subject to 310 CMR 7.08(2) that is subject to 310 CMR 7.00 and 310 CMR 19.00 shall be in compliance with, or on a Department approved compliance schedule to meet, all provisions of 310 CMR 7.00 and 310 CMR 19.00 and any plan approval, order, notice of noncompliance or permit issued there under. The facility is subject to the monitoring/testing, record keeping, and reporting requirements as contained in Tables 3, 4 and 5 and 310 CMR 7.08, as well as the applicable requirements contained in Table 2:

# Table 2 - Emission Limit, Standard or Restrictions in Operating Practices

| Emission Unit # | Pollutant | Emission Limit, Standard or Restrictions in Operating Practices | Applicable Regulation or Plan Approval |
| --- | --- | --- | --- |
| EU #1 and #2 | Particulate Matter | < 27 mg/dscm at 7% O2 dry basis. No person shall cause, suffer, allow or permit emissions from any incinerator of any particles that have a dimension greater than 100 microns. [Be referred to 310 CMR 7.06(2)] | 310CMR 7.08(2)(f) |
|  | Sulfur Dioxide | < 29 ppmvd by volume at 7% O2 dry basis or 75% reduction by weight or volume, whichever is less stringent. Compliance is based on a 24-hour geometric mean. |  |
|  | Carbon Dioxide | < 84 ppmvd by volume at 7% O2 dry basis at ESP outlet (4-hour block average) Current CO permit limit is more stringent than Subpart Cb CO limit [Approval #CM-85-IF-001 (A)]. The current permit unit of 0.88 #/MMBTU is equivalent to 84 ppmvd at 7% O2. |  |
|  | Nitrogen Oxides | < 205 ppmvd by volume at 7% O2 dry basis (24-hour daily arithmetic average) | 310 CMR 7.08(2)(f) |
|  | Hydrogen Chloride | < 29 ppmvd by volume at 7% O2 dry basis or 95% reduction by weight or volume, whichever is less stringent. | 310 CMR 7.08(2)(f) |
|  | Cadmium | < 0.04 mg/dscm at 7% O2 dry basis |  |
|  | Lead | < 0.44 mg/dscm at 7% O2 dry basis |  |
|  | Mercury | < 0.028 mg/dscm at 7% O2 dry basis (see Section IV Emission Limits #5.) |  |
|  | Dioxin- Furon | < 60 ng/dscm total mass at 7% O2 dry basis with ESP controls. < 30 ng/dscm total mass at 7% O2 dry basis with fabric filtration. |  |
|  | Opacity | < 10% (6 minute average) |  |
|  |  | Unit Load < 110% of maximum demonstrated load (based on steam flow), calculated in 4-hour block arithmetic averages, measured during the most recent dioxin/furan compliance test in which compliance is achieved. PM control device inlet temperature < 17C (30F) above maximum demonstrated PM control device inlet temperature, calculated in 4-hour block arithmetic averages, measured during the most recent dioxin/furan compliance test in which compliance is achieved. |  |
| EU # 3 | Visible Emissions of Fugitive Ash | < 5% of the observation period (9 minutes per three hour period) No person subject to 310 CMR 7.08(2) shall cause, suffer, allow or permit the discharge into the atmosphere of any visible emissions of combustion ash from an ash conveying system (including transfer points) in excess of 5 percent of the observation period (nine minutes per three hour period). This emission limit does not cover visible emissions discharged inside buildings or enclosures of ash conveying systems; however the emission limit does apply to visible emissions discharged to the atmosphere from buildings or enclosures of ash conveying systems. This subsection does not apply during maintenance and repair of ash conveying systems. Maintenance and repair of the ash conveying systems must be done in accordance with best management practices. | 310 CMR 7.08(2)(f) |

+Legend to Abbreviated Terms within Table 2

EU# = Emission Unit Number				PM = Particulate Matter		Cd = Cadmium

mg/dscm = milligram per dry standard cubic meter 		HCl = Hydrogen Chloride		O2 = Oxygen

ppm = parts per million					SO2 = Sulfur Dioxide		Pb = Lead		      % = percent		                                                            NH3 = Ammonia     		NOx = Nitrogen Oxides

C = Degrees Centigrade					CO = Carbon Monoxide		Hg = Mercury

F = Degrees Fahrenheit

< = less than or equal to

# VI.	MONITORING and TESTING REQUIREMENTS

| EU# | # Table 3 – Monitoring and Testing Requirements |
| --- | --- |
| EU#1 & #2 | 1. In accordance with 310 CMR 7.08(2)(g), the Permittee shall continue to comply with all the requirements of the Monitoring and Testing as specified in Table 3 until such time as the ESP control system on each Unit has been replaced with the new Fabric Filtration System as specified within this ECP. For each Unit, within 180 days of replacement of the ESP with the Fabric Filter and re-start, the Permittee shall conduct an "initial performance" and compliance test and shall other wise comply with all the provision of Monitoring and Testing as specified in Table 3. Any time schedules as noted in Table 3 shall be adjusted to coincide with the re-start and re-testing of each Unit after control system replacement as noted herein. |
|  | 2. Following the date of the initial performance test for dioxin/furan, the facility shall conduct compliance tests for dioxin/furan emissions according to one of the schedules specified below, as required by 310 CMR 7.08(2)(g) 1.a. and b.: a. conduct compliance test for dioxin/furan emissions on all municipal waste combustor unit(s) on a nine month basis, or b. for municipal waste combustor unit(s) where all compliance tests for all unit(s) over a 27 month period indicate that dioxin/furan emissions are less than or equal to 7 nanograms per dry standard cubic meter total mass (ng/dscm), corrected to 7 percent oxygen, the facility may elect to conduct compliance tests for one unit every nine months. At a minimum, a compliance test for dioxin/furan emissions shall be conducted every nine months following the previous compliance test for one unit at the municipal waste combustor plant. Every nine months a different unit at the municipal waste combustor plant shall be tested, and the units at the plant shall be tested in sequence (e.g., unit 1, unit 2, unit 3, as applicable). The facility may continue to conduct compliance testing on only one unit per nine month basis so long as the dioxin/furan emissions remain less than or equal to 7 ng/dscm @ 7% O2. If any nine month compliance test indicates dioxin/furan emissions greater than the specified limit, compliance tests shall thereafter be conducted on all units at the plant every nine months until and unless all nine month compliance test for all units at the plant over a 27 month period indicate dioxin/furan emissions less than or equal to the 7 ng/dscm @ 7% O2. |
|  | 3. In accordance with 310 CMR 7.08(2)(g) 1.d., for municipal waste combustor units where carbon injection (or equivalent) is used to comply with the dioxin/furan emission limits specified in section 310 CMR 7.08(2)(f) 2. or the dioxin/furan emission limit specified in 310 CMR 7.08(2)(g) 1.b, measure and calculate the carbon (or equivalent) usage rate following the procedures specified in 40 CFR 60.58b(m) effective December 19, 1995 and as amended October 24, 1997. |
|  | 4. In accordance with 310 CMR 7.08(2)(g) 2., following the date of the initial performance test for Hg, compliance testing for Hg shall be conducted on all municipal waste combustor unit(s)on a quarterly basis. Compliance with the emissions limit specified in 310 CMR 7.08(2)(f) 2. shall be based on the average of four quarterly compliance tests per rolling twelve months but shall not exceed 0.080 mg/dscm in any quarterly test. If compliance with the Hg emission limit has been achieved in each quarter for eight consecutive quarters, the facility may elect to perform compliance testing on a nine-month basis. Any municipal waste combustor unit(s) which cannot achieve compliance with the emission limitation in 310 CMR 7.08(2)(f) 2. during the nine-month compliance test shall resume quarterly compliance testing as specified above. |
|  | 5. In accordance with 310 CMR 7.08(2)(g) 3., for municipal waste combustor unit(s) which employ a carbon injection (or equivalent) Hg emission control system, conduct optimization tests. These tests will determine the optimum feed rate for the Hg emissions control apparatus by determining the carbon (or equivalent) feed rate at which the emissions of Hg are equal to or less than the applicable limit at 310 CMR 7.08(2)(f) 2. The optimization test shall be conducted as follows: a. The optimization tests shall be performed during the initial performance test, after a change in carbon (or equivalent), upon completion of replacement of the ESP with Fabric Filter Collection, upon request by the Department, upon request by the facility or annually if required under 310 CMR 7.08(2)(g) 4. (See Section X. (7). SPECIAL CONDITIONS FOR MODIFIED ECP) b. If there are identical municipal waste combustor units at the municipal waste combustor plant, then optimization tests may be performed on one unit, and the resulting parameters applied to the other unit(s), which are identical to that unit at that plant. c. Within 60 calendar days of the conclusion of any optimization test, the facility shall submit to the Department for approval a proposed optimized carbon (or equivalent) feed rate, which minimizes Hg emissions. An approvable feed rate is the feed rate such that a higher feed rate achieves insignificant additional reductions in Hg emissions compared to the amount of carbon (or equivalent) added. The carbon (or equivalent) feed rate approved by the Department shall be used to operate the carbon injection (or equivalent) Hg control system until the next optimization test is performed and the feed rate approved. |
| EU#1 & #2 | 6. In accordance with 310 CMR 7.08(2)(g) 6., the facility shall conduct compliance testing for PM, Cd, Pb, HCL, opacity and fugitive emissions every nine months for each municipal waste combustor unit(s). Compliance testing for dioxin/furan and Hg shall be as specified in 310 CMR 7.08(2)(g) 1. and 2. |
|  | 7. In accordance with 310 CMR 7.08(2)(g) 5.a. and b., Continuous Emissions Monitoring Systems (CEMS) which monitor NOx, SO2, operating practices and parameters, (e.g., CO, unit load and PM control device inlet temperature) shall obtain at a minimum valid continuous emissions monitoring system data for 75% of the hours per day (18 hours per day) for 75% of the days per month (23 days per month for a 30 day month), and 90% of the hours per quarter that the municipal waste combustor unit is combusting municipal solid waste. CO CEMS installed and operated in accordance with Performance Specification 4 of 40 CFR Part 60, Appendix B, will satisfy the requirements in 310 CMR 7.08(2)(g). |
| EU#3 | 8. Conduct performance test every nine months for visible emissions associated with ash handling and fugitive operations to insure compliance with visible emission standards as specified in Table 2. |

# VII.	RECORD KEEPING REQUIREMENTS

| EU# | # Table 4 –Record-Keeping Requirements |
| --- | --- |
| EU #1, EU #2 and EU#3 | 1. In accordance with 310 CMR 7.08(2)(h) 9., the results of the initial performance tests and all nine compliance tests conducted to determine compliance with the PM, opacity, Cd, Pb, Hg, dioxin/furan, HCl, and fugitive ash emission limits shall be recorded along with supporting calculations and submitted to the Department within 90 days after the test. In addition, the results of the quarterly Hg compliance tests shall also be recorded and submitted to the Department within 60 days after the test. |
|  | 2. For the initial dioxin/furan performance test and all subsequent dioxin/furan compliance tests recorded under 7.08(2)(h), the maximum demonstrated municipal waste combustor load and maximum PM control device temperature (for each PM control device) shall be recorded along with supporting calculations, as required by 310 CMR 7.08(2)(h) 10. |
|  | 3. As required by 310 CMR 7.08(2)(h) 4., for municipal waste combustor unit(s) that apply carbon (or equivalent) for Hg or dioxin/furan control and maintain, the following records: a. The average carbon (or equivalent) mass feed rate (in lbs/hr) measured as required under 40 CFR 60.58b(m)(1)(i) effective December 19, 1995 and as amended October 24, 1997, during the initial Hg performance test and all subsequent compliance tests, with supporting calculations. b. The average carbon (or equivalent) mass feed rate (in lbs/hr) measured for each 8 hour block average of operation as required under 40 CFR 60.58b(m)(1)(ii) effective December 19, 1995 and as amended October 24, 1997, during the initial dioxin/furan performance test and all subsequent nine month compliance tests, with supporting calculations. c. The average carbon (or equivalent) mass feed rate (in lbs/hr) measured for each 8 hour block average of operation as required under 40 CFR 60.58b(m)(3)(ii) effective December 19, 1995 and as amended October 24, 1997, with supporting calculations. d. The total carbon (or equivalent) usage for each calendar quarter measured as specified under 40 CFR 60.58b(m)(3) effective December 19, 1995 and as amended October 24, 1997, with supporting calculations. e. The carbon (or equivalent) injection system operating parameter data for the parameter(s) that are the primary indicator(s) of carbon (or equivalent) feed rate. |
|  | 4. As required by 310 CMR 7.08(2)(h) 13. for municipal waste combustor units that apply carbon (or equivalent) for Hg or dioxin/furan control: a. Identification of the calendar dates when the average carbon (or equivalent) mass feed rates recorded under 310 CMR 7.08(2)(h) 4.c. were less than either of the hourly carbon feed rates measured during compliance tests for Hg or dioxin/furan emissions and recorded under paragraphs 310 CMR 7.08(2)(h) 4. a. or b. of this section, respectively, with reasons for such feed rates and a description of corrective actions taken. b. Identification of the calendar dates when the carbon injection (or equivalent) system operating parameter(s) that are the primary indicator(s) of carbon mass feed rate (or equivalent) recorded under 310 CMR 7.08(2)(h) 4. e., are below the level(s) estimated during the compliance tests as specified in 40 CFR 60.58b(m)(1)(i) and 60.58b(m)(1)(ii) effective December 19, 1995 and as amended October 24, 1997, with reasons for such occurrences and a description of corrective actions taken. |
|  | 5. In accordance with 310 CMR 7.08(2)(h) 2., record the emission concentrations and parameters measured using continuous emissions monitoring systems. The measurements specified below shall be recorded and shall be available for submittal to the Department or for onsite review by an inspector: a. All 6-minute average opacity levels as specified under 40 CFR 60.58b(c) effective December 19, 1995 and as amended October 24, 1997, including the highest level measured. b. All 1-hour average SO2 emission concentrations as specified under 40 CFR 60.58b(e) effective December 19, 1995 and as amended October 24, 1997. c. All 1-hour average NOx emission concentrations as specified under 40 CFR 60.58b(h) effective December 19, 1995 and as amended October 24, 1997. d. All 1-hour average CO emission concentrations, municipal waste combustor unit load measurements, and PM control device inlet temperatures as specified under 40 CFR 60.58b(i) effective December 19, 1995 and as amended October 24, 1997. e. All 24-hour daily geometric average SO2 emission concentrations and all 24-hour daily geometric average percent reductions in SO2 emissions as applicable, as specified under 40 CFR 60.58b(e) effective December 19, 1995 and as amended October 24, 1997 including the highest level recorded. f. All 24-hour daily arithmetic average NOx emission concentrations as specified under 40 CFR 60.58b(h) effective December 19, 1995 and as amended October 24, 1997, including the highest level recorded. g. All 4-hour block averages, CO emission concentrations, as applicable, as specified under 40 CFR 60.58b(i) effective December 19, 1995 and as amended October 24, 1997, including the highest level recorded. h. All 4-hour block arithmetic average municipal waste combustor unit load levels (steam flow) and PM control device inlet temperature as specified under 40 CFR 60.58b(i) effective December 19, 1995 and as amended October 24, 1997, including the highest level recorded. |
|  | 6. As required by 310 CMR 7.08(2)(h) 3., record the calendar dates when any of the average emissions concentrations or percent reductions, or operating parameters recorded under section 7.08(2)(h) 2., exceed the applicable limits, with detailed specific reasons for such exceedances and a description of corrective actions taken. |
| EU#1, EU #2 and EU#3 | 7. As required by 310 CMR 7.08(2)(h) 5., record the calendar dates and time periods for which the minimum number of hours of any of the data specified below have not been obtained including reasons for not obtaining sufficient data and a description of corrective actions taken: a. SO2 emissions data. b. NOx emissions data. c. CO emissions data. d. Municipal waste combustor unit load data, including PM control device inlet temperature data. |
|  | 8. As required by 310 CMR 7.08(2)(h) 6., record each occurrence that SO2 emissions data, NOx emissions data, or operational data (e.g. CO emissions, unit load, and PM control device temperature) have been excluded from the calculation of average emission concentrations or parameters, along with detailed and specific reasons for excluding the data. |
|  | 9. As required by 310 CMR 7.08(2)(h) 7., record the results of daily drift tests and quarterly accuracy determinations for SO2, NOx, and CO continuous emission monitoring systems, as required under 40 CFR, Part 60, Appendix F, Procedure 1. |
| EU#1, EU #2 and EU#3 | 10. As required by 310 CMR 7.08(2)(h) 8., record each occurrence of a start-up, shut-down or malfunction, including the specific reasons for each occurrence, date, time, and unit involved. Average emissions concentrations or percent reductions, or operating parameters recorded under section 7.08(2)(h) 2., shall be recorded during start-up, shut-down or malfunction. |
|  | 11. In accordance with 310 CMR 7.08(2)(h) 11. maintain records showing the names of the municipal waste combustor chief facility operator, shift supervisors, and control room operators who are certified by ASME (Operator Certification and Provisional Certification), including the dates of initial and renewal certifications and documentation of current certification. Records showing the names of the municipal waste combustor chief facility operator, shift supervisors, and control room operators who have completed the EPA municipal waste combustor operator-training course if required. |
|  | 12. In accordance with 310 CMR 7.08(2)(h) 12. maintain the records showing the names of the persons who have completed a review of the operating manual as required by section 7.08(2)(f) 6. d. including the date of the initial review and subsequent annual reviews. |
|  | 13. As required by 310 CMR 7.08(2)(h) 1., maintain the calendar date of each record. |
|  | 14. The facility shall maintain records of the information specified in this section, as applicable, for each municipal waste combustor unit. All records shall be retained at the facility for at least 5 years, in accordance with 310 CMR 7.08(2)(h) and shall be made available to Department personnel upon request. |

# VIII.	REPORTING REQUIREMENTS

| EU# | # Table 5 –Reporting Requirements |
| --- | --- |
| EU#1, EU#2 and EU#3 | 1. As required by 310 CMR 7.08(2)(i), the facility shall submit an initial performance report, any re-test reports, as well as an annual report of the information specified in 310 CMR 7.08(2)(i) 1., as applicable. The facility which elects to follow the compliance testing schedule specified in 310 CMR 7.08(2)(g) 1.b., shall follow the procedures specified in section 310 CMR 7.08(2)(i) 1. For reporting the selection of this schedule. 2. Annual Reporting Requirements – The information specified in (a.) through (g.) below shall be reported: a. 310 CMR 7.08(2)(h) 2.a., e. through h. for the highest emission levels recorded. b. 310 CMR 7.08(2)(h) 4.a. and b. c. 310 CMR 7.08(2)(h) 5. – 6. d. 310 CMR 7.08(2)(h) 8. – 10. e. Summary of a. through d. for the previous year. f. The performance evaluation of the continuous emission monitoring system using the applicable performance specifications in Appendix B of 40 CFR, Part 60. g. A notification of intent to begin the reduced dioxin/furan compliance testing schedule specified in section 310 CMR 7.08(2)(g) 1. b. during the following calendar year. 3. Annual reports shall be submitted to this Office no later than February 15 of each year following the calendar year in which the data was collected. |
|  | 4. As required by 310 CMR 7.08(2)(i), in meeting the reporting requirements of 310 CMR 7.08(2)(i) 1. and 310 CMR 7.08(2)(i) 2., the facility shall report the information in a format determined by the Department that is designed to be understandable and informative to the public. The information shall be submitted in written format and electronic format. |

+Legend to Abbreviated Terms within Tables 3, 4 and 5:

mg/dscm = milligram per dry standard cubic meter

ng/dscm = nanogram per dry standard cubic meter

Cd = Cadmium                                   	Pb = Lead

Hg = Mercury                                   	NOx = Nitrogen Oxides

CO = Carbon Monoxide               	PM = Particulate Matter

HCl = Hydrogen Chloride            	SO2 = Sulfur Dioxide

O2 = Oxygen                                       	% = percent

NH 3  = Ammonia

# IX.	COMPLIANCE SCHEDULE

As required by 310 CMR 7.08(2)(k), the subject municipal waste combustor unit(s) shall be in full compliance with the applicable requirements of 310 CMR 7.08(2). The Permittee shall submit a final construction schedule within 30 days of receiving this Modified ECP approval.  Incremental monthly progress reports shall be submitted to the Department by the 15th of each month. The Permittee shall achieve full compliance by December 31, 2003 unless an extension of the Mercury Waiver is granted in accordance with 310.   CMR 7.08(2)(g) 4.e.  Initial performance test shall be completed within of 180 days after initial operation of each fabric filter collector.

# X.	SPECIAL CONDITIONS FOR MODIFIED ECP

1.	The Permittee shall follow good operating practices at all times.

2.	The Permittee shall have ash handling doors closed at all times when in full operation except for when loading out metals from recycling operation on a daily basis and for routine repairs and maintenance activities where applicable.  The ash handling system is automated in regards to the 30-yard ash containers on a rail system.  The doors located on the North and South side of Ash Handling Building must remain partially open to accommodate the 30-yard containers.  The doors are equipped with heavy-duty 24” weather strips that prevent potential fugitive emissions and shall provide closure for these two doors.

3.	The Permittee shall comply with the requirements contained in Tables 2, 3, 4, 5 and 6 on and after December 19, 2000 and in accordance with dates as allowed within this Modified ECP.  The final compliance date is December 31, 2003 unless an extension of the Mercury Waiver is granted in accordance with 310 CMR 7.08(2)(g) 4.e.   Compliance with applicable requirements as set forth in 310 CMR 7.08(2)(8) and Section 4 of this ECP, shall be determined in accordance with 40 CFR 60.58b except as provided under 310 CMR 7.08(20(g) 1,2,3,4,5 and 6 and as specified within this ECP.

4.	The Permittee shall not combust sewage sludge in any of the municipal waste combustor units.

5.	The Permittee shall have a mechanical sweeper equipped with a water dust suppression system utilized on a daily basis to maintain the on-site paved areas free of sand deposits.

6.	 	     Upon written request of the Department the Permittee shall conduct an optimization/minimization-testing program regarding the use of urea on the SNCR systems to insure that the emission of ammonia (ammonia slip) is minimized.  Such testing shall be witnessed by a representative of the Department.  A test report shall be submitted to the Department within 60 days of the completion of such testing.  The test results will set an ammonia emission limit, which will be incorporated into this emission control plan.  The ammonia limit will set forth as a “state only” enforceable requirement in the ECP.

7. 	During the limited mercury waiver period the Permittee shall perform optimization testing of mercury control on an annual basis and submit results to the Department. Annual optimization testing shall continue until compliance with the limit in 310 CMR 7.8(2)(f)2. is achieved.

# XI.	GENERAL CONDITIONS FOR ECP

A.	SITE ASSIGNMENT

In accordance with 310 CMR 7.08(2)(a), no person shall, suffer, allow, or permit the construction, substantial reconstruction, alteration or operation of a municipal waste combustor unit on a site which has not received a site assignment in accordance with M.G.L. c.111, s.150A.

B.	COMPLIANCE AND PERFORMANCE TESTING

As required by 310 CMR 7.08(2)(g), the facility shall comply with the provisions of 40 CFR 60.58b, "Compliance and performance testing", effective December 19, 1995 and as amended October 24, 1997, the provisions of which are hereby incorporated by reference. Compliance with the applicable requirements as set forth in 310 CMR 7.08(2)(f) of this ECP, shall be determined in accordance with 40 CFR 60.58b, except as provided under 310 CMR 7.08(2)(g) 1., 2., 3., 4., 5., and 6, and as specified within this ECP. The initial performance test must be completed within 180 days after the final compliance date.

C.	OPERATOR TRAINING AND CERTIFICATION

1. 	In accordance with 310 CMR 7.08(2)(f) 6., the facility shall implement the following municipal waste combustor operator training and certification requirements. The Permittee:

a.    Shall have each chief facility operator and shift supervisor obtain and maintain an Operator Certificate issued by the American Society of Mechanical Engineers (ASME).

b.   Shall not allow the municipal waste combustor unit to be operated at any time unless one of the following persons is on duty: A chief facility operator or a shift supervisor who has obtained an Operator Certificate. (A Provisional Certificate is acceptable provided the supervisor is scheduled to obtain an Operator Certificate in accordance with section (f) below). If one of the persons listed above must leave the municipal waste combustor plant during his or her operating shift, a provisionally certified control room operator who is onsite at the municipal waste combustor plant may fulfill these requirements.

c.     Shall have all chief facility operators, shift supervisors, and control room operators who have not obtained an Operator Certificate from ASME complete the National Technical Information Service - "EPA Municipal Waste Combustor Operating Course."

d.    Shall establish a training program to review the operating manual with each person who has responsibilities affecting the operation of an affected municipal waste combustor unit, including, but not limited to, chief facility operators, shift supervisors, control room operators, ash handlers, maintenance personnel, and crane/load handlers. The operating manual shall address at a minimum the following:

i.	A summary of all applicable requirements in this regulation;

ii.	Basic combustion theory applicable to a municipal waste combustor unit;

iii.	Procedures for receiving, handling, and feeding municipal solid waste;

iv.	Municipal waste combustor unit startup, shutdown, and malfunction procedures;

v.	Procedures for maintaining proper combustion air supply levels;

vi.	Procedures for operating the municipal waste combustor unit within the requirements established under this regulation;

vii.	Procedures for responding to periodic upset or off-specification conditions;

viii.	Procedures for minimizing PM carryover;

ix.	Procedures for handling ash;

x.	Procedures for monitoring municipal waste combustor unit emissions; and

xi.	Reporting and record keeping procedures.

e.  	Shall make available to the Department for inspection upon request all the operating manuals and      records of training.

f.     Shall be in compliance with all training and certification requirements specified in 310 CMR 7.08(2)(f) 6. by six months after the date of start up or August 21, 1999, whichever is later.

# XII.   ADDITIONAL REQUIREMENTS

In accordance with 310 CMR 7.08(2)(j) 5., additional requirements may be included in the emission control plan approval if the Department determines that the emissions from a municipal waste combustor plant's unit(s) alone or cumulatively with other municipal waste combustor plant's unit(s) cause or contribute to a condition of air pollution or a violation of any other regulation. Such requirements include but are not limited to emissions limits on air contaminants, and additional stack testing or emission monitoring requirements.

The Department may modify the emission control plan at any time if the Department determines that a municipal waste combustor plant's unit(s) alone or cumulatively with other municipal waste combustor plant's unit(s) cause or contribute to a condition of air pollution or a violation of any other regulation.

Cumulative Impact: The Department did not perform cumulative impact analysis about the Wheelabrator Millbury Inc. since no other MWC facilities are located within the vicinity of the Wheelabrator Millbury Inc. MWC.

# XIII.    MODIFICATION TO THE ECP

In accordance with 310 CMR 7.08(2)(j) 7., if the Department proposes to modify a municipal waste combustor plant's emission control plan, the Department shall publish a notice of public comment in accordance with M.G.L. c. 30A detailing the proposed modification.  The Department shall allow for a 30-day public comment period following the published notice. The Department will modify the emission control plan after the close of the public comment period.

# XIV.	GENERAL RESPONSIBILITY

The Permittee  (WMI) shall maintain continuous compliance at all times with the terms of this emission control plan.  This approval may be suspended, modified, or revoked by the Department if at any time the facility is violating any applicable Regulation(s) or conditions of this approval letter. The application material submitted and this approval letter together constitute the approved emission control plan.  Where there is a conflict between the submitted information and this approval letter, this letter shall rule.

Please be advised that this approval does not negate the responsibility of The Permittee to comply with this or any other applicable federal, state, or local regulations now or in the future.  Nor does this approval imply compliance with any applicable federal, state or local regulations now or in the future.

Should any nuisance condition(s) occur as a result of the operation of this facility, then WMI shall immediately take appropriate steps to abate said nuisance conditions.

# XV.	 MASSACHUSETTS ENVIRONMENTAL POLICY ACT

The Department has determined that the filing of an Environmental Notification Form (ENF) with the Secretary of Environmental Affairs, for air quality control purposes, was not required prior to this action by the Department. Notwithstanding this determination, the Massachusetts Environmental Policy Act (MEPA) and Regulation 301 CMR 11.00 Section 11.03, provide certain “Fail Safe Provisions” which allow the secretary to require the filing of an ENF and/or Environmental Impact Report at a later time.

Should The Permittee have questions concerning this matter or regarding the terms or conditions of this approval, please do not hesitate to contact Gary Roscoe, in the Central Regional Office, 627 Main Street, Worcester, Massachusetts 01608.

Yours truly,

Date:	July 2, 2002						Thomas P. Cusson

Section Chief,

Bureau of Waste Prevention