Commonwealth of Massachusetts

Department of Labor Standards

OSHA Consultation Program

www.mass.gov/dols/consult

Fire Extinguishers

(29CFR 1910.157)

There are four possible situations which may arise in the workplace.  The requirements for extinguisher depends on which of  these categories applies.  First determine which situation applies then look at applicable requirements.

Situation #1  No fire extinguisher in the workplace.

If an employer has both an emergency action plan and a fire prevention plan, and, if the plan calls for the total evacuation of employees, then no fire extinguisher are required by OSHA.  The only exception to this rule is when another OSHA Standard requires it.  For example, there are requirements for fire extinguisher in both the spray finishing and welding standards.  (Note - although OSHA may not require it, there are often local ordinances requiring fire extinguisher.  Check with your local fire department for details).

Situation #2  Fire extinguisher are located in the workplace, no   employee is expected to use them.

Often a workplace is required by the local fire department or building code to have fire extinguisher on site.  However, the employer may still choose to call for the total evacuation of employees in the emergency action plan.  If there are extinguisher at the workplace, but employees are not expected to use them, then the only requirements that apply are the Inspection, Maintenance, and Testing requirements.

Situation #3  Fire extinguisher to be used by designated employees  only.

If the emergency action plan designates only certain employees to use the fire extinguisher then the selection and distribution requirements do not apply.  All other requirements, Inspection, Maintenance and Testing, and Training and Education requirements apply.

Situation #4  Fire extinguisher to be used by all employees.

If the emergency action plan calls for all employees to fight fires, then all the requirements, Selection and Distribution, Inspection, Maintenance Testing, and Training and Education requirements apply.

Fire Extinguisher Requirements

Again, remember that none, some or all of these requirements apply depending on which situation is applicable to your workplace.

Selection and Distribution

The fire extinguisher selected must be appropriate for the particular type and size of fire anticipated.  In general, there are four classes of fire extinguisher (A, B, C, D) available either separately or in combination.  Often a combination extinguisher is chosen if there may be more than one type of fire in the area.  The four classes and required distribution are summarized as follows:

Travel Distance to get

Class			Use					   to Extinguisher

Class A		Combustibles such 			No more than 75 feet

as wood/paper

Class B		Flammable Liquids			No more than 50 feet

Class C		Electrical fires			Generally no more than

50 feet

Class D		Combustible materials		No more than 75 feet

(flakes, shavings)

Inspection, Maintenance, Testing

All portable extinguishers must be visually inspected monthly and subjected to an annual maintenance check.  Records of the annual maintenance must be maintained.

There are specific requirements for hydrostatic testing for refillable extinguisher (typically performed by the fire extinguisher maintenance contractor).

Training and Education

Any employee who will use a fire extinguisher must be trained on the use of fire extinguisher and hazards involved with firefighting initially and annually thereafter.