`1	`	Notes:

- Use the following formulas to calculate the Calculated Fluoride Ion Dosage in Section III of Form A of the Mass DPH fluoridation report.

- The natural fluoride level for Massachusetts of 0.1 ppm is incorporated into all calculated dosage formulas below.

- Million Gallons (MG) must be expressed in decimal form. Ex.1,000,000 would be entered as 1.0; 500,000 would be 0.5 .

- Calculations of Daily Dosage

1.   a) If using a Saturator- using gallons of makeup water (saturated solution) added each day.

Calculated dosage (ppm) = Gallons of makeup water added each day

Water treated each day (MG) X 50

b) If using a Saturator- using cubic feet of makeup water added each day.

Calculated dosage (ppm) = Cubic feet of makeup water added each day

Water treated each day (MG) X 6.7

- a) If using Hydrofluosilicic acid- using pounds added each day.

Calculated dosage (ppm) =  __Pounds of acid added each day__

Water treated each day (MG) X C4*

*For C4 values use the following table:

| Commercial purity of H2SiF6 in % | C4 |
| --- | --- |
| 22 | 43.1 |
| 23 | 41.2 |
| 24 | 39.5 |
| 25 | 37.8 |
| 26 | 36.5 |
| 27 | 35.1 |
| 28 | 33.9 |
| 29 | 32.7 |
| 30 | 31.7 |

3.   a) If using a Dry  Feeder-  using pounds of sodium Silicofluoride added each day.

Calculated dosage (ppm) = Pounds of Silicofluoride added each day

Water treated each day (MG) X 12.4

# Only For systems using a Saturator - Calculation of monthly dosage **

1.    a) If using a Saturator- using pounds of sodium fluoride added each month

Calculated dosage (ppm) = Pounds of Sodium Fluoride added each month

Water treated each month (MG) X 16.9

** If you have any questions on the monthly dosage calculation see the MA State Recommended Standard Operating Procedures for Sodium Fluoride (NaF) Saturators on the following website: Mass DEP/DWP- http://www.mass.gov/eea/agencies/massdep/service/approvals/fluoride.html  or contact DPH at 617-624-5573.

DPH daily fluoride report calculation 6-2015