INDOOR AIR QUALITY ASSESSMENT

Galvin Middle School

525 Main Street

Wakefield

Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health

Indoor Air Quality Program

August 2020

# Background

| Building: | Galvin Middle School (GMS) |
| --- | --- |
| Address: | 525 Main St, Wakefield |
| Requested by: | Bob Schiaroli, Director of Facilities, Wakefield Public Schools (WPS) |
| Reason for Request: | Collaborative effort to perform general indoor air quality (IAQ) assessments throughout the WPS |
| Date of Assessment: | February 13, 2020 |
| Massachusetts Department of Public Health/Bureau of Environmental Health (MDPH/BEH) Staff Conducting Assessment: | Ruth Alfasso, Environmental Engineer/Inspector, and Jason Dustin, Environmental Analyst/Inspector, IAQ Program |
| Building Description: | GMS is a three-story brick building |
| Windows: | Windows are openable in most areas of the school. |

# Methods

Please refer to the IAQ Manual for methods, sampling procedures, and interpretation of results (MDPH, 2015).

# Results

The following is a summary of indoor air testing results (Table 1).

- Carbon dioxide levels were below the MDPH recommended level of 800 parts per million (ppm) in about ¾ of areas assessed, indicating adequate air exchange in most areas of the building.

- Temperature was within or close to the MDPH recommended range of 70°F to 78°F in occupied areas.

- Relative humidity was below the lower end of the MDPH recommended range of 40 to 60% in nearly all areas tested the day of assessment, which is typical of conditions during the heating season.

- Carbon monoxide levels were detected at low levels in a few areas. This is discussed further in the “Other Conditions” section of this report.

- Particulate matter (PM2.5) concentrations measured were below the National Ambient Air Quality (NAAQS) level of 35 μg/m3 in all areas tested.

# Discussion

## Ventilation

A heating, ventilating, and air conditioning (HVAC) system has several functions. First it provides heating and, if equipped, cooling. Second, it is a source of fresh air. Finally, an HVAC system will dilute and remove normally occurring indoor environmental pollutants by not only introducing fresh air, but by filtering the airstream and ejecting stale air to the outdoors via exhaust ventilation. Even if an HVAC system is operating as designed, point sources of respiratory irritation may exist and cause symptoms in sensitive individuals.

Fresh air ventilation in the GMS is supplied by air handing units (AHU) located on the roof. Fresh air is supplied to classrooms, offices and common areas via ceiling-mounted supply vents (Picture 1). Ceiling-mounted exhaust vents remove stale air.

Air in classrooms is additionally heated and filtered through the use of fan coil units (FCU) located on exterior walls (Picture 2). These units draw in room air through a vent along the bottom, and supply conditioned air via the vent on the top. In order to function effectively, top and bottom vents on units must remain unobstructed by furniture and items. Note that each unit is equipped with a fairly inefficient filter. The MDPH recommends pleated filters with a Minimum Efficiency Reporting Value (MERV) of 8, which are adequate in filtering out pollen and mold spores (ASHRAE, 2012). Filters should also be changed two to four times a year, or per the manufacturer’s recommendations. More importantly, the FCUs did not appear to have any sort of bracket or holder to keep the filters in place in the airstream of the unit, relying only on the pressure of the air flowing through the unit to hold the filter in place. Many of the filters in these units were found on the floor underneath (Table 1), where they provide no filtration and can become covered in dust and debris. Facility staff reported that this is due to a design issue with the units, and that a new method of holding filters in place was being implemented at the school.

To maximize air exchange, the MDPH recommends that both supply and exhaust ventilation operate continuously during periods of occupancy. In order to have proper ventilation with a mechanical supply and exhaust system, the systems must be balanced to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room. It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).

Note that many of the exhaust vents and wall-mounted thermostats are located near the doors to the hallway (Picture 3). These are both designed to function most efficiently when the hallway doors are closed. When hallway doors are open, the exhaust vents tend to draw stale air from the hallway instead of the room, and thermostats measure hallway temperatures instead of room temperatures.

Microbial/Moisture Concerns

In order for building materials to support mold growth, a source of water exposure is necessary. Identification and elimination of the source of water moistening building materials is necessary to control mold growth. Water-damaged ceilings/tiles were observed in some classrooms and offices (Picture 4; Table 1), which can indicate current or historic roof/plumbing leaks. Water-damaged ceiling tiles can provide a source of mold and should be replaced after a water leak is discovered and repaired. The United States Environmental Protection Agency (US EPA) and the American Conference of Governmental Industrial Hygienists (ACGIH) recommend that porous materials be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2008; ACGIH, 1989). If porous materials are not dried within this time frame, they should be removed and discarded.

The refrigerator in the staff lunchroom had evidence of a spill (Picture 5; Table 1). Refrigerators should be cleaned out regularly to prevent odors and microbial growth. Stained gaskets should be cleaned with a mild antimicrobial solution; if they are too heavily stained/damaged, they should be replaced. Refrigerators should not be placed on carpet/porous materials to protect carpets from spills.

Plants were present in some classrooms and other areas (Picture 6). Plants should be well maintained, not overwatered, and not placed on porous materials or in the airstream of ventilation equipment.

There is a shower area in Room 107 which appears to be used for storage. If showers, floor drains or other fixtures are unused, the drain traps may dry out and allow sewer gases and odors into occupied spaces. Seldom used drains should be moistened periodically to maintain the trap seal. Drains/fixtures which are no longer needed should be properly cut and capped.

Door sweeps and weather stripping were worn out in some areas of the building (Picture 7). Doors should be made tight-fitting to prevent unconditioned air, moisture and pests from entering the building.

Other Conditions

Low levels of carbon monoxide (CO) were measured in a few areas, including outdoors.   Background reading outside of the GMS measured 2 ppm prior to the assessment. Indoor levels ranged from trace levels (below 1ppm) to 2.9 ppm in one area of the kitchen (near dishwasher). A few rooms and a hallway in one small wing of the 1st floor measured between 1ppm and 2 ppm (Table 1). It is possible that the AHU serving the first floor wing is entraining some CO in the fresh air intake and then distributing it to that wing. Several outside sources of carbon monoxide where observed in close proximity to the GMS AHU fresh air intakes.

- The town Department of public works (DPW) building is close to the GMS (Picture 8). Trucks frequently drive to and from the building and may idle at times during repair work. DPW fleets are usually predominantly diesel which is much lower in CO emissions than gasoline engines.

- The GMS is in close proximity to major roadways which could have an impact on the background CO levels during certain wind directions.

- The GMS appears to have gas-fired boilers with flues that terminate a few feet above the roof line (Picture 9). It is possible that under certain weather conditions (e.g., temperature inversions), the AHUs may draw in products of combustion (including CO) from the flues and distribute them through supply air to the areas served by those AHUs affected.

The Facilities Director was informed of the low levels of CO on the day of this assessment and reported that he would have someone investigate the source. It should be stressed that the low levels of CO experienced during this assessment did not pose an immediate risk to health and safety but when any level is found indoors, the source should be identified and steps taken to mitigate chronic low levels from occurring. The American Conference of Governmental Industrial Hygienists (ACGIH) has assigned carbon monoxide a threshold limit value (TLV) of 25 ppm as a time-weighted average (TWA) for a normal 8-hour workday and a 40-hour workweek (ACGIH 1999).

Exposure to low levels of total volatile organic compounds (TVOCs) may produce eye, nose, throat, and/or respiratory irritation in some sensitive individuals. BEH/IAQ staff examined rooms for products containing VOCs. BEH/IAQ staff noted hand sanitizers, scented products, plug in air fresheners/diffusers and candles, home cleaning products, and dry erase materials in use within the building (Pictures 10 and 11). All of these products have the potential to be irritants to the eyes, nose, throat, and respiratory system of sensitive individuals.

Several of the science classrooms have laboratory hoods (Picture 12). These units are designed to draw pollutants up and out of the building during experiments. In order to ensure they are functioning properly, they need to be calibrated. In addition, no chemicals should be stored in the hoods. Some of the laboratory preparation rooms had storage cabinets for flammable and corrosive materials. These cabinets and other chemical storage should be kept clean and organized.

The wood shop area had several kinds of saws and other wood-cutting/shaving  equipment. A vacuum system is present to collect wood chips and sawdust from the equipment (Pictures 13 and 14). A collection vessel was located both indoors and outdoors. These containers should be emptied regularly and the system maintained so that it is functioning well to remove wood chips and dust. At the time of the visit, there was wood dust and debris on the floor and counters in the room (Picture 15). Wood dust should be cleaned promptly to avoid becoming aerosolized where it can cause irritation; it can also be a slipping hazard when on the floor.

Dust and debris was noted on floors, other flat surfaces and in and on FCUs (Picture 16). This dust and debris should be cleaned periodically. Staff should avoid storing items on top of the vents and discourage students from putting items inside.

Missing ceiling tiles were noted in a few areas. Tiles that are missing from the ceiling system can allow unconditioned air and debris from above into occupied spaces.

A few areas of the school are carpeted and some classrooms have area rugs. Carpeting should be vacuumed regularly with a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner to avoid particulates from causing further irritation or serving as a reservoir for microbial colonization. Also, carpeting and rugs should be cleaned at least once per year according to IICRC recommendations (IICRC 2012). Area rugs too worn to be effectively cleaned should be replaced. Area rugs should be rolled up and stored in a clean, dry place when rooms are not occupied during the summer months to prevent moistening due to condensation.

In many classrooms, large numbers of items were on floors, windowsills, tabletops, counters, bookcases and desks, which provide a source for dusts to accumulate. These items (e.g., papers, folders, boxes) make it difficult for custodial staff to clean. Items should be relocated and/or be cleaned periodically to avoid excessive dust build up. In addition, dust and debris can accumulate on flat surfaces (e.g., desktops, shelving and carpets) in occupied areas and subsequently be re-aerosolized causing further irritation.

Note that the Environmental Protection Agency (EPA) conducted a National School Radon Survey in which it discovered nearly one in five schools had “…at least one frequently occupied ground contact room with short-term radon levels above 4 [picocuries per liter] pCi/L” (US EPA 1993). The BEH/IAQ Program therefore recommends that every school be tested for radon, and that this testing be conducted during the heating season while school is in session in a manner consistent with USEPA radon testing guidelines. Radon measurement specialists and other information can be found at www.nrsb.org and http://aarst-nrpp.com/wp, with additional information at: http://www.mass.gov/eohhs/gov/departments/dph/programs/environmental-health/exposure-topics/iaq/radon.

# Conclusions/Recommendations

# Based on the observations made during the visit, the following is recommended:

# Investigate the source of the low levels of carbon monoxide (CO) measured in Table 1. Ensure CO detectors are in proper working order. Rule out any possible internal CO source such as gas-fired combustion units (e.g. boilers, gas stoves, etc.). Then determine if flue stacks for boilers are at sufficient height/flow velocity to avoid CO entrainment in nearby AHU units. Lastly, determine if other sources of CO could be contributing to the low background levels found outside the GMS and take appropriate measures to mitigate entrainment into the affected AHUs.

# Utilize a system to report and track maintenance issues so that concerns can be reported by staff and maintenance staff can indicate when issues have been resolved.

# Operate the HVAC system to provide for continuous fresh air ventilation during occupied hours.

# Remove furniture and items blocking the front and top of FCUs.

# Consider closing classroom doors for most efficient exhaust vent and thermostat function.

# Use openable windows to supplement fresh air during temperate weather. Ensure all windows are closed tightly at the end of each day. Do not use AC system while windows are opened to prevent condensation/mold growth.

# Consider adopting a balancing schedule of every 5 years for all mechanical ventilation systems, as recommended by ventilation industrial standards (SMACNA, 1994).

# Replace water-damaged ceiling tiles once a leak is discovered and repaired. Ensure that dust from cutting ceiling tiles is cleaned promptly.

# Regularly fill any drains with water that are seldom used. If drains are to be abandoned, ensure they are properly capped.

# Replace any missing or ajar ceiling tiles to avoid pathways to unconditioned areas.

# Keep classroom/office plants in good condition, avoid overwatering, and keep them away from the airstream of ventilation equipment.

# Ensure all refrigerators are kept clean to prevent microbial growth and odors. Clean gaskets and other surfaces with a mild antimicrobial solution to remove debris and mold. If they cannot be adequately cleaned-replace.

# Replace worn out door sweeps. Check for light and drafts around doors.

# Reduce or eliminate the use of air fresheners, scented cleaners, and dry erase materials to reduce irritation.

# Ensure wood dust collection units, air filters and local exhaust fans are turned on whenever the equipment is operating. The collection system should be emptied and maintained regularly to prevent a build-up of wood shavings and filters should be changed per manufacturer recommendations.

# Change filters in HVAC units at least twice a year with MERV 8 or higher filters. Clean HVAC and FCU cabinets of debris and dust when filters are changed.

# Clean supply/exhaust vents and personal fans regularly to remove accumulated dust/debris. Replace surrounding ceiling tiles that cannot be adequately cleaned.

# For buildings in New England, periods of low relative humidity during the winter are often unavoidable. Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low. To control for dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended. Avoid the use of feather dusters. Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

# Clean carpeting and area rugs at least once per year according to IICRC recommendations (IICRC 2012). Area carpets too worn to be effectively cleaned should be replaced. Roll up and store are rugs in a clean, dry place during the summer.

# Relocate or consider reducing the amount of materials stored in classrooms to allow for more thorough cleaning of classrooms. Clean items regularly with a wet cloth or sponge to prevent excessive dust build-up.

# Continue to utilize the US EPA’s (2000), “Tools for Schools”, as an instrument for maintaining a good IAQ environment in the building available at: http://www.epa.gov/iaq/schools/index.html.

# The school should be tested for radon by a certified radon measurement specialist during the heating season when school is in session. Radon measurement specialists and other information can be found at: www.nrsb.org, and http://aarst-nrpp.com/wp.

# Refer to resource manuals and other related IAQ documents for further building-wide evaluations and advice on maintaining public buildings. Copies of these materials are located on the MDPH’s website: http://mass.gov/dph/iaq.

# References

ACGIH. 1989. Guidelines for the Assessment of Bioaerosols in the Indoor Environment. American Conference of Governmental Industrial Hygienists, Cincinnati, OH.

ACGIH. 1999. Guide to Occupational Exposure Values-1999. American Conference of Governmental Industrial Hygienists, Cincinnati, OH.

ASHRAE. 2012. American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) Standard 52.2-2012 -- Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size (ANSI Approved).

IICRC. 2012. Carpet Cleaning FAQ 4 Institute of Inspection, Cleaning and Restoration Certification. Institute of Inspection Cleaning and Restoration, Vancouver, WA.

MDPH. 2015. Massachusetts Department of Public Health. “Indoor Air Quality Manual: Chapters I-III”. Available at: http://www.mass.gov/eohhs/gov/departments/dph/programs/environmental-health/exposure-topics/iaq/iaq-manual/.

SMACNA. 1994. HVAC Systems Commissioning Manual. 1st ed. Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

US EPA. 1993. Radon Measurement in Schools, Revised Edition. Office of Air and Radiation, Office of Radiation and Indoor Air, Indoor Environments Division (6609J). EPA 402-R-92-014. https://www.epa.gov/sites/production/files/2014-08/documents/radon_measurement_in_schools.pdf.

US EPA. 2000. Tools for Schools. Office of Air and Radiation, Office of Radiation and Indoor Air, Indoor Environments Division (6609J). EPA 402-K-95-001, Second Edition. http://www.epa.gov/iaq/schools/index.html.

US EPA. 2008. “Mold Remediation in Schools and Commercial Buildings”. Office of Air and Radiation, Indoor Environments Division, Washington, DC. EPA 402-K-01-001. September 2008. Available at: http://www.epa.gov/mold/mold-remediation-schools-and-commercial-buildings-guide.​

Picture 1

One style of supply vent

Picture 2

Fan coil unit (FCU)

Picture 3

Return/exhaust vent next to door (arrow)

Picture 4

Water-damaged ceiling tile

Picture 5

Spills/debris inside fridge in a teacher’s workroom

Picture 6

Hydroponic plant setup in hallway

Picture 7

Light visible around door showing missing weather stripping

Picture 8

GMS showing close proximity to DPW to the south (arrow)

Picture 9

GMS showing gas boiler flues in close proximity to AHUs

Picture 10

Plug-in air freshener

Picture 11

Scented candles on FCU

Picture 12

Laboratory hood in between science classroom and prep room

Picture 13

Wood chip collection inside wood shop room

Picture 14

Wood shop equipment with vacuum system

Picture 15

Wood dust/debris on floor

Picture 16

Debris inside FCU

| # Location | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | Temp (°F) | Relative Humidity (%) | PM2.5 (µg/m3) | Occupants in Room | Windows Openable | Ventilation |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| Background | 402 | 2.0 | 46 | 58 | 25 | NA | - | - | - | Low level of carbon monoxide (CO) detected –GMS near DPW & busy street |
| Third Floor |  |  |  |  |  |  |  |  |  |  |
| 308 | 673 | ND | 73 | 29 | 4 | 7 | Y | Y | Y | 2 WD CT, DEM, candle on FCU |
| 309 | 618 | ND | 73 | 26 | 4 | 0 | Y 1 open | Y | Y | DEM, FCU |
| 310 | 558 | ND | 72 | 26 | 4 | 1 class left 20 minutes ago | Y | Y | Y | DEM, 3 sinks and gas taps |
| 301 prep room |  |  |  |  |  |  | N | Y | Y | Hood and exhaust vent. No calibration sticker for hood, sink and gas tap, microwave, refrigerator and dish washer |
| 6th grade girls restroom |  |  |  |  |  |  | N | Y | Y dusty | Floor drains |
| 313 locked |  |  |  |  |  |  | N | Y | Y |  |
| 317 project room | 653 | ND | 72 | 28 | 4 | 10 | N | Y | Y | Sink, high ceilings, art items, messy storage closet, DEM |
| 318 Teachers’ workroom | 519 | ND | 73 | 27 | 4 | 0 | N | Y | Y | DEM, food, sink, fridge, microwave, toaster oven, PC |
| 319 | 715 | ND | 72 | 28 | 5 | 25 | N | Y | Y | Skylights, DEM, HS |
| 076 | 535 | ND | 73 | 26 | 3 | 0 | N | Y | Y | Office, carpet, HS |
| 031 | 552 | ND | 73 | 26 | 5 | 0 | N | Y | Y | Office, DEM, carpet, plants |
| 320 | 543 | ND | 74 | 25 | 4 | 0 | N | Y | Y | Office/classroom, sinks, DEM, plants |
| 307 | 540 | ND | 73 | 26 | 10 | 1 | Y | Y | Y | DEM, hood |
| 307 prep room |  |  |  |  |  |  |  |  |  | Dishwasher, sink and gas tap, microwave, refrigerator, room is disorganized |
| 306 | 623 | ND | 73 | 29 | 7 | 10 | Y | Y | Y | DEM, HS |
| 336 | 1033 | ND | 72 | 31 | 5 | 16 | N | Y | Y | Skylights, sinks and gas taps, DEM, hood, fridge, emergency shower and eyewash |
| 336 prep room is locked |  |  |  |  |  |  |  |  |  | Looks clean and organized, has dishwasher, microwave, sink and gas tap |
| 337 | 624 | ND | 72 | 26 | 5 | 3 | N | Y | Y | Skylight, DEM, sink, HS |
| 338 project room | 546 | ND | 73 | 27 | 4 | 4 | N | Y | Y | High ceilings, sink, DEM |
| 339 | 512 | ND | 73 | 25 | 5 | 0 | N | Y | Y | Teachers workroom, DEM, food, microwave, toaster oven (crumbs) |
| 340 | 496 | ND | 73 | 25 | 4 | 0 | N | Y | Y | Small office, DEM |
| 349 | 939 | ND | 73 | 28 | 2 | 20 | Y | Y | Y | DEM, food/AF odor, plant over FCU |
| 348 | 729 | ND | 73 | 27 | 3 | 21 | Y | Y | Y | DEM, emergency shower and eyewash, sinks and gas taps, hood, HS |
| 348 prep room |  |  |  |  |  |  |  |  |  | Items on floor, dust/debris, appliances, hood |
| 346 | 875 | ND | 74 | 28 | 3 | 19 | Y | Y | Y | DEM |
| 328 | 580 | ND | 74 | 26 | 3 | 0 | Y | Y | Y | Plants, DEM, HS |
| 326 | 512 | ND | 73 | 27 | 3 | 2 | Y | Y | Y | DEM |
| 325 | 859 | ND | 73 | 29 | 3 | 7 more left during class change | Y | Y | Y | DEM, WD CT |
| 300 | 712 | ND | 72 | 29 | 5 | 22 left 15 min ago | Y | Y | Y | DEM |
| 301 | 652 | ND | 72 | 28 | 4 | 0 | Y | Y | Y | DEM |
| 302 | 968 | ND | 72 | 31 | 4 | 23 | Y | Y | Y | DEM, WD CT |
| 303 | 981 | ND | 72 | 31 | 4 | 17 | Y | Y | Y | DEM |
| 304 | 732 | ND | 73 | 27 | 5 | 1 | Y | Y | Y | HS |
| 305 | 700 | ND | 72 | 28 | 4 | 1 | Y | Y | Y | FCU with inefficient filters that keep falling down onto ground (no filter rack to secure in place) |
| 331 | 1006 | ND | 72 | 29 | 1 | 14 | Y | Y | Y | DEM |
| 332 | 1056 | ND | 73 | 31 | 3 | 20 | Y | Y | Y | DEM |
| 333 | 928 | ND | 73 | 28 | 1 | 25 | Y | Y | Y | DEM |
| 334 | 939 | ND | 73 | 28 | 3 | 17 | Y | Y | Y | DEM, DO with exhaust vent in close proximity |
| 335 | 1001 | ND | 73 | 28 | 1 | 15 | Y | Y | Y | DEM |
| Hallway | - | - | - | - | - | - | - | - | - | WD above locker 3511 |
| 350 | 1140 | ND | 73 | 30 | 2 | 24 | Y | Y | Y | DEM |
| 347 | 957 | ND | 74 | 29 | 1 | 14 | Y | Y | Y | CPs, DEM, HS |
| 330 | 903 | ND | 73 | 29 | 1 | 18 | Y | Y | Y |  |
| 329 | 538 | ND | 72 | 26 | 3 | 0 | Y | Y | Y | DO near exhaust vent, HS, WD CT x 2, AI |
| 327 | 566 | ND | 71 | 27 | 1 | 2 | Y | Y | Y | Housekeeping needed, WD CTs x 3, CPs, FCU filter down |
| 2nd floor |  |  |  |  |  |  |  |  |  |  |
| 217 | 579 | ND | 73 | 29 | 4 | 0 | N | Y | Y | Workroom, microwave, fridge, DEM, PC, utility space behind/in workroom with missing CT and ductwork |
| 218 project room | 507 | ND | 74 | 26 | 3 | 0 | N | Y | Y | Sink, microwave, food odors, skylights, high ceilings, DEM, HS |
| 221 | 615 | ND | 73 | 26 | 5 | 0 | N | Y | Y | Office, area rug, DEM |
| 220 | 533 | ND | 74 | 26 | 4 | 0 | N | Y | Y | Plug-in AF, PF |
| 065D | 510 | ND | 73 | 24 | 5 | 1 | Y | Y | Y | Carpet and area rug |
| 065 storage |  |  |  |  |  |  |  |  |  | Items on floor |
| Upper auditorium | 564 | ND | 73 | 24 | 7 | 0 | N | Y | Y | Carpet and UF |
| 233 | 883 | ND | 73 | 28 | 4 | 16 | Y | Y | Y | FCU is making new loud noise, FCU filter on floor, DEM |
| 232 | 704 | ND | 73 | 27 | 5 | 1 | Y | Y | Y | DEM, sinks, soiled floor |
| 219 | 509 | ND | 73 | 25 | 4 | 0 | N | Y | Y | Plug-in AF, DEM, HS, heater |
| 213 | 815 | ND | 76 | 25 | 3 | 0 | N | Y | Y | Small classroom, feels hot and stuffy |
| 210 | 629 | ND | 74 | 27 | 4 | 13 | Y | Y | Y | Sink and gas taps, DEM, plants, HS |
| 210 prep room |  |  |  |  |  |  |  |  |  | Sink and gas taps, fridge, microwave, chemical storage (not many chemicals) |
| 209 | 790 | ND | 75 | 28 | 4 | 21 | Y | Y | Y | DEM, DO |
| 208 | 586 | ND | 74 | 25 | 4 | 0 | Y | Y | Y | DEM, FCU, filter on floor |
| 200 | 727 | ND | 74 | 28 | 4 | 21 | Y | Y | Y | DEM, FCU filter on floor, DO |
| 201 | 941 | ND | 75 | 31 | 3 | 19 | Y | Y | Y | DEM |
| 202A | 605 | ND | 74 | 27 | 4 | 3 | Y | Y | Y | DEM, UF, area rug, divider |
| 202B | 578 | ND | 74 | 26 | 4 | 0 | Y | Y | Y | FCU filter on floor, FCU squeaks, DEM |
| 225 | 575 | ND | 71 | 28 | 1 | 12 | Y | Y | Y | DEM, HS, DO |
| 226 | 1036 | ND | 72 | 33 | 2 | 23 | Y | Y | Y | DEM |
| 227 | 955 | ND | 73 | 31 | 3 | 21 | Y | Y | Y | DEM |
| 228 | 841 | ND | 73 | 30 | 3 | 21 | Y | Y | Y | DO w/nearby exhaust vent, HS |
| 229 | 716 | ND | 72 | 28 | 2 | 21 | Y | Y | Y | Plants, DEM |
| 065E | 542 | ND | 72 | 26 | 2 | 1 | Y | Y | Y | Carpet tiles |
| 065C | 601 | ND | 74 | 27 | 2 | 2 | Y | Y | Y | Carpet |
| 232 | 680 | ND | 73 | 27 | 2 | 1 | Y | Y | Y | Dusty vents |
| 231 | 654 | ND | 72 | 27 | 1 | 0 | Y | Y | Y | Plants |
| 230 | 753 | ND | 73 | 28 | 1 | 19 | Y | Y | Y | HS, FCU filter on ground |
| 207 | 703 | ND | 73 | 28 | 2 | 25 | Y | Y | Y | HS, DEM, WD CT |
| 206 | 738 | ND | 73 | 28 | 1 | 19 | Y | Y | Y | DEM |
| 205 | 904 | ND | 74 | 30 | 1 | 18 | Y | Y | Y |  |
| 204 | 877 | ND | 74 | 29 | 1 | 17 | Y | Y | Y | DEM |
| 203 | 581 | ND | 74 | 26 | 2 | 1 | Y | Y | Y | HS, FCU filter fell down |
| 1st floor |  |  |  |  |  |  |  |  |  |  |
| 100 | 811 | ND | 73 | 30 | 4 | 20 | Y | Y | Y | DEM, students sitting on floors (and in adjacent classrooms and hallways), sink |
| 101 | 797 | ND | 73 | 30 | 3 | 15 | Y | Y | Y | DEM, dust/debris on floor |
| 102 | 778 | ND | 73 | 30 | 3 | 17 | Y | Y | Y | Sink, DEM, items on FCU, AI |
| 103 | 755 | ND | 75 | 31 | 4 | 19 | Y | Y | Y | Many candles including on FCU, HS, DEM, plush toys |
| 104 | 593 | ND | 74 | 25 | 4 | 3 | Y | Y | Y | Salt lamp, DEM |
| 105 | 694 | ND | 74 | 28 | 5 | 17 | Y | Y | Y | Sink, dirty floor, FCU off, debris in FCU |
| 106 | 858 | ND | 74 | 29 | 3 | 18 | Y | Y | Y | Dust and debris in FCU, plants, DEM |
| 107 | 654 | ND | 73 | 27 | 4 | 5 | Y | Y | Y | UF, kitchen equipment, washer/dryer. Attached shower room appears unused, check drains, DEM |
| 124 | 601 | ND | 72 | 27 | 5 | 16 | N | Y | Y | Computer, dirty floors, DEM |
| 121 media classroom with TV studio | 521 | ND | 72 | 26 | 4 | 0 | N | Y | Y | DEM, computers |
| 030 main office | 713 | ND | 72 | 29 | 4 | 5 | Y | Y | Y |  |
| Assistant Principal | 644 | ND | 73 | 27 | 5 | 0 | Y | Y | Y | Plants, DEM |
| Mr. Colantuoni | 615 | ND | 74 | 26 | 6 | 0 | Y | Y | Y | Tiny room, DEM, NC |
| 031 SRO | 623 | ND | 74 | 27 | 5 | 0 | Y | Y | Y | Plants, carpet |
| 044 | 741 | ND | 74 | 27 | 7 | 2 | Y | Y | Y | Carpet |
| 036 | 684 | ND | 74 | 28 | 6 | 0 | N | Y | Y | Carpet, DEM, streamers |
| Admin kitchenette |  |  |  |  |  |  |  |  |  | Dishes in sink, toaster oven with crumbs, microwave |
| 038 conference | 637 | ND | 74 | 27 | 6 | 0 | Y | Y | Y | Carpet, DEM |
| 035 | 671 | ND | 73 | 26 | 5 | 0 | Y | Y | Y | Carpet |
| Staff women’s restroom |  |  |  |  |  |  | N | N | Y | AF odor |
| Cafeteria | 886 | 1.3 | 73 | 31 | 5 | ~400 | N | Y | Y | Low level of CO detected |
| 107? (technology) | 714 | ND | 72 | 29 | 3 | 21 | Y | Y | Y | Sink, dusty floor, DEM |
| Wood shop |  |  |  |  |  |  | N | Y | Y | Wood dust collection system, wood cutting equipment, dust/debris on floor |
| 125 |  | 1.2 | 71 | 30 | 4 | 0 | Y | Y | Y | DEM, dust/debris on floor, low level of CO detected |
| Nurse | 654 | ND | 71 | 30 | 5 | 2 |  | Y | Y | WD CT in rest area |
| 050 | 612 | ND | 72 | 29 | 5 | 1 | Y | Y | Y | Faculty lunch, debris in fridge, vending |
| 145 | 601 | ND | 72 | 28 | 2 | 1 | Y | Y | Y | Music mac lab, DEM |
| 146 | 739 | ND | 72 | 30 | 3 | 40-50 | Y | Y | Y | Chorus, DEM, guitars, sink |
| 147 | 711 | ND | 72 | 27 | 2 | 0 | Y | Y | Y | Sink, NC, guitars, drums |
| 055 | 646 | ND | 72 | 29 | 3 | 3 | N | Y | Y |  |
| 018 | 472 | ND | 67 | 29 | 9 | 0 | N | Y | Y | WD CT in hallway |
| 108 | 607 | ND | 73 | 26 | 1 | 0 | Y | Y | Y | AI, boxes on slab floor, HS |
| 109 | 903 | ND | 72 | 31 | 1 | 21 | Y | Y | Y | DEM, CP |
| 110 | 921 | ND | 73 | 30 | 1 | 20 | Y | Y | Y | WD CT |
| 111 | 660 | ND | 73 | 28 | 2 | 1 | Y | Y | Y | Boxes on slab floor |
| 113 | 585 | ND | 72 | 27 | 1 | 1 | N | Y | Y |  |
| 117 | 592 | ND | 72 | 27 | 1 | 4 | N | Y | Y |  |
| 118 | 622 | ND | 72 | 27 | 1 | 0 | N | Y | Y | PC, paper stored on slab floor |
| 119 | 593 | ND | 72 | 27 | 1 | 2 | N | Y | Y | DEM |
| Library-front | 645 | ND | 72 | 26 | 1 | 3 | N | Y | Y | Carpet tiles |
| Library-center | 640 | ND | 72 | 26 | 2 | 5 | N | Y | Y | PC |
| Café-front | 914 | 1.0 | 72 | 32 | 1 | 70+ | N | Y | Y | Low level of CO detected |
| Kitchen | - | 1.3-2.9 | - | - | - | - | - | - | Y | Low levels of CO detected, highest near dishwasher (dishwasher exhaust was off during assessment) |
| 128 | 750 | ND | 72 | 30 | 1 | 1 | Y | Y | Y | CP, DEM, HS, FCU filter off |
| 127 | 747 | 1.0 | 72 | 30 | 1 | 1 | Y | Y | Y | CPs, FCU filter off, CO low level |
| Hallway near 127 | - | 2.0 | - | - | - | - | - | - | - | Low level of CO detected |
| 126 | 815 | 1.0 | 71 | 30 | 1 | 0 | Y | Y | Y | DEM, low level CO detected |
| Auditorium | 862 | ND | 69 | 30 | 1 | 40+ | N | Y | Y | Carpet |
| 149 Instruments | 552 | ND | 70 | 30 | 1 | 0 | Y | Y | Y | WD x 10 in Hall, 1 WD CT inside |
| Gym | 774 | ND | 69 | 34 | 1 | ~50 | N | Y | Y | Wood floor |
| 22 | 481 | 1.3 | 66 | 31 | 14 | 0 | N | Y | N | Hall door open to outside, low level CO detected |