INDOOR AIR QUALITY

FOLLOW-UP ASSESSMENT

Georgetown Middle/High School

11 Winter Street

Georgetown, MA

Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health

Indoor Air Quality Program

July 2010

# Background/Introduction

At the request of Carol Jacobs, Superintendent of Georgetown Public Schools (GPS), the Massachusetts Department of Public Health (MDPH), Bureau of Environmental Health (BEH) provided assistance and consultation regarding indoor air quality concerns at the Georgetown Middle/High School, 11 Winter Street, Georgetown, Massachusetts (the building).  The purpose of this visit was to assess the adequacy of repairs made to the heating, ventilating and air conditioning system, as well as to address concerns of musty odors in the band room.  A report detailing the previous MDPH assessment conducted in October 2008 includes observations at the time of assessment and recommendations for improving indoor air quality (MDPH, 2009a).  On March 12, 2010, a visit to conduct a follow-up assessment was made by Michael Feeney, Director of BEH’s Indoor Air Quality (IAQ) Program.  Mr. Feeney was accompanied by Sharon Lee, an Environmental Analyst/Inspector within BEH’s IAQ Program.

The school is a multi-level brick building originally constructed in 1962.  An addition was built in 1969.  In 1997, renovations were made to the building.  Windows are openable throughout the building.

# Methods

Air tests for carbon dioxide, carbon monoxide, temperature and relative humidity were conducted with the TSI, Q-TRAK™ IAQ Monitor, Model 7565.  Air tests for airborne particulate matter with a diameter less than 2.5 micrometers were taken with the TSI, DUSTTRAK™ Aerosol Monitor Model 8520.  BEH staff also performed a visual inspection of building materials for water damage and/or microbial growth.

# Results

The building houses both middle and high school students in grades 6 through 12 with a student population of approximately 800 and a staff of approximately 110.  Tests were taken during normal operations and results appear in Table 1.

# Discussion

## Ventilation

It can be seen from Table 1 that carbon dioxide levels were above 800 parts per million (ppm) in 30 of 71 areas surveyed.  These results demonstrate improvement over previous air sampling period in a number of areas.  Of note is the reduction of carbon dioxide levels when 2008 results are compared to those of 2010.  Overall, carbon dioxide levels were uniformly lower across the building, regardless of differences in the number of room occupants (Table 2); however, a number of areas still warrant further improvement.  The reductions observed in some areas are due to reactivation of rooftop exhaust vents, which were reported to be repaired prior to the 2010 reassessment.

Unit ventilators (univents) that supply fresh outside air to classrooms were operating during the reassessment.  The operation of univents in combination with the reactivation of rooftop exhaust vents would play a significant role in reducing carbon dioxide levels, improving airflow in the building and resulting in increased comfort for building occupants.  However, it is also important to note that several areas were sparsely populated or unoccupied at the time carbon dioxide measurements were taken, which can greatly reduce carbon dioxide levels.  Carbon dioxide levels would be expected to be higher with full occupancy.

As discussed in a previous report, some classroom exhaust vents are located at the base of the wall near the classroom’s door.  The exhaust capabilities of these vents can be diminished when classroom doors are open.  In one instance, the vent was drawing air from the hallway due to its proximity to the open door.  Doors should be closed to maximize exhaust capabilities.

Mechanical ventilation for common areas such as the auditorium, cafeteria and gymnasiums is provided by rooftop or ceiling-mounted air handling units (AHUs).  AHUs distribute fresh air via ceiling-mounted air diffusers and returns stale air back to AHUs via exhaust vents.

To maximize air exchange, the MDPH recommends that both supply and exhaust ventilation operate continuously during periods of occupancy.  In order to have proper ventilation with a mechanical supply and exhaust system, the systems must be balanced to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room.  It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).  The systems at the building have not been balanced since the exhaust vent fans were repaired.

The Massachusetts Building Code requires that each room have a minimum ventilation rate of 15 cubic feet per minute (cfm) per occupant of fresh outside air or openable windows (SBBRS, 1997; BOCA, 1993).  The ventilation must be on at all times the room is occupied.  Providing adequate fresh air ventilation with open windows and maintaining the temperature in the comfort range during the cold weather season is impractical.  Mechanical ventilation is usually required to provide adequate fresh air ventilation.

Carbon dioxide is not a problem in and of itself.  It is used as an indicator of the adequacy of the fresh air ventilation.  As carbon dioxide levels rise, it indicates that the ventilating system is malfunctioning or the design occupancy of the room is being exceeded.  When this happens, a buildup of common indoor air pollutants can occur, leading to discomfort or health complaints.  The Occupational Safety and Health Administration (OSHA) standard for carbon dioxide is 5,000 parts per million parts of air (ppm).  Workers may be exposed to this level for 40 hours/week, based on a time-weighted average (OSHA, 1997).

The MDPH uses a guideline of 800 ppm for publicly occupied buildings.  A guideline of 600 ppm or less is preferred in schools due to the fact that the majority of occupants are young and considered to be a more sensitive population in the evaluation of environmental health status.  Inadequate ventilation and/or elevated temperatures are major causes of complaints such as respiratory, eye, nose and throat irritation, lethargy and headaches.  For more information concerning carbon dioxide, consult Appendix A.

Temperature measurements in the building ranged from 65° F to 78° F, which were below the MDPH recommended range in some areas surveyed during the assessment (Table 1).  The MDPH recommends that indoor air temperatures be maintained in a range of 70o F to 78o F in order to provide for the comfort of building occupants.  In many cases concerning indoor air quality, fluctuations of temperature in occupied spaces are typically experienced, even in a building with an adequate fresh air supply.

The relative humidity in the building ranged from 23 to 37 percent, which was below the MDPH recommended comfort range (Table 1).  The MDPH recommends a comfort range of 40 to 60 percent for indoor air relative humidity.  Relative humidity levels in the building would be expected to drop during the winter months due to heating.  The sensation of dryness and irritation is common in a low relative humidity environment.  Low relative humidity is a very common problem during the heating season in the northeast part of the United States.

## Microbial/Moisture Concerns

During the course of this follow-up assessment, a number of issues related to water damage were noted.  A musty odor was detected in a band instrument storage room.  The musty odor was traced to a variety of instrument cases that are stored in this room.  A number of large brass instrument cases were opened and each had a distinct musty odor, indicating likely mold contamination.  The instrument cases are constructed of leather, cardboard, glue and a carpet-like lining, which are all porous materials that can support mold colonization.  The band room does not have a HVAC system capable of providing temperature and humidity control during hot, humid weather.  Without adequate temperature and relative humidity control, materials that are highly susceptible to mold growth will become moistened in hot, humid weather and lead to microbial colonization.

A material installed on exterior walls of the band wing is enhancing humidity levels in the band room.  The exterior wall material in this area appears discolored in an asymmetrical pattern (Picture 1).  This patterning of the wall system may indicate that rainwater is being held between the exterior wall system and the original cement block exterior wall.  In this configuration, moisture is likely to pass into the interior of the band room, resulting in increased relative humidity and moistening of carpets and other materials susceptible to mold colonization.  In addition, it appears that this wall system has been chronically damaged by moisture resulting from pipes that drain water from the band room’s flat roof onto the exterior wall (Pictures 2 and 3).

The wall covering on the exterior of the band room wing is likely exterior insulating foam system (EIFS).  EIFS, commonly known as fake stucco, “is an exterior wall cladding that utilizes rigid insulation boards on the exterior of the wall sheathing with a plaster type exterior skin” (Zwayer, 2007).  “An EIFS wall typically consists of several layers of materials sandwiched together into a single panel, which is attached to a substrate mounted on the wall studs” (Figure 1) (FEMA, Unknown).  In buildings constructed with a curtain wall, water is intercepted by a drainage plane once it penetrates through the brickwork; the drainage plane allows water to exit the wall system through weep holes (Figure 2).  The EIFS system on the band room wing appears to be a barrier wall system.  The “barrier EIFS wall systems rely primarily on the base coat portion of the exterior skin to resist water penetration” (Zwayer, 2007).  In essence, the rainwater is shed by the exterior “stucco” surface, which functions as drainage plane (Figure 1).  However, a number of problems exist with such a system:

Problems observed with EIFS installations are primarily related to moisture intrusion.  EIFS provides protection against moisture infiltration at the base coat; however, moisture migration through openings for windows, flashings and other items, or holes and cracks in the EIFS itself, have allowed for moisture invasion of EIFS clad buildings.  With barrier EIFS installations, or where weather barriers and flashing are improperly installed in conjunction with wall drainage EIFS installations, moisture has entered the wall system at these locations and caused damage to the wall sheathing and framing (emphasis added) (Zwayer, G.L., 2007).

Since the initial introduction of EIFS, a second type of system, which contains a water drainage system similar to Figure 2 was developed.  The EIFS system at the building is not likely a water drainage system due to the following:

- Lack of weep holes exist on the exterior wall; and

- Lack of drainage plane behind the substrate;

Considering these observations, the EIFS system installed on the band room wing of the building is most likely a barrier system which has little or no means to drain water from the wall system.

According to the National Institute of Building Science (NIBS), the following are problems typical of buildings clad with EIFS; these same conditions were also observed at the building:

- Failure to install or properly install sealant joints around windows, doors, pipes, conduits, and other penetrations of the field of the EIFS;

- Failure to flash window and door openings in the field of the EIFS to divert leakage through the window or door to the exterior;

- Failure to properly backwrap edges of EIFS at terminations and penetrations in the field of the EIFS (Picture 4); and

- Water erosion damage that has not been repaired (Picture 3).

Each of these conditions can allow for water to penetrate through the EIFS, causing water damage to carpet and interior walls in the band wing.  It is also important to note that significant portions of the main building are also clad with EIFS, which have a similar type of pattern on the wall surface which may indicate water penetration through the installed wall system.  While this condition does not appear to currently affect the main building, it should be closely monitored for water penetration.

Relative humidity in excess of 70 percent can provide an environment for mold and fungal growth (ASHRAE, 1989).  In the experience of MDPH staff, excessively humid weather can provide enough airborne water vapor to create adequate conditions for mold growth in buildings, particularly in porous materials that are stored under these conditions.  The US Environmental Protection Agency (US EPA) and the American Conference of Governmental Industrial Hygienists (ACGIH) recommend that porous materials be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2001; ACGIH, 1989).  If not dried within this time frame, mold growth may occur.

Water-damaged/missing ceiling tiles were noted in a number of areas throughout the building.  Water-damaged ceiling tiles can indicate sources of water penetration and provide a source of mold.  Ceiling tiles should be replaced after a water leak is discovered and repaired.  Once mold has colonized porous materials, they are difficult to clean and should be removed/discarded.

Plants were noted in several classrooms.  Plants can be a source of pollen and mold, which can be respiratory irritants for some individuals.  Plants should be properly maintained and equipped with drip pans to prevent water damage to porous building materials, which can lead to mold growth.  Plants should also be located away from ventilation sources (e.g., air intakes, univent diffusers) to prevent the entrainment and/or aerosolization of dirt, pollen or mold.

## Other IAQ Evaluations

Indoor air quality can be negatively influenced by the presence of respiratory irritants, such as products of combustion.  The process of combustion produces a number of pollutants.  Common combustion emissions include carbon monoxide, carbon dioxide, water vapor and smoke (fine airborne particle material).  Of these materials, exposure to carbon monoxide and particulate matter with a diameter of 2.5 micrometers (μm) or less (PM2.5) can produce immediate, acute health effects upon exposure.  To determine whether combustion products were present in the indoor environment, BEH staff obtained measurements for carbon monoxide and PM2.5.

### Carbon Monoxide

Carbon monoxide is a by-product of incomplete combustion of organic matter (e.g., gasoline, wood and tobacco).  Exposure to carbon monoxide can produce immediate and acute health affects.  Several air quality standards have been established to address carbon monoxide and prevent symptoms from exposure to these substances.  The MDPH established a corrective action level concerning carbon monoxide in ice skating rinks that use fossil-fueled ice resurfacing equipment.  If an operator of an indoor ice rink measures a carbon monoxide level over 30 ppm, taken 20 minutes after resurfacing within a rink, that operator must take actions to reduce carbon monoxide levels (MDPH, 1997).

The American Society of Heating Refrigeration and Air-Conditioning Engineers (ASHRAE) has adopted the National Ambient Air Quality Standards (NAAQS) as one set of criteria for assessing indoor air quality and monitoring of fresh air introduced by HVAC systems (ASHRAE, 1989).  The NAAQS are standards established by the US EPA to protect the public health from six criteria pollutants, including carbon monoxide and particulate matter (US EPA, 2006).  As recommended by ASHRAE, pollutant levels of fresh air introduced to a building should not exceed the NAAQS levels (ASHRAE, 1989).  The NAAQS were adopted by reference in the Building Officials & Code Administrators (BOCA) National Mechanical Code of 1993 (BOCA, 1993), which is now an HVAC standard included in the Massachusetts State Building Code (SBBRS, 1997).  According to the NAAQS, carbon monoxide levels in outdoor air should not exceed 9 ppm in an eight-hour average (US EPA, 2006).

Carbon monoxide should not be present in a typical, indoor environment.  If it is present, indoor carbon monoxide levels should be less than or equal to outdoor levels.  On the day of the assessment, outdoor carbon monoxide concentrations were non-detect (ND) (Table 1).  No measurable levels of carbon monoxide were detected in the building at the time of the assessment (Table 1).

### Particulate Matter

The US EPA has established NAAQS limits for exposure to particulate matter.  Particulate matter is airborne solids that can be irritating to the eyes, nose and throat.  The NAAQS originally established exposure limits to particulate matter with a diameter of 10 μm or less (PM10).  According to the NAAQS, PM10 levels should not exceed 150 micrograms per cubic meter (μg/m3) in a 24-hour average (US EPA, 2006).  These standards were adopted by both ASHRAE and BOCA.  Since the issuance of the ASHRAE standard and BOCA Code, US EPA established a more protective standard for fine airborne particles.  This more stringent PM2.5 standard requires outdoor air particle levels be maintained below 35 μg/m3 over a 24-hour average (US EPA, 2006).  Although both the ASHRAE standard and BOCA Code adopted the PM10 standard for evaluating air quality, MDPH uses the more protective PM2.5 standard for evaluating airborne particulate matter concentrations in the indoor environment.

Outdoor PM2.5 concentrations the day of the assessment were measured at 5 μg/m3.  PM2.5 levels measured inside the building were below the NAAQS PM2.5 level of 35 μg/m3 in all but two areas.  The kiln room and the adjacent art office measured 38 and 39 μg/m3 respectively, slightly exceeding the NAAQS PM2.5 level of 35 μg/m3 (Table 1).  The elevated PM2.5 levels were related to aerosolized clay fumes from the pottery kiln, which was in operation at the time of the PM2.5 testing.  It is important to note that the exhaust vent for the kiln was not ducted in this area, which would serve to remove airborne fumes and particulates from the source.  Clay fumes can be irritating to the eyes, nose, throat and respiratory system.  Frequently, indoor air levels of particulates (including PM2.5) can be at higher levels than those measured outdoors.  A number of mechanical devices and/or activities that occur indoors can generate particulate during normal operations.  Sources of indoor airborne particulates may include but are not limited to: particles generated during the operation of fan belts in the HVAC system; cooking in the cafeteria stoves and microwave ovens; use of photocopiers, fax machines and computer printing devices; operation of an ordinary vacuum cleaner; and, heavy foot traffic indoors.

### Volatile Organic Compounds

Indoor air concentrations can be greatly impacted by the use of products containing volatile organic compounds (VOCs).  VOCs are carbon-containing substances that have the ability to evaporate at room temperature.  Frequently, exposure to low levels of total VOCs (TVOCs) may produce eye, nose, throat and/or respiratory irritation in some sensitive individuals.  For example, chemicals evaporating from a paint can stored at room temperature would most likely contain VOCs.  Materials containing VOCs were present in the building.

Of note was the distinct odor of hand disinfectant, which could be readily detected in some classrooms.  Hand disinfectant contains ethyl alcohol and fragrances, both of which can be eye and respiratory irritants to some individuals (Betco Corporation, 2007; Birchwood Laboratories, Inc., 2007; B4 Brands by AMA, 2006; Georgia-Pacific Consumer Products, 2007).  According to MDPH recommendations concerning H1N1 Flu, protection from flu virus can be achieved by either washing your hands often with soap and water or using alcohol-based hand gel (MDPH, 2009b, Appendix B).

Several classrooms contained dry erase boards and dry erase board markers.  Materials such as permanent markers, dry erase markers and dry erase board cleaners may contain VOCs, such as methyl isobutyl ketone, n-butyl acetate and butyl-cellusolve (Sanford, 1999), which can be irritating to the eyes, nose and throat.

Cleaning products were also observed in a number of classrooms (Table 1).  Like dry erase materials, cleaning products contain VOCs and other chemicals.  These chemicals can be irritating to the eyes, nose and throat and should be kept out of reach of students.  Additionally, a Material Safety Data Sheet (MSDS) should be available at a central location for each product in the event of an emergency.  Consideration should be given to providing teaching staff with school issued cleaning products to ensure that MSDS information is available for all products used at the school.

Air fresheners and deodorizing materials were observed in some areas (Table 1).  Air deodorizers contain chemicals that can be irritating to the eyes, nose and throat of sensitive individuals.  Many air fresheners contain 1,4-dichlorobenzene, a VOC which may cause reductions in lung function (NIH, 2006).  Furthermore, deodorizing agents do not remove materials causing odors, but rather mask odors that may be present in the area.

### Other Conditions

Other conditions that can affect indoor air quality were observed during the assessment.  In several classrooms, items were observed on the floor, windowsills, tabletops, counters, bookcases and desks.  The large number of items stored in classrooms provides a source for dusts to accumulate.  These items (e.g., papers, folders, boxes) make it difficult for custodial staff to clean.  Items should be relocated and/or be cleaned periodically to avoid excessive dust build up.  In addition, these materials can accumulate on flat surfaces (e.g., desktops, shelving and carpets) in occupied areas and subsequently be re-aerosolized causing further irritation.

Of note was the use of containers that previously contained food products.  Exposed food products and use of containers originally intended for foods can attract a variety of pests. The presence of pests inside a building can produce conditions that can degrade indoor air quality. For example, rodent infestation can result in indoor air quality related symptoms due to materials in their wastes.  Mouse urine is known to contain a protein that is a known sensitizer (US EPA, 1992).  A sensitizer is a material that can produce symptoms in exposed individuals, including nose irritations and skin rashes.  Pest attractants should be reduced/eliminated.  Proper food storage is an integral component in maintaining indoor air quality.  Food should be properly stored and clearly labeled.  Reuse of food containers (e.g., for art projects) is not recommended since food residue adhering to the container surface may serve to attract pests

# Conclusions/Recommendations

The repairs to exhaust vent fans have increased airflow throughout the building, since carbon dioxide levels appear to be significantly lower in some areas evaluated in this assessment when compared to the previous air sampling; however, a number of areas still warrant further attention.  With the repair of that system, the activity that would be most helpful to further increase airflow would be to balance the HVAC system.  Also of note is the continued problem regarding musty odors in the band room.  The most obvious source of odors appears to be the old instrument cases that are subjected to moist conditions created by poor water drainage from the building envelope as well as hot, humid weather during summer months.  In view of the findings at the time of the assessment, the following recommendations are made to improve indoor air quality:

- Continue with plans to balance the HVAC system.  Consider adopting a balancing schedule of every 5 years for all mechanical ventilation systems, as recommended by ventilation industrial standards (SMACNA, 1994).

- Ensure all exhaust vents are repaired and are operating.  Close classroom doors to maximize exhaust capabilities.

- Install downspouts on pipes that drain the flat roof of the band room to prevent further water damage to the EIFS exterior wall.  Consideration should be given to removing the EIFS exterior wall system on the band room.  If this is done, the exterior of the cement block should be sealed with an appropriate material.  Consideration should be given to consulting a building engineer on the most appropriate method for repairing the band room exterior wall.

- Monitor main building for signs of water penetration through he building envelope, make repairs as necessary.

- Consideration should be given to replacing instrument cases that have become mold colonized.  One method that may be used in the interim to prevent further exposure would be to wrap each half of an instrument case with an airtight covering of plastic so that the materials that are moldy are sealed.

- Use openable windows in conjunction with mechanical ventilation to facilitate air exchange.  Care should be taken to ensure windows are properly closed at night and weekends to avoid the freezing of pipes and potential flooding.

- Consider installing mechanical ventilation to the band rooms to control airflow, temperature and relative humidity.  At the least, dehumidifiers should be used during hot, humid months.

- Clean/maintain dehumidifiers as per the manufactures instructions or more frequently if needed.

- Repair any existing water leaks and replace water-damaged ceiling tiles.  Examine the area above these tiles for mold growth.  Disinfect areas of water leaks with an appropriate antimicrobial, as needed.

- Ensure plants are equipped with drip pans.  Examine drip pans periodically for mold growth and disinfect with an appropriate antimicrobial, as needed. Move plants away from univents.

- For buildings in New England, periods of low relative humidity during the winter are often unavoidable.  Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low.  To control for dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended.  Avoid the use of feather dusters.  Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

- Ensure kiln is vented to the outdoors and operating during kiln-firing operations.

- It is highly recommended that the principles of integrated pest management (IPM) be used to rid the building of pests. A copy of the IPM recommendations can be obtained from the Massachusetts Department of Food and Agriculture (MDFA) website at the following website: http://www.state.ma.us/dfa/pesticides/publications/IPM_kit_for_bldg_mgrs.pdf. Activities that can be used to eliminate pest infestation may include the following activities.

  - Do not use food as components in student artwork.

  - Rinse out recycled food containers. Seal recycled containers in a tight fitting lid to prevent rodent access.

  - Stored foods in tight fitting containers.

  - Avoid eating at workstations. In areas were food is consumed, periodic vacuuming to remove crumbs are recommended.

  - Regularly clean crumbs and other food residues from ovens, toasters, toaster ovens, microwave ovens coffee pots and other food preparation equipment;

  - Holes as small as ¼” are enough space for rodents to enter an area.  Examine each room and the exterior walls of the building for means of rodent egress and seal.  If doors do not seal at the bottom, install a weather strip as a barrier to rodents.  Reduce harborages (cardboard boxes) where rodents may reside (MDFA, 1996).

- All cleaning products used at the facility should be approved by the school department with MSDS’ available at a central location.  Consider providing staff with school department issued cleaners.

- Refrain from using plug-in air fresheners or other air deodorizers.

- Relocate or consider reducing the amount of materials stored in classrooms to allow for more thorough cleaning of classrooms.  Clean items regularly with a wet cloth or sponge to prevent excessive dust build-up.

- Consider adopting the US EPA (2000) document, “Tools for Schools”, as an instrument for maintaining a good indoor air quality environment in the building.  This document is available at: http://www.epa.gov/iaq/schools/index.html.

- Refer to resource manual and other related indoor air quality documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings.  These documents are available at: http://mass.gov/dph/iaq.

# References

ACGIH.  1989.  Guidelines for the Assessment of Bioaerosols in the Indoor Environment.  American Conference of Governmental Industrial Hygienists, Cincinnati, OH.

ASHRAE.  1989.  Ventilation for Acceptable Indoor Air Quality.  American Society of Heating, Refrigeration and Air Conditioning Engineers. ANSI/ASHRAE 62-1989

B4 Brands by AMA.  2006.  Avant OriginalTM Instant Hand Sanitizer Materials Safety Data Sheet.  B4 Brands by AMA., Nixa, MO.

BETCO Corporation.  2007.  Clario Foaming Alcohol Instant Hand Sanitizer Material Safety Data Sheet.  BETCO Corporation, Toledo, OH.

Birchwood Laboratories, Inc.  2007.  Hand Wipe Take Alongs Materials Safety Data Sheet.  Birchwood Laboratories, Inc., Eden Prairie, MN.

BOCA.  1993.  The BOCA National Mechanical Code/1993.  8th ed.  Building Officials and Code Administrators International, Inc., Country Club Hill, IL.

FEMA.  Unknown.  Protecting Your Business From Wind. Federal Emergency Management Agency, Washington, DC.  http://www.fema.gov/pdf/plan/prevent/howto/how2027.pdf

Georgia-Pacific Consumer Products.  2007.  Cormatic® High Capacity Instant Hand sanitizer Material Safety Data Sheet.  Georgia- Pacific Consumer Products, Atlanta, GA.

MDFA.  1996.  Integrated Pest Management Kit for Building Managers.  Massachusetts Department of Food and Agriculture, Pesticide Bureau, Boston, MA.

MDPH.  1997.  Requirements to Maintain Air Quality in Indoor Skating Rinks (State Sanitary Code, Chapter XI).  105 CMR 675.000.  Massachusetts Department of Public Health, Boston, MA.

MDPH.  2009a.  Indoor Air Quality Assessment.  Georgetown Senior/Middle School, Georgetown, MA.  Massachusetts Department of Public Health, Bureau of Environmental Health Assessment, Boston, MA.  August 2009.

MDPH.  2009b.  Public Health Fact Sheet H1N1 Flu (Swine Flu).  Massachusetts Department of Public Health, Boston, MA.  http://www.mass.gov/Eeohhs2/docs/dph/cdc/factsheets/swine_flu.pdf

NIH.  2006.  Chemical in Many Air Fresheners May Reduce Lung Function.  NIH News.  National Institute of Health.  July 27, 2006.  http://www.nih.gov/news/pr/jul2006/niehs-27.htm

OSHA.  1997.  Limits for Air Contaminants.  Occupational Safety and Health Administration.  Code of Federal Regulations.  29 C.F.R 1910.1000 Table Z-1-A.

Sanford.  1999.  Material Safety Data Sheet (MSDS No: 198-17).  Expo Dry Erase Markers Bullet, Chisel, and Ultra Fine Tip.  Sanford Corporation.  Bellwood, IL.

SBBRS.  1997.  Mechanical Ventilation.  State Board of Building Regulations and Standards.  Code of Massachusetts Regulations.  780 CMR 1209.0

SMACNA.  1994.  HVAC Systems Commissioning Manual.  1st ed.  Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

US EPA.  1992.  Indoor Biological Pollutants.  US Environmental Protection Agency, Environmental Criteria and Assessment Office, Office of Health and Environmental Assessment, research Triangle Park, NC.  EPA 600/8-91/202 January 1992.

US EPA.  2000.  Tools for Schools.  Office of Air and Radiation, Office of Radiation and Indoor Air, Indoor Environments Division (6609J). EPA 402-K-95-001, Second Edition.  http://www.epa.gov/iaq/schools/tools4s2.html.

US EPA.  2001.  “Mold Remediation in Schools and Commercial Buildings”.  Office of Air and Radiation, Indoor Environments Division, Washington, DC.  EPA 402-K-01-001.  March 2001.  Available at: http://www.epa.gov/iaq/molds/mold_remediation.html.

US EPA.  2006.  National Ambient Air Quality Standards (NAAQS).  US Environmental Protection Agency, Office of Air Quality Planning and Standards, Washington, DC.  http://www.epa.gov/air/criteria.html.

Zwayer, G.L.  2007.  Exterior Insulation and Finish System (EIFS).  National Institute of Building Sciences, Washington, DC.  http://www.wbdg.org/design/env_wall_eifs.php

Figure 1

Configuration of an EIFS Wall Panel

(FEMA, Unknown)

Picture 1

Asymmetrical Pattern in Exterior Wall System, Which May Indicate Moisture Attempting to Pass/Evaporate Through the Material

Picture 2

Pipe That Drains Water From Band Room Roof

Picture 3

Pipe That Drains Water From Band Room Roof, Note Damage to Exterior Wall

Picture 4

Lack of Back Wrap or Flashing on EIFS Edge

| Location/ Room | Occupants in Room | Temp (°F) | Relative Humidity (%) | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | PM2.5 (µg/m3) | Windows Openable | Ventilation |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| background |  | 50 | 26 | 387 | ND | 8 |  |  |  |  |
| 3150 | 0 | 71 | 28 | 727 | ND | 10 | Y | Y | Y | DO, Clutter ,Cleaners |
| 3180/media | 80 | 72 | 32 | 1212 | ND | 12 | Y | Y | Y | PF |
| 3210 | 1 | 72 | 25 | 695 | ND | 8 | Y | Y | Y | Fresh air supply blocked, PF, DO, Bowing CT |
| 3220 | 0 | 78 | 24 | 580 | ND | 10 | Y | Y | Y | PF |
| 3240 | 25 | 75 | 28 | 1553 | ND | 9 | Y | Y | Y | DO, DEM |
| 3250 | 14 | 73 | 25 | 908 | ND | 10 | Y | Y | Y | DEM, Cleaners, 3 WD CT |
| 3070 | 29 | 71 | 35 | 1592 | ND | 6 | N | Y | Y | DEM, Pencil shavings, Wall mounted air-conditioning unit |
| 3060 office | 2 | 73 | 26 | 1020 | ND | 6 | N | N | N | DO |
| 3080 | 20 | 72 | 33 | 1669 | ND | 7 | Y | Yes | Yes | Exhaust vent blocked, Broken window, PF, Cleaners, DO |
| 3100 | 22 | 73 | 27 | 837 | ND | 12 | Yes | Yes | Yes | Exhaust vent blocked, DO |
| 3110 | 0 | 72 | 26 | 734 | ND | 5 | Yes | Yes | Yes | 3 WD CT, Cleaners |
| 3130 | 1 | 71 | 29 | 886 | ND | 9 | Yes | Yes | Yes |  |
| 3260 | 0 | 70 | 25 | 728 | ND | 7 | Yes | Yes | Yes | DEM, PF |
| 3270 | 2 | 71 | 28 | 839 | ND | 7 | Yes | Yes | Yes | Air deodorizer |
| Band Director’s office | 1 | 71 | 26 | 734 | ND | 8 | Yes | No | No | DO |
| Band room | 5 | 69 | 28 | 824 | ND | 6 | No | Yes | Yes | DO, WD carpet, WD instrument cases |
| Band practice room 3 | 0 | 65 | 25 | 802 | ND | 13 | No | Yes | No | 3 WD CT, Bowing CT, DO |
| Band practice room 2 | 0 | 66 | 32 | 588 | ND | 9 | Yes | Yes | No | Leak, DO, Food containers |
| Band practice room 1 | 0 | 66 | 30 | 530 | ND | 10 | Yes | Yes | No | DO |
| 2210 | 3 | 73 | 25 | 768 | ND | 9 | Yes | Yes | Yes | Exhaust vent off, DO, DEM |
| 2190 | 14 | 73 | 27 | 760 | ND | 14 | Yes open | Yes | Yes | Broken window, DEM, PF, Orange odor |
| 2170 | 18 | 73 | 27 | 998 | ND | 9 | Yes | Yes | Yes | Strong perfume odor, Cleaners, DEM |
| 2150 | 15 | 72 | 26 | 786 | ND | 11 | Yes | Yes | Yes | DEM, DO, Cleaners, Hand sanitizer odor |
| 2140 | 13 | 73 | 27 | 831 | ND | 11 | Yes | Yes | Yes | DEM |
| 2100 | 13 | 73 | 27 | 760 | ND | 7 | Yes | Yes | Yes | DO, PF, DEM |
| 2090 | 18 | 72 | 26 | 810 | ND | 8 | Yes | Yes | Yes | DEM |
| 2070 | 22 | 74 | 31 | 1397 | ND | 11 | Yes | No? | Yes | PF, Dusty PF blades, Cleaners, Wall mounted air conditioner |
| 2060 | 2 | 73 | 23 | 515 | ND | 6 | No | No | Yes | 22 computers, Wall mounted air conditioner |
| 2040 | 21 | 75 | 26 | 793 | ND | 12 | Yes Open | Yes | No? | PF, Cleaners, DEM |
| 2030 | 9 | 76 | 25 | 774 | ND | 11 | Yes Open | Yes | Yes | Cleaners |
| 2010 | 13 | 75 | 26 | 930 | ND | 12 | Yes | Yes | Yes | DEM, Cleaner |
| Cafeteria | 120 | 68 | 31 | 686 | ND | 13 | Yes | Yes | Yes | DO, 2 WD CT |
| 1330 | 24 | 72 | 29 | 709 | ND | 10 | No | Yes | Yes |  |
| 1331 storage | 0 | 75 | 29 | 849 | ND | 9 | No | No | Yes | Washer and dryer |
| 1190 | 14 | 71 | 30 | 942 | ND | 11 | Yes | Yes | Yes | DEM, DO, Burnt out motor |
| 1170 | 17 | 71 | 29 | 735 | ND | 28 | Yes | Yes | Yes | Clay |
| 1172 kiln room |  |  |  |  |  | 38 | No | No | Yes | Exhaust vent not ducted, kiln operating |
| 1171 art office | 0 | 70 | 31 | 924 | ND | 39 | No | Yes | No | Missing CT |
| Auditorium | 50 | 68 | 30 | 422 | ND | 8 | No | Yes | Yes |  |
| Gymnasium | 80 | 67 | 37 | 943 | ND | 9 | No | Yes | Yes |  |
| 1320 | 21 | 71 | 28 | 769 | ND | 11 | No | Yes | Yes | DEM |
| 1270 | 22 | 71 | 33 | 1113 | ND | 10 | No | Yes | Yes | Chalk dust, Terrarium, DO |
| 1250 | 18 | 71 | 31 | 910 | ND | 14 | No | Yes | Yes | Plants, DEM, Terrarium, DO |
| Girls locker room | 0 | 65 | 32 | 605 | ND | 10 | No | Yes | Yes | Strong perfume/cologne odor, Fresh air supply off, Exhaust vent off |
| Main office | 3 | 67 | 33 | 630 | ND | 9 | Yes | Yes | No | Air-conditioner |
| 1014 Staff room | 0 | 70 | 31 | 690 | ND | 10 | No | Yes | No | DO, Air-conditioner |
| 1011 | 0 | 70 | 29 | 619 | ND | 8 | Yes | Yes | No | DO, Air-conditioner |
| 1012 | 1 | 70 | 29 | 598 | ND | 8 | Yes | Yes | Yes | DO, Air-conditioner |
| Guidance Director | 0 | 70 | 28 | 614 | ND | 9 | Yes | Yes | Yes | DO, Air-conditioner |
| Guidance | 0 | 71 | 27 | 679 | ND | 9 | Yes | Yes? | Yes | 9 WD CT, Air-conditioner, DO |
| 1031 | 2 | 72 | 27 | 898 | ND | 2 | Yes | Yes | Yes | Fresh air supply off, Exhaust vent off, Air-conditioner |
| 3290 | 23 | 72 | 34 | 1199 | ND | 6 | Yes | Yes | Yes | DO |
| 3050 | 1 | 74 | 27 | 737 | ND | 2 | Yes | Yes | Yes | 2 WD CT, DO |
| 3040 | 0 | 73 | 27 | 733 | ND | 2 | Yes | Yes | Yes | 3 WD CT |
| 3090 | 23 | 72 | 31 | 861 | ND | 7 | Yes Open | Yes | Yes | Exhaust vent off, 2 WD CT, DO |
| 3140 | 21 | 71 | 29 | 737 | ND | 5 | No | Yes | Yes | DEM, DO |
| 3160 | 1 | 73 | 27 | 677 | ND | 6 | No | Yes | Yes | DO |
| 3120 | 16 | 72 | 29 | 800 | ND | 7 | No |  |  | TB, DEM, 2 WD CT |
| 3280 | 25 | 72 | 31 | 936 | ND | 7 | Yes Open | Yes | Yes | supply off, DO |
| 2250 | 12 | 69 | 36 | 729 | ND | 4 | Yes | Yes | Yes | DEM |
| 2260 | 21 | 72 | 35 | 1367 | ND | 5 | Yes | Yes | Yes | Exhaust vent blocked |
| Media Center | 12 | 72 | 29 | 876 | ND | 4 | Yes | Yes | Yes |  |
| 2161 | 17 | 71 | 35 | 1441 | ND | 2 | No | Yes |  | 24 computers, 2 WD CT, DO |
| 2130 | 21 | 72 | 30 | 605 | ND | 4 | No | Yes | Yes | DEM |
| Teachers room | 3 | 73 | 28 | 566 | ND | 5 | Yes | Yes | Yes | Copier, Soda vending machine |
| 1110 | 13 | 74 | 28 | 632 | ND | 1 | No | Yes | Yes | 24 computers |
| 1290 | 3 | 71 | 30 | 487 | ND | 9 | No | No | No | DEM, DO |
| 1240 | 13 | 74 | 30 | 456 | ND | 7 | No | No | No | DEM, 20 computers |
| Darkroom | 2 | 74 | 31 | 632 | ND | 6 | No | No | Yes | Exhaust located at center of room |
| Wood shop | 6 | 73 | 28 | 518 | ND | 7 | No | No | Yes |  |
| 1152 | 21 | 73 | 29 | 837 | ND | 11 | No | Yes | Yes | 24 computers |
| Boys locker room | 0 | 65 | 34 | 443 | ND | 10 | No | Yes | Yes | Cologne odor |

| Location/ Room | Carbon Dioxide (ppm) 2008 | Carbon Dioxide (ppm) 2010 | Difference Carbon Dioxide (ppm) | Occupancy Level during Carbon Dioxide Sampling |
| --- | --- | --- | --- | --- |
| background | 340 | 387 | +47 |  |
| 3180/media | 1292 | 1212 | -80 | Pop 2008 = 0 Pop. 2010 = 80 |
| 1150 Wood shop | 987 | 518 | -469 | Pop 2008 = 14 Pop. 2010 = 6 |
| 1152 | 1149 | 837 | -312 | Pop 2008 = 0 Pop. 2010 = 21 |
| 1170 | 1101 | 735 | -366 | Pop 2008 = 1 Pop. 2010 = 17 |
| 1190 | 1304 | 942 | -362 | Pop 2008 = 17 Pop. 2010 = 14 |
| 1240 | 1395 | 456 | -939 | Pop 2008 = 20 Pop. 2010 = 13 |
| 1250 | 1299 | 910 | -389 | Pop 2008 = 19 Pop. 2010 = 18 |
| 1270 | 1766 | 1113 | -653 | Pop 2008 = 1 Pop. 2010 = 22 |
| 1290 | 1421 | 487 | -934 | Pop 2008 = 6 Pop. 2010 = 3 |
| 1320 | 1006 | 769 | -237 | Pop 2008 = 18 Pop. 2010 = 21 |
| 1330 | 871 | 709 | -162 | Pop 2008 = 3 Pop. 2010 = 24 |
| 1331 storage | 1120 | 849 | -271 | Pop 2008 = 0 Pop. 2010 = 0 |
| 2010 | 2942 | 930 | -2012 | Pop 2008 = 34 Pop. 2010 = 13 |
| 2030 | 3238 | 774 | -2464 | Pop 2008 = 24 Pop. 2010 = 9 |
| 2040 | 1998 | 793 | -1205 | Pop 2008 = 18 Pop. 2010 = 21 |
| 2060 | 2675 | 515 | -2160 | Pop 2008 = 18 Pop. 2010 = 2 |
| 2070 | 3080 | 1397 | -1683 | Pop 2008 = 27 Pop. 2010 = 22 |
| 2090 | 1703 | 810 | -893 | Pop 2008 = 23 Pop. 2010 = 18 |
| 2100 | 2776 | 760 | -2016 | Pop 2008 = 28 Pop. 2010 = 13 |
| 2130 | 2723 | 605 | -2118 | Pop 2008 = 24 Pop. 2010 = 21 |
| 2140 | 1578 | 831 | -747 | Pop 2008 = 31 Pop. 2010 = 13 |
| 2150 | 1075 | 786 | -289 | Pop 2008 = 3 Pop. 2010 = 152 |
| 2170 | 1015 | 998 | -17 | Pop 2008 = 0 Pop. 2010 = 18 |
| 2210 | 1627 | 768 | -859 | Pop 2008 = 13 Pop. 2010 = 3 |
| 2250 | 1016 | 729 | -287 | Pop 2008 = 19 Pop. 2010 = 12 |
| 3070 | 1526 | 1592 | +66 | Pop 2008 = 1 Pop. 2010 = 29 |
| 3080 | 2052 | 1669 | -383 | Pop 2008 = 1 Pop. 2010 = 20 |
| 3090 | 1186 | 861 | -325 | Pop 2008 = 3 Pop. 2010 = 23 |
| 3100 | 930 | 837 | -93 | Pop 2008 = 2 Pop. 2010 = 22 |
| 3110 | 1314 | 734 | -580 | Pop 2008 = 1 Pop. 2010 = 0 |
| 3120 | 1749 | 800 | -949 | Pop 2008 = 0 Pop. 2010 = 16 |
| 3130 | 1990 | 886 | -1104 | Pop 2008 = 25 Pop. 2010 = 1 |
| 3140 | 1484 | 737 | -747 | Pop 2008 = 0 Pop. 2010 = 21 |
| 3150 | 1059 | 727 | -332 | Pop 2008 = 0 Pop. 2010 = 0 |
| 3160 | 1232 | 677 | -555 | Pop 2008 = 31 Pop. 2010 = 1 |
| 3210 | 1642 | 695 | -947 | Pop 2008 = 30 Pop. 2010 = 1 |
| 3220 | 1192 | 580 | -612 | Pop 2008 = 1 Pop. 2010 = 0 |
| 3240 | 2265 | 1553 | -712 | Pop 2008 = 1 Pop. 2010 = 251 |
| 3250 | 2761 | 904 | -1857 | Pop 2008 = 24 Pop. 2010 = 14 |
| 3260 | 2391 | 728 | -1663 | Pop 2008 = 30 Pop. 2010 = 0 |
| 3270 | 840 | 839 | -1 | Pop 2008 = 1 Pop. 2010 = 2 |
| 3280 | 1209 | 936 | -273 | Pop 2008 = 0 Pop. 2010 = 25 |
| 3290 | 1476 | 1199 | -277 | Pop 2008 = 20 Pop. 2010 = 23 |
| Auditorium | 673 | 422 | -251 | Pop 2008 = 40+ Pop. 2010 = 50 |
| Band Room | 653 | 824 | +171 | Pop 2008 = 0 Pop. 2010 = 5 |
| Dark Room | 1419 | 632 | -787 | Pop 2008 = 0 Pop. 2010 = 2 |
| Library/ Media Center | 1440 | 876 | -564 | Pop 2008 = 7 Pop. 2010 = 12 |
| Main Gym | 968 | 943 | -25 | Pop 2008 = 0 Pop. 2010 = 80 |