## Master GFCIUnwantedTrippingRepo
Date | Name (First) | Name (Last) | Electrician's License Number | Address (Address) | Address (Address2) | Address (City) | Address (State) | Address (Zip) | Telephone | Role/Title | Email | GFCI Manufacturer Part/Model Number | GFCI Type | Other (Type) | Select Amperage of GFCI | Other (Amperage) | Select Poles of GFCI | Select the Manufacturer/Brand Name of GFCI | Please select location type: | Image | Date of Occurrence | Date of Installation | Installation Location (if different) (Address) | Installation Location (if different) (Address2) | Installation Location (if different) (City) | Installation Location (if different) (State) | Installation Location (if different) (Zip) | Describe the Tripping Incident | Equipment Manufacturer Name | Equipment Model Number | Other Equipment on the circuit | Residence Type | Please describe room(s) affected by trip | Have you contacted the GFCI manufacturer? | If no, would you like to be contacted by them? | Have you contacted the Equipment manufacturer? | Did the equipment manufacturer provide any recommendations? | Attach pictures of the installation and equipment nameplates. | Signature
2023-02-15 07:25 | Chris | Vining |  | 5 longwood ave |  | NORTH ANDOVER | MA | 01845-5217 | 17818447889 | electrician |  | siemens | Breaker | circuit breaker | 20 |  | 1 Pole | Siemens | Residence |  | 2023-01-13 | 2023-01-06 | 198 dale street |  | NORTH ANDOVER | MA | 01845-5217 | tripped overnight. | refrigerator | type ko-kbm36us | kitchen counter outlets nothing plugged in at the time of trip | single family | kitchen | No | Yes | No | No
2023-02-16 09:15 | Raymond | Wyman |  | 161 Mechanic Street | Building 5103 | Bellingham | MA | 2019 | 978-235-0161 | Construction Superintendent |  | QF240A | Breaker | L2202122641 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | Oven trips GFCI during preheat. | General Electric | JB645RK8SS | None | Apartment | Kitchen | No | No | Yes | Yes
2023-02-16 09:21 | Raymond | Wyman |  | 161 Mechanic Street | Building 5101 | Bellingham | MA | 2019 | 978-235-0161 | Construction Superintendent |  | QF240A | Breaker | M2202210445 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | Oven trips GFCI during preheat. | General Electric | JB645RK8SS | NONE | Apartment | Kitchen | No | No | Yes | Yes
2023-02-16 09:27 | Raymond | Wyman |  | 161 Mechanic Street | Building 5102 | Bellingham | MA | 2019 | 978-235-0161 | Construction Superintendent |  | QF240A | Breaker | L2202122642 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 09:31 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5104 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122586 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 09:35 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5105 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M2202150139 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 09:39 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5107 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150384 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 09:42 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5108 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M2202150140 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 09:47 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5109 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122585 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 09:51 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5110 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202141724 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-23 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 09:56 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5111 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M2202150141 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:06 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5112 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122584 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:11 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5113 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202210540 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITHCEN | No | No | Yes | Yes
2023-02-16 11:15 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5201 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202201167 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:18 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5202 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202210541 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:21 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5203 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202210539 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:25 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5205 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150527 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:29 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5206 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150496 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:32 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5207 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150525 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:36 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5208 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150528 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:39 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5209 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2292159526 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:42 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5210 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202111132 | 40 |  | 3 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:44 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5211 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150522 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:47 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5212 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150385 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:49 | Raymond | Wyman |  | 161 Mechanic Street | BULDING 5213 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTON SUPERINTENDENT |  | QF240A | Breaker | L2292150524 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 11:59 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5301 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202210548 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 12:02 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5302 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122625 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | J645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 12:05 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5303 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202210547 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 12:08 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5304 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150495 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 13:00 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5305 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M2202150159 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 13:04 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5306 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | JB645RK8SS | Breaker | M2202210446 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 13:09 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5307 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122626 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN¦ | No | No | Yes | Yes
2023-02-16 13:13 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5308 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202141719 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 13:16 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5309 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202141720 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 13:18 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5310 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122627 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 13:21 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5311 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202141717 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN¦ | No | No | Yes | Yes
2023-02-16 13:24 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5312 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202141718 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 13:26 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5313 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150497 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 13:30 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5401 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202182083 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN¦ | No | No | Yes | Yes
2023-02-16 13:32 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5402 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202210549 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN¦ | No | No | Yes | Yes
2023-02-16 13:36 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5403 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122658 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 13:38 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5404 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M2202150138 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-16 13:46 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5406 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202102400 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-14 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-17 09:04 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5413 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M2202101815 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-16 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-17 09:07 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5408 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150379 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-16 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-17 09:10 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5409 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122581 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-16 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-17 09:14 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5410 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150380 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-16 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-17 09:17 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5411 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122583 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-16 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-17 09:19 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 5412 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150523 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-16 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK8SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 09:37 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1401 | Bellingham | MA | 2019 | 9782350161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150488 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-17 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 09:42 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1402 | Bellingham | MA | 2019 | 9782350161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | NONE | 40 | L2202150454 | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-17 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 09:46 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1403 | Bellingham | MA | 2019 | 9782350161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122622 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-17 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 09:50 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1404 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202141506 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-17 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 09:53 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1406 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202141502 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-17 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT. | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 09:57 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1408 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202141505 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-17 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:00 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1409 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L220214503 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-17 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:09 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1410 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202141510 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-17 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:13 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1411 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202141509 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-17 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:16 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1412 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M2202150107 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-17 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:19 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1413 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202141504 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-17 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:24 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1301 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122612 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-17 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:27 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1302 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122616 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:30 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1303 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122614 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:36 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1305 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122623 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PRHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:39 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1306 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122613 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:42 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1308 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202271007 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:45 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1309 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122603 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:48 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1310 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202261970 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 10:51 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1311 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202270975 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:01 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1313 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202271010 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:11 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1201 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202280444 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:13 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1202 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202271005 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DUIRNG PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:15 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1203 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M2202270657 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:18 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1204 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202280445 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:20 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1205 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150498 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:22 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1206 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M220212447 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:25 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1207 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M220212446 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:27 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1208 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M2202121450 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:29 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1209 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150485 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:32 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1210 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDNT |  | QF240A | Breaker | L2202150486 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:34 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1211 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L220215081 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:36 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1212 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150484 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:38 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1213 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150387 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:41 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1101 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150506 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:43 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1102 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M2202121458 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:46 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1103 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122638 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:48 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1104 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150505 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DUIRNG PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:50 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1105 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150474 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:52 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1108 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M2202121461 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:55 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1109 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | M2202121460 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 11:57 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1110 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202122637 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 13:10 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1111 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202150507 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 13:12 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1112 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202210900 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-21 13:15 | Raymond | Wyman |  | 161 Mechanic Street | BUILDING 1113 | Bellingham | MA | 2019 | 978-235-0161 | CONSTRUCTION SUPERINTENDENT |  | QF240A | Breaker | L2202210901 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-02-06 | 2023-02-20 | [5 empty] | OVEN TRIPS GFCI DURING PREHEAT | GENERAL ELECTRIC | JB645RK9SS | NONE | APARTMENT | KITCHEN | No | No | Yes | Yes
2023-02-22 12:28 | Alexandro | Gonzalz |  | 677 Winchester st | Unit 507 | Newton | MA | 2459 | 857-544-7090 | VP/ MAster Electrician |  | Eaton GFTCB240 | Breaker | Eaton GFTCB240 | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/14227134942 | 2023-02-02 | 2023-02-07 | [5 empty] | This is a Multi Unit Building consisting of 142 apartments. Client on numerous occasions has called about GFCI breaker tripping while she's cooking ¦Actions Taken: ¦Test and inspect factory supplied cord for damage or irregularities, Inspect range (ground jumper) for irregularities - tighten anything if needed, Open surface-mounted outlet, pull cover off, remove compression screw terminals, Remove conductors from breaker - neutral, ground and 2 current carrying conductors, Megger test conductors from panel to range outlet and megger test factory cord. Record values/ findings and Re-Torque breaker/ Range terminals/ and surface mounted outlet to manufacturers recommended specification. ¦ | GE | JBS460DMWW | No | GE | Only Kitchen Range | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/14227134955
2023-02-28 12:30 | Jenna | Zadek |  | 12 Kylie lane |  | Natick | MA | 1760 | 410-446-3376 | Homeowner |  | 722013980 | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-01-19 | 2023-01-19 | [5 empty] | Breaker holds when stove is not plugged in. When the stove is plugged in, the unit immediately trips. Technician checked the voltage to the ground, continuing across all 4 wires, and then plugged in the stove. The unit works fine on a regular breaker, but trips on GFUI breaker. The technician replaced GFI with a second one and it continues to immediately trip. | Bertazzoni | MAST365INMXE |  | Single family home | Stove in kitchen only. | No | Yes | Yes | No
2023-03-02 13:35 | Daniel | Hanlon |  | 75 GETCHELL WAY |  | CANTON | MA | 2021 | 6178397839 | Project Manager |  | BFGA2 | Breaker | BAFH2 | 20 |  | 1 Pole | Siemens | Commercial |  | 2023-01-11 | 2022-07-15 | [5 empty] | Dual GFCI/AFCI circuit breaker serving the apartment's refrigerator repeatedly trips within a day or two after being turned on. | Bosch | B091B91NSP |  | Studio apartment | Unit 407. The refrigerator in the kitchen repeatedly trips. | Yes | No | Yes | No
2023-03-02 14:12 | Daniel | Hanlon |  | 1260 Boylston Street |  | Boston | MA | 2215 | 6178397839 | Project Manager |  | BFGA2 | Breaker | BAFH2 | 20 |  | 1 Pole | Siemens | Commercial |  | 2023-01-12 | 2022-07-13 | [5 empty] | Dual GFCI/AFCI circuit breaker serving the apartment's refrigerator repeatedly trips within a day or two after being turned on. | Bosch | B091BP1NSP |  | Studio Apartment | Unit 417. Refrigerator in Kitchen | Yes | No | Yes | No
2023-03-02 14:16 | Daniel | Hanlon |  | 1260 Boylston Street |  | Boston | MA | 2215 | 6178397839 | Project Manager |  | BFGA2 | Breaker | BAFH2 | 20 |  | 1 Pole | Siemens | Commercial |  | 2023-02-01 | 2022-07-13 | [5 empty] | Dual GFCI/AFCI circuit breaker serving the apartment's refrigerator repeatedly trips within a day or two after being turned on. | Bosch | B091B91NSP |  | Studio Apartment | Unit 421 Refrigerator | Yes | No | Yes | No
2023-03-02 14:21 | Daniel | Hanlon |  | 1260 Boylston Street |  | Boston | MA | 2215 | 6178397839 | Project Manager |  | BFGA2 | Breaker | BAFH2 | 20 |  | 1 Pole | Siemens | Commercial |  | 2023-02-01 | 2022-07-13 | [5 empty] | Dual GFCI/AFCI circuit breaker serving the apartment's refrigerator repeatedly trips within a day or two after being turned on. | Bosch | B091B91NSP |  | Studio Apartment | Unit 430. Refrigerator | Yes | No | Yes | No
2023-03-02 14:28 | Daniel | Hanlon |  | 1260 Boylston Street |  | Boston | MA | 2215 | 6178397839 | Project Manager |  | BFGA2 | Breaker | BAFH2 | 20 |  | 1 Pole | Siemens | Residence |  | 2023-02-24 | 2022-07-13 | [5 empty] | Dual GFCI/AFCI circuit breaker serving the apartment's refrigerator repeatedly trips within a day or two after being turned on. | Bosch | B091B91NSP |  | Studio Apartment | Unit 435. Refrigerator | Yes | No | Yes | No
2023-03-21 10:48 | Brandon | Hill |  | 45 Petronelli Way |  | Brockton | MA | 2301 | 4012567684 | Project Manager |  | Siemens QPF | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/14362502414 | 2023-02-28 | 2023-03-20 | [5 empty] | This is a Multi Unit Building consisting of 111 apartments. The Building Manager has called multiple times to the General Contractor¦¦Actions Taken: ¦We tested all GE Electric Ranges. We looked for obvious signs, Megger tested all cords and branch circuits for the ranges. We made sure that the Grounds and Neutrals were not touching. The problem still existed. We called the manufacture for ideas to rectify the issue but still no results. Therefor, we replaced all the breakers to a standard 50A 2 Pole breaker. ¦¦Unit Numbers:¦109¦110¦112¦113¦114¦115¦116¦117¦118¦119¦120¦121¦122¦123¦124¦201¦202¦203¦204¦205¦208¦209¦210¦211¦212¦213¦214¦215¦216¦217¦218¦219¦220¦221¦222¦223¦224¦301¦302¦303¦304¦305¦306¦307¦308¦309¦311¦312¦313¦314¦315¦316¦317¦318¦319¦320¦321¦322¦323¦324¦325¦401¦402¦403¦404¦405¦406¦407¦408¦409¦411¦412¦414¦415¦416¦417¦418¦419¦420¦421¦422¦423¦424¦425¦501¦502¦503¦504¦505¦506¦507¦508¦509¦510¦511¦512¦513¦514¦515¦516¦517¦518¦519¦520¦521¦ | GE | JB655SKASS |  | Apartment | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14362502426
2023-03-24 08:25 | Bryan | Culliton |  | 150 | Pittsfield Road | Lenox | MA | 1240 | 4132071566 | Project Manager |  | Eaton GFTCB250CS | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-01-27 | 2023-01-27 | 910 South Main Street (Windrush Commons) |  | Great Barrington | MA | 1230 | The oven was turned on and then burners were turned on one at a time until the GFCI breaker popped. The breaker would pop somewhere between one and four burners running simultaneously. | GE | JB256DMWW Electric Range |  | Multi family, subsidized housing | All 36 units that were required to have GFCI breakers. ¦¦¦The following units did not require GFCI breakers b/c of the distance of receptacle to edge of sink: 1, 2, 3, 4, 17, 18, 19, 20, 21, 38, 39, 40 & 41. | Yes | No | Yes | No
2023-03-27 08:21 | Tyler | Daniels |  | 944 Salem St |  | Groveland | MA | 1834 | 978-815-0779 | Manager |  | QF250AP Type QPF GFCI | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/14390536600 | 2023-03-03 | 2023-02-24 | 31 Woodcock Ave, Unit 9 |  | Haverhill | MA | 1832 | Oven trips during preheat cycle. | Whirpool | WFC315s0JS1 |  | Apartment | Kitchen oven only | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/14390536613
2023-03-29 14:22 | David | Cooper |  | 80 Hampshire St |  | Metheun | MA | 1844 | 9783877467 | Electrician |  | Seimans S-A QF250A GFCI Breaker | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-03-27 | 2023-03-27 | 23 Ruane Rd |  | Newton | MA |  | Installed 1 2pole 50 AMP GFCI breaker on Wolf Range. As soon as range plugs in it trips GFCI breaker automatically¦¦Everything rung out clear with mete | Wolf Range | IR36550/S/T |  | Single family house | Tripping was only to electric range in Kitchen | Yes | No | Yes | No
2023-04-05 12:47 | Donal | McNulty |  | 51 Main St |  | Norwell | MA | 2061 | 6172934525 | Master Electrician |  | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence |  | 2023-04-05 | 2023-02-05 | 1005 Broadway |  | Chelsea | MA | 2150 | This is a multi-family residential building consisting of 38 units. Of the 38 units, 34 are furnished with a brand new GE JB645DK range wired to a GFCI equipped Eaton GFTCB240 breaker. ¦¦In order to test an individual appliance, the bake and/or broil function was turned on and set to some temperature between 300 and 400 degrees. At all 34 locations, the breaker tripped roughly 30 seconds into preheating, regardless of set tempurature. This result repeated itself several times at each location. ¦¦The following units are affected: 201, 202, 203, 204, 205, 206, 207, 209, 210, 211, 212, 213, 214, 301, 302, 303, 304, 305, 306, 307, 309, 310, 311, 312, 313, 314, 401, 402, 403, 404, 405, 406, 407, 408, 409, 410. | General Electric | JB645DK | None | Multifamily Apartment Building | Kitchens in units: ¦¦201, 202, 203, 204, 205, 206, 207, 209, 210, 211, 212, 213, 214, 301, 302, 303, 304, 305, 306, 307, 309, 310, 311, 312, 313, 314, 401, 402, 403, 404, 405, 406, 407, 408, 409, 410.¦ | Yes | No | Yes | Yes
2023-04-05 20:32 | Andrew | Cunha |  | 7 pine valley dr |  | Dracut | MA | 1826 | 9785964159 | President |  | Hom250gfic | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-03-30 | 2023-01-04 | 850 Washington st |  | Walpole | MA | 2081 | We wired the cord into the stove, broke the ground and neutral bonding connection, tested breaker before we got our final inspection, breaker worked as it suppose to. Homeowner then contacted me stating that the breaker would not hold anymore two months after our final. It's been happening multiple days in a row. | Cafe 30"" | Chs90xp2msl | None | Single family home. | No rooms affected, just besides customer cannot cook food. | No | No | Yes | No
2023-04-12 22:41 | Gregory | Kehlhem |  | 3 saddle hill road |  | Medway | MA | 2053 | 774-993-9697 | Electrician |  | Siemens QF250AP | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-03-27 | 2023-03-27 | 1 whites pond drive |  | Norfolk | MA | 2056 | Electric stove trips gfci breaker. The cooktop burners run fine without issue. After the oven is running for a bit it will trip at random different times. I have confirmed there is no issue with the wire, receptacle, cord whip, or breaker. | KitchenAid | Kfeg500ess3 |  | Residential kitchen | Kitchen stove | No | No | No | No | https://www.formstack.com/admin/download/file/14474935016
2023-04-18 09:18 | Bill | Harland |  | PO Box 94 |  | Littleton | MA | 01460-0094 | (978) 486-8154 | President |  | Siemens - AG7MB00L H003GN 50Q-R | Breaker | None | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/14498409836 | 2023-04-13 | 2023-04-13 | 491 Main Street |  | Acton | MA | 1720 | Replacing cook top with induction appliance, and as soon as unit is turned on, the GFCI breaker trips. Manufacturer paperwork states ""GFCI protection not recommended and will cause interruption."" | Wolf Appliance | C1365T/S | None | First Choice - Single family Dwelling | Kitchen | No | No | No | Yes | https://www.formstack.com/admin/download/file/14498409850
2023-04-18 11:09 | Tom | Walsh |  | 90 Logan Dr |  | Braintree | MA | 2184 | 781 686 7334 | Home owner |  | THQL2130FT | Breaker | NONE | 30 |  | 2 Pole | ABB | Residence |  | 2023-04-07 | 2023-04-07 | [5 empty] | The Dryer trips GFIC AS SOON AS IT IS PLUGGED IN | LG | thinQ WSEX200H*A/WSGX201H*A | none | Single family home | Only dryer affected dedicated circuit | No | No | Yes | No
2023-04-24 06:28 | Thomas | Chapman |  | 3 Breed Ave | Unit F | Woburn | MA | 1801 | 603-765-4945 | Vice President |  | GFTCB240 | Breaker | None | 40 |  | 2 Pole | Eaton | Residence |  | 2023-01-03 | 2023-01-02 | 3100 Briarwood Village: Units 3213, 3311, 3204 |  | Clinton | MA | 1510 | During preheat cycle of electric range GFCI breaker trips. Wiring has been test to confirm no shorts or grounds exist in the electrical wiring from load center to electric range receptacle located in Kitchens. | GE | JB655SKSS | Nothing | Kitchen | Circuit only serves electric range located in the Kitchen. | Yes | No | Yes | No
2023-04-26 11:17 | Diversified Funding INC | Rob Damiano |  | 78 Parker St | UNIT F | Acton | MA | 1720 | 6177196707 | manager |  | EATON | Breaker | EATON | 50 |  | 2 Pole | Eaton | Residence |  | 2023-04-13 | 2023-02-14 | [5 empty] | Continuous tripping on GFCI feeing range receptacle | Hot Point | RAS 200 DMWW |  | apartment | kitchen stove | No | No | No | No
2023-05-02 11:04 | David | Hamner |  | 187 Longfellow Rd |  | Waltham | MA | 2453 | 6172937185 | Electrician |  | GFTCB230 | Breaker | GFI | 30 |  | 2 Pole | Eaton | Residence |  | 2023-02-15 | 2023-01-15 | 260 Weston Rd |  | Wellesley | MA | 2482 | Dryer keeps tripping at the same spot everytime when heats up. Appliance guy came out and said breaker needs to be changed to a 22 amp. I ordered it and it will not be here for a bit. I will need to put a regular 30 amp breaker in for time being | Electrolux Dryer | ELFE7637BT | Only dryer on this circuit | Single family home | Laundry Room Dryer Circuit | No | Yes | Yes | Yes
2023-05-02 12:29 | Thomas | Chapman |  | 3 Breed Ave | Unit F | Woburn | MA | 1801 | 6037654945 | Vice President |  | Eaton BR240 | Breaker | NO | 40 | NONE | 2 Pole | Eaton | Residence |  | 2023-05-02 | 2023-05-03 | 3100 Briarwood Village |  | Clinton | MA | 1510 | Condo community new development. Reviewed wiring for shorts/ground faults none found. The following units have been replaced with standard type breaker. 3101, 3102, 3103, 3104, 3105, 3106, 3107, 3108, 3109, 3110, 3111, 3112, 3113, 3114, 3201, 3202, 3203, 3204, 3205, 3206, 3207, 3208, 3209, 3210, 3211, 3212, 3213, 3214, 3301, 3302, 3303, 3304, 3305, 3306, 3307, 3308, 3309, 3310, 3311, 3312, 3313, 3314. Total of (42) units.¦ | GE | JB655SKSS | NONE | CONDO | Kitchen | Yes | No | Yes | No
2023-05-02 14:29 | Corey | Watson |  | P.O Box 34 |  | Mendon | MA | 1756 | 7745739636 | Electrician |  | Cutler Hammer GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/14569154875 | 2023-04-13 | 2023-01-01 | 45 Main St |  | Milford | MA | 1757 | A.S Jones installed 2 pole 50-amp GFCI Breakers GFTCB250's for 37 residential units at 45 Main Street Milford Massachusetts. These provided power to UL Listed 30"" GE free standing range Model #JB645RKSS. Once powered, A.S. Jones tested each range and found that the range and the GFCI breakers were not compatible and tripped instantly. We brought the electrical inspector, Mike Mancini, in to witness this on April 13th, 2023. He witnessed this happen in 2 of the units. The recommended solution was to install standard 2 pole 50-amp breakers in lieu of the GFCI breakers. | General Electric | JB645RKSS | None | Condo Building 37 Unit | Kitchen | Yes | No | No | No
2023-05-02 16:12 | Mark | VanMolle |  | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Owner |  | Q120DF | Breaker | Arc fault | 20 |  | 1 Pole | Siemens | Residence |  | 2023-04-26 | 2023-04-25 | [5 empty] | The Refrigerator, trips multiple times daily. | Thermador | T36FT820NS/01 |  | Kitchen | It is the Refrigerator in the Kitchen. | No | Yes | Yes | Yes
2023-05-04 11:29 | Randy | Valerio |  | 117 Central St | A-09 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | N/A | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-02-01 | 2022-08-01 | [5 empty] | Stove trips when being used. | FRIGIDAIRE | FFEF3016VSF |  | APARTMENT | KITCHEN STOVE | No | No | Yes | No
2023-05-04 11:33 | Randy | Valerio |  | 117 Central St | A-03 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-11-01 | 2022-10-01 | [5 empty] | Stove trips when being used. | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | Yes | No
2023-05-04 12:12 | Randy | Valerio |  | 117 Central St | D-05 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-02-15 | 2023-02-10 | [5 empty] | Stove tripping when being used. | Frigidaire | FFE3011LBF |  | Apartment | Kitchen | No | No | Yes | No
2023-05-04 12:14 | Randy | Valerio |  | 117 Central St | E-04 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-02-15 | 2023-02-10 | [5 empty] | Stove tripping when being used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | Yes | No
2023-05-04 12:17 | Randy | Valerio |  | 117 Central St | F-02 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-09-03 | 2022-08-15 | [5 empty] | Stove tripping when being used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | Yes | No
2023-05-04 12:19 | Randy | Valerio |  | 117 Central St | F-11 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-04-01 | 2023-02-10 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | Yes | No
2023-05-12 19:08 | Richard | Clapp |  | 534 Shunpike Rd |  | Sheffield | MA | 1257 | 413 441 4468 | Electrician |  | Cutler Hammer CH250 | Breaker | Same | 50 |  | 2 Pole | Eaton | Residence |  | 2023-05-11 | 2023-05-11 | [5 empty] | Trips when new stove plugged in | Bosch. Stove. Serial no. 020604108 | MBH H1S8055U |  | Single family home | Kitchen | No | No | No | No
2023-05-16 10:22 | Steven | Ballard |  | 191 Clyde Street |  | Chestnut Hill | MA | 2467 | 617-456-3962 | Facilities Director |  | GE | Breaker | GFCI Breaker | 20 |  | 1 Pole | ABB | Commercial |  | 2023-05-08 | 2023-05-01 | [5 empty] | Rational Oven Tipped, 2nd Floor Bakery Function Kitchen | Rational | SCCWE62G |  | Kitchen | 2nd Floor Function Kitchen | No | No | No | No
2023-05-16 10:37 | Steven | Ballard |  | 191 Clyde Street | Facilities | Brookline | MA | 2467 | 617-456-3962 | Facilities Director |  | GE THQL1120GFCI | Breaker | GFCI Breaker | 20 |  | 1 Pole | ABB | Commercial |  | 2023-05-08 | 2023-05-01 | [5 empty] | Blodgett unit tripped, 2nd floor bakery kitchen | Blodgett | HV-100G |  | Room Affected : Bakery Kitchen | Clubhouse- 2nd floor Bakery Kitchen | No | No | No | No
2023-05-16 10:45 | Steven | Ballard |  | 191 Clyde Street | The Country Club | Chestnut Hill | MA | 2467 | 617463962 | Facilities Director |  | GE - THGL1120GFCI | Breaker | GFCI Breaker | 20 |  | 1 Pole | ABB | Commercial |  | 2023-05-09 | 2023-05-01 | [5 empty] | Rational oven tripped, Clubhouse 2nd floor function kitchen | Rational | sccwe62g |  | Room affected: Clubhouse 2nd floor function kitchen | Clubhouse 2nd Floor Function Kitchen | No | No | No | No
2023-05-16 10:51 | Steve | Ballard |  | 191 Clyde Street | The Country Club | Chestnut Hill | MA | 2467 | 6174563962 | Facilities Director |  | GE - THQL1120GFCI | Breaker | GFCI Breaker | 20 |  | 1 Pole | ABB | Commercial |  | 2023-05-09 | 2023-05-01 | [5 empty] | Blodgett unit tripped, Clubhouse 2nd Floor Bakery Kitchen | Blodgett | HV-100G |  | Room affected: Clubhouse 2nd floor bakery kitchen | Clubhouse 2nd Floor Bakery Kitchen | No | No | No | No
2023-05-16 11:01 | Steven | Ballard |  | 191 Clyde Street | The Country Club | Chestnut Hill | MA | 2467 | 6174563962 | Facilities Director |  | GE THQL1120GFCI | Breaker | GFCI BREAKER | 20 |  | 1 Pole | ABB | Commercial |  | 2023-05-10 | 2023-05-01 | [5 empty] | Blodgett unit tripped | Blodgett | HV-100G |  | Room affected: Clubhouse 2nd floor bakery kitchen | Clubhouse 2nd floor bakery kitchen | No | No | No | No
2023-05-18 15:40 | edward | kaczor |  | 20 douglas ave |  | Leominster | MA | 1453 | 9788334579 | Electrician |  | THQL1120DF | Breaker | General Electric dual function breaker | 20 |  | 1 Pole | ABB | Residence |  | 2023-05-18 | 2023-05-18 | 47 Meadowbrook Rd. |  | bedfrord | MA | 1453 | The circuit breakers holds closed without the refrigerator plugged in. When you plug the refrigerator in the circuit holds for a moment until the refrigerator cycles on and the GFCI breaker trips. | Whirlpool | WRQA59CNKZ |  | Single family home | Refrigerator plug in the kitchen. | No | No | Yes | No
2023-05-18 16:53 | Edward | Kaczor |  | 20 douglas ave |  | leomisnter | MA | 1453 | 978 833 4579 | Electrican |  | THQL2130GFT | Breaker | General Electric Ground fault | 30 |  | 2 Pole | ABB | Residence |  | 2023-05-18 | 2023-05-18 | 47 Meadowbrook Rd. |  | bedfrord | MA | 1453 | The circuit breaker holds with the dryer unplugged. the breaker holds with the dryer plugged in and turned on. the GFCI breaker trips once you try and run the dryer. | LG | WKEX200HWA |  | Single family home | Laundry room dryer plug. | No | No | Yes | No
2023-05-19 08:37 | Lampasona & Bloomer Electrical Service Inc. | LaBrache |  | 1 Summer Street |  | Watertown | MA | 2472 | 6179248866 | Electrician on site |  | QF250A | Breaker | 2-pole 50 | 50 |  | 2 Pole | Siemens | Residence |  | 2023-05-18 | 2023-05-12 | 94 Saint Botolph Street |  | Boston | MA | 2116 | GFI circuit breaker would trip instantly when plugging in range. | Wolf | IR36550/S/T |  | Multi Family | Kitchen | No | Yes | Yes | Yes
2023-05-19 14:08 | Anthony | LoVuolo |  | 944 Salem St |  | Groveland | MA | 1834 | 978-373-1393 | Electrician |  | GFTCB250 | Breaker | breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-05-18 | 2023-05-18 | Pine Brook Place 33 Woodcock Unit 18 |  | Haverhill | MA | 1832 | Trips while using oven, will not heat up to temp | GE | 164D3871P008-9 |  | Apartment | Kitchen stove | No | No | No | No | https://www.formstack.com/admin/download/file/14655275875
2023-05-23 11:37 | Robert | O Mahony |  | 174 Sheri Ln, South Weymouth, MA 02190 |  | South Weymouth | MA | 2190 | 6174156345 | Master Electrician/President |  | Leviton LB250-GF | Breaker | na | 50 |  | 2 Pole | Leviton | Residence |  | 2023-05-16 | 2023-05-15 | 7 Comiskey Rd |  | Dover | MA | 2030 | Installed a 2 pole 50A GFCi breaker from Leviton on a Thermador cooktop. Turned the breaker on and it held in the on position until the power button of the cooktop was pressed. It immediatley tripped upon the pressing of the power button. | Thermador | CIT367YG | No other equipment | Single family home | Kitchen cooktop only | No | Yes | No | No
2023-05-24 13:22 | Anthony | Lovuolo |  | 944 Salem St |  | groveland | MA | 1834 | 978-373-1393 | Electrician |  | Square D/AD-910 | Breaker | N/A | 15 |  | 1 Pole | ABB | Residence |  | 2023-05-04 | 2023-05-09 | 10 School House Road Apt 1202 |  | Gloucester | MA | 1930 | The breaker for the oven would turn on for a few¦seconds and then immediately turn off. | GE Range | JB645RK6SS | None | Kitchen | Kitchen | No | No | No | No
2023-05-24 21:59 | Michael | Bucciero |  | 125 Old Colony DR |  | Mashpee | MA | 2649 | 617-908-9501 | Electrician |  | EATON GFTCB240 | Breaker | circuit breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2023-05-20 | 2023-05-19 | 125 Old Colony Dr |  | Mashpee | MA | 2649 | Holds until range is plugged in | Kenmore | unk | none | Kitchen | Kitchen range receptacle | No | No | No | No
2023-05-25 08:45 | BRIAN | CLARK |  | 461 LOWER COUNTY RD |  | HARWICH PORT | MA | 2646 | 5084323959 | Electrical Manager |  | Siemens QF250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/14682311187 | 2023-05-03 | 2023-04-05 | 1 Willey Way |  | Falmouth | MA | 2536 | When built in air fryer comes on the circuit trips. | Frigidaire | GCRE3060RF | N/A | Low income residential housing | Kitchen range | No | Yes | No | Yes | https://www.formstack.com/admin/download/file/14682311201
2023-05-25 08:48 | BRIAN | CLARK |  | 461 LOWER COUNTY RD |  | HARWICH PORT | MA | 2646 | 5084323959 | Electrical Manager |  | Siemens QF250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/14682320616 | 2023-05-03 | 2023-04-05 | 7 Willey Way |  | Falmouth | MA | 2536 | When built in air fryer comes on the circuit trips. | Frigidaire | GCRE3060RF | N/A | Low income residential housing | Kitchen range | No | Yes | No | Yes | https://www.formstack.com/admin/download/file/14682320630
2023-05-25 08:49 | BRIAN | CLARK |  | 461 LOWER COUNTY RD |  | HARWICH PORT | MA | 2646 | 5084323959 | Electrical Manager |  | Siemens QF250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/14682324262 | 2023-05-03 | 2023-04-05 | 11 Willey Way |  | Falmouth | MA | 2536 | When built in air fryer comes on the circuit trips. | Frigidaire | GCRE3060RF | N/A | Low income residential housing | Kitchen range | No | Yes | No | Yes | https://www.formstack.com/admin/download/file/14682324276
2023-05-25 08:49 | BRIAN | CLARK |  | 461 LOWER COUNTY RD |  | HARWICH PORT | MA | 2646 | 5084323959 | Electrical Manager |  | Siemens QF250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/14682327235 | 2023-05-03 | 2023-04-05 | 19 Willey Way |  | Falmouth | MA | 2536 | When built in air fryer comes on the circuit trips. | Frigidaire | GCRE3060RF | N/A | Low income residential housing | Kitchen range | No | Yes | No | Yes | https://www.formstack.com/admin/download/file/14682327249
2023-05-25 08:50 | BRIAN | CLARK |  | 461 LOWER COUNTY RD |  | HARWICH PORT | MA | 2646 | 5084323959 | Electrical Manager |  | Siemens QF250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/14682330428 | 2023-05-03 | 2023-04-05 | 27 Willey Way |  | Falmouth | MA | 2536 | When built in air fryer comes on the circuit trips. | Frigidaire | GCRE3060RF | N/A | Low income residential housing | Kitchen range | No | Yes | No | Yes | https://www.formstack.com/admin/download/file/14682330442
2023-05-25 08:51 | BRIAN | CLARK |  | 461 LOWER COUNTY RD |  | HARWICH PORT | MA | 2646 | 5084323959 | Electrical Manager |  | Siemens QF250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/14682334559 | 2023-05-03 | 2023-04-05 | 30 Willet Way |  | Falmouth | MA | 2536 | When built in air fryer comes on the circuit trips. | Frigidaire | GCRE3060RF | N/A | Low income residential housing | Kitchen range | No | Yes | No | Yes | https://www.formstack.com/admin/download/file/14682334573
2023-05-25 13:18 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 617-445-6901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 201 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes
2023-05-25 13:21 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (202) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 202 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14683885231
2023-05-25 13:28 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (203) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 203 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14683927972
2023-05-25 13:33 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (204) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 204 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14683958668
2023-05-25 13:34 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (205) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 205 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14683970767
2023-05-25 13:37 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (206) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 206 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14683987504
2023-05-25 13:38 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (207) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 207 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14683995460
2023-05-25 13:39 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (208) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 208 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684001389
2023-05-25 13:40 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (209) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 209 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684007227
2023-05-25 13:43 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (210) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 210 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684022320
2023-05-25 13:44 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (211) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 211 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684027697
2023-05-25 13:45 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (212) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 212 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684036287
2023-05-25 13:46 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (213) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 213 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684042760
2023-05-25 13:48 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (214) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 214 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684058922
2023-05-25 13:50 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (216) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 216 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684069712
2023-05-25 13:51 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (217) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 217 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684077003
2023-05-25 13:52 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (218) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 218 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684083402
2023-05-25 13:54 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (219) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 219 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684092264
2023-05-25 13:55 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (301) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 301 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684101254
2023-05-25 13:57 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (302) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 302 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684110665
2023-05-25 13:58 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (303) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 303 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684118681
2023-05-25 13:59 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (304) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 304 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684126223
2023-05-25 14:00 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (305) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 305 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684132496
2023-05-25 14:01 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (306) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 306 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684140126
2023-05-25 14:03 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (307) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 307 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684151010
2023-05-25 14:04 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (308) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 308 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684159234
2023-05-25 14:05 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (309) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 309 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684165644
2023-05-25 14:06 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (310) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 310 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684171891
2023-05-25 14:08 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (311) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 311 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684181512
2023-05-25 14:09 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (312) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 312 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684188036
2023-05-25 14:10 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | Project Manager |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (314) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 314 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684197300
2023-05-25 14:11 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (315) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 315 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684204079
2023-05-25 14:12 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (316) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 316 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684209290
2023-05-25 14:13 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (317) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 317 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684215317
2023-05-25 14:16 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (401) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 401 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684234020
2023-05-25 14:18 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (402) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 402 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684248182
2023-05-25 14:19 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (403) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 403 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684257576
2023-05-25 14:20 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (404) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 404 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684264776
2023-05-25 14:21 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (405) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 405 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684271381
2023-05-25 14:22 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (406) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 406 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684276408
2023-05-25 14:23 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (407) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 407 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684281194
2023-05-25 14:24 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (408) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 408 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684290442
2023-05-25 14:25 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (409) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 409 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684296655
2023-05-25 14:26 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (410) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 410 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684303113
2023-05-25 14:27 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (411) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 411 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684308835
2023-05-25 14:28 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (412) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 412 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684315000
2023-05-25 14:30 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (413) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 413 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684322093
2023-05-25 14:33 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (414) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 414 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684342899
2023-05-25 14:35 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (415) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 415 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684357550
2023-05-25 14:37 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (416) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 416 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes
2023-05-25 14:38 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (417) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 417 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684375211
2023-05-25 14:39 | John | Teixeira |  | One John Eliot Square |  | Roxbury | MA | 2119 | 6174456901 | PM |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-05-19 | 2023-05-08 | 8 Clifford Street (419) |  | Roxbury | MA | 2119 | As directed by the electrical inspector Always Electric installed 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric GE Range (JB645RK9SS) at Unit 419 (8 Clifford Street Roxbury MA) Once powered Always Electric tested the range and found that the range and GFCI were not compatible and would trip once all the burns were on. Always Electric tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Always Electric will change the GFCI Breaker to a standard 2 Pole breaker.¦¦¦¦ | General Electric | JB645RK9SS |  | Kitchen | It is the Range in the kitchen.. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14684384792
2023-05-26 14:20 | Diversified Funding INC | Parker Street Trust |  | 74E Parker Street. Acton, MA 01720. |  | Acton | MA | 1720 | 6177196707 | Rob- Oversees all properties |  | 2P 50A Siemens GFCI | Breaker | 2pole 50 amp siemens GFCI | 50 |  | 2 Pole | Siemens | Residence |  | 2023-05-23 | 2023-05-23 | [5 empty] | stove trips gfci breaker- | HotPoint | RAS200DMWW |  | Apartments | kitchen | Yes | Yes | Yes | No
2023-05-27 16:26 | Joseph | Penney |  | 222 Haverhill Street |  | Reading | MA | 1867 | 617-590-0558 | Electrician |  | THQL2140GFT | Breaker | 2 pole 40 gfci breaker GE | 40 |  | 2 Pole | Siemens | Residence |  | 2023-03-28 | 2023-03-12 | [5 empty] | EV charger is 40 amp cord and plug connected style so inspector wanted gfci breaker incase the homeowner used the plug for another purpose such as a welder, however the EV charger trips the GFCI breaker and so the inspector permits use of non-gfci 2 pole breaker in the garage so that the EV charger can be used. | ChargePoint, Inc | CPH50 |  | garage | garage 50 amp receptacle | Yes | No | No | No
2023-06-01 13:20 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | Owner |  | NA | Breaker | Na | 30 |  | 2 Pole | Eaton | Commercial |  | 2023-06-01 | 2023-05-31 | 152 washington St |  | Salem | MA | 1970 | Ice coffee brewer will constantly trip circuit breaker | BUNNserve | IC3-DBC |  | NOT A RESIDANCE | Sales area | Yes | No | Yes | No
2023-06-01 13:29 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | owner |  | NA | Breaker | Na | 30 |  | 2 Pole | Eaton | Commercial |  | 2023-06-01 | 2023-05-31 | 152 washington St |  | Salem | MA | 1970 | Ice coffee brewer will constantly trip circuit breaker | BUNNserve | ICB SH |  | NOT A RESIDANCE | Sales area | Yes | No | Yes | No
2023-06-01 13:34 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | owner |  | NA | Breaker | Na | 30 |  | 2 Pole | Eaton | Commercial |  | 2023-06-01 | 2023-05-31 | 152 washington St |  | Salem | MA | 1970 | Ice coffee brewer will constantly trip circuit breaker | Xpresschef | MXP22DB |  | NOT A RESIDANCE | Sales area | Yes | No | Yes | No
2023-06-01 13:35 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | owner |  | NA | Breaker | Na | 30 |  | 2 Pole | Eaton | Commercial |  | 2023-06-01 | 2023-05-31 | 152 washington St |  | Salem | MA | 1970 | Ice coffee brewer will constantly trip circuit breaker | Xpresschef | MXP22DB |  | NOT A RESIDANCE | Sales area | Yes | No | Yes | No
2023-06-01 13:38 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | OWNER |  | NA | Breaker | Na | 30 |  | 2 Pole | Eaton | Commercial |  | 2023-06-01 | 2023-05-31 | 152 washington St |  | Salem | MA | 1970 | Ice coffee brewer will constantly trip circuit breaker | HATCO CORPORATION | ITQ-1750-2C |  | NOT A RESIDANCE | Sales area | Yes | No | Yes | No
2023-06-01 13:45 | Nolan | Coponen |  | 579 NH Route 119 Unit 4 |  | Rindge | NH | 3461 | 603-562-8203 | Electrician |  | GFTCB240 | Breaker | Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2023-05-30 | 2022-09-30 | 1067 King Phillip Trail |  | Baldwinville | MA | 1436 | Ongoing nuisance tripping. Careful inspection of all the wiring was completed and appliance provider inspected appliance. | GE | JS760SP5SS |  | Single Family | Kitchen | Yes | No | Yes | No
2023-06-01 15:59 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | owner |  | NA | Breaker | na | 30 |  | 2 Pole | Eaton | Residence |  | 2023-06-01 | 2023-05-31 | 152 washington St |  | Salem | MA | 1970 | GFCI breaker trips constantly | Schaerer AG CH-4528 | AG CH-4528 |  | NOT A RESIDANCE | Sales area | Yes | No | No | No
2023-06-01 16:01 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | OWNER |  | NA | Breaker | na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-06-01 | 2023-05-31 | 152 washington St |  | Salem | MA | 1970 | GFCI breaker trips constantly | BUNN | ICB TWIN SH |  | NOT A RESIDANCE | Sales area | Yes | No | No | No
2023-06-02 14:01 | Steve | Ballard |  | 191 Clyde Street | Facilities | Brookline | MA | 2467 | 6174563962 | Facilities Director |  | GE THQL1120GFCI | Breaker | GFCI Breaker | 20 |  | 1 Pole | ABB | Commercial |  | 2023-06-01 | 2023-05-01 | [5 empty] | Rational Oven Tripped June 1 3:55PM | Rational | G62S118042659336 |  | CLUBHOUSE: 2ND FLOOR FUNCTION KITCHEN | 2ND FLOOR FUNCTION KITCHEN, CLUBHOUSE | No | No | No | No
2023-06-05 09:15 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | owner |  | Levington/R03-LB230-GFR | Breaker | NA | 30 |  | 2 Pole | Leviton | Commercial |  | 2023-06-01 | 2023-06-01 | 1931 Dorchester Ave |  | Boston | MA | 2124 | GFCI Breaker holds for a while and trips | Bunn | IC3-DBC |  | Not a residence | Sales area | Yes | No | Yes | No
2023-06-05 09:16 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | owner |  | Levington/R03-LB230-GFR | Breaker | NA | 30 |  | 2 Pole | Leviton | Commercial |  | 2023-06-01 | 2023-06-01 | 1931 Dorchester Ave |  | Boston | MA | 2124 | GFCI Breaker holds for a while and trips | Bunn | ICB-SH |  | Not a residence | Sales area | Yes | No | Yes | No
2023-06-05 09:19 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | owner |  | Levington/R03-LB230-GFR | Breaker | NA | 30 |  | 2 Pole | Leviton | Commercial |  | 2023-06-01 | 2023-06-01 | 1931 Dorchester Ave |  | Boston | MA | 2124 | GFCI Breaker holds for a while and trips | Xpress Chef | MXP22DB |  | Not a residence | Sales area | Yes | No | Yes | No
2023-06-05 09:19 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | OWNER |  | Levington/R03-LB230-GFR | Breaker | NA | 30 |  | 2 Pole | Leviton | Commercial |  | 2023-06-01 | 2023-06-01 | 1931 Dorchester Ave |  | Boston | MA | 2124 | GFCI Breaker holds for a while and trips | Xpress Chef | MXP22DB |  | Not a residence | Sales area | Yes | No | Yes | No
2023-06-05 09:26 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | OWNER |  | Levington/R03-LB230-GFR | Breaker | NA | 30 |  | 2 Pole | Leviton | Commercial |  | 2023-06-01 | 2023-06-01 | 1931 Dorchester Ave |  | Boston | MA | 2124 | GFCI Breaker holds for a while and trips | Bunn | IMIX-5 |  | Not a residence | Sales area | Yes | No | Yes | No
2023-06-05 09:29 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | OWNER |  | Levington/R03-LB230-GFR | Breaker | NA | 30 |  | 2 Pole | Leviton | Commercial |  | 2023-06-01 | 2023-06-01 | 1931 Dorchester Ave |  | Boston | MA | 2124 | GFCI Breaker holds for a while and trips | HATCO Corporation | ITQ-1750-2C |  | Not a residence | Sales area | Yes | No | Yes | No
2023-06-05 09:33 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | LOWELL | MA | 1852 | 7818660616 | OWNER |  | Levington/LB250-GS | Breaker | NA | 50 |  | 2 Pole | Leviton | Commercial |  | 2023-06-01 | 2023-06-01 | 1931 Dorchester Ave |  | Boston | MA | 2124 | GFCI Breaker holds for a while and trips | Bunn | ICB TWIN SH |  | Not a residence | Sales area | Yes | No | Yes | No
2023-06-07 10:16 | Steve | Ballard |  | 191 Clyde Street | Facilities | Brookline | MA | 2467 | 6174563962 | facilities director |  | GE THQL1120GFCI | Breaker | GFCI BREAKER | 20 |  | 1 Pole | ABB | Commercial |  | 2023-06-05 | 2023-05-01 | [5 empty] | Bunn Coffee machine tripped | BUNN | DUAL TF DBC | DUAL128742 | COMMERICAL - CLUBHOUSE 2ND FLOOR FUNCTION KITCHEN | CLUBHOUSE 2ND FLOOR FUNCTION KITCHEN | No | No | No | No
2023-06-07 10:18 | Mark | Roussel |  | 33 Old Forge Ln |  | Sudbury | MA | 1776 | 978-697-2762 | Electrician |  | Siemens Model #US2-QF250AP | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2023-05-31 | 2023-05-31 | 4 McKeever Dr |  | Lexington | MA | 2420 | Instant tripping on any personal protection 5MA GFCI.¦The manufacturer dictates in their instructions that a 30MA GFCI (Equipment Protection) should be used. | Grizzel-E | Grizzel-E Duo Model GCD-6-24-P | Nothing | Single Family Home | Nothing else affected, just a carger | No | No | Yes | Yes
2023-06-07 14:47 | Jonathan | Sonis |  | 38 maple street |  | concord | MA | 1742 | 6178512665 | appliance installer |  | seimens | Breaker | gfci | 50 |  | 2 Pole | ABB | Residence |  | 2023-06-06 | 2023-06-06 | [5 empty] | breaker trips as soon as turned on | wolf | ci365cb |  | home | cooktop | Yes | Yes | Yes | No
2023-06-07 15:18 | Mark | VanMolle |  | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Owner |  | Siemens QF250A | Breaker | no | 50 |  | 2 Pole | Siemens | Residence |  | 2023-06-05 | 2023-06-05 | 38 Maple St |  | Concord | MA | 1742 | Installed a new 2 pole 50 amp gfci breaker on the new cooktop. Add appliance company check the unit. Installed a new 2 pole 50 amp gfci breaker. No change. | Wolf | C1365C/B |  | Single family | Kitchen | No | Yes | No | No
2023-06-09 15:19 | Mary | Ruhl |  | 9 Johnson Ave |  | Medford | MA | 2155 | (617) 968-7586 | Home owner |  | 00634738 BOSCH | Breaker | Siemens 2pole 50 GFCI | 50 |  | 2 Pole | Siemens | Residence |  | 2023-06-09 | 2023-06-05 | [5 empty] | Stove was heating up and tripped the breaker | Bosch Induction glass cooktop | Model #LSCE365ST |  | Home | Kitchen | Yes | No | Yes | No
2023-06-13 10:03 | John | Murphy |  | 379 Liberty Street | Suite 204 | Rockland | MA | 2370 | 7817920059 | Engineer of Record |  | Siemens, QF250a | Breaker | None | 40 | 50/2 | 2 Pole | Siemens | Residence |  | 2023-02-01 | 2023-05-18 | VYNEBROOKE |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | GE | JP5030DJ | None | Kitchen | Kitchen | No | Yes | No | Yes
2023-06-13 11:49 | Mason | Bernier |  | 325 Hopping Brook Rd |  | Holliston | MA | 1746 | 800-633-7473 | Journeyman Electrician |  | Siemens Q115DF | Breaker | N/A | 15 |  | 1 Pole | Siemens | Residence |  | 2023-02-15 | 2023-02-13 | 27 Hitching Post Dr |  | Walpole | MA | 2081 | Breaker tripped while using gas stove. | Wolfe | Wgr364g |  | Single Family | Kitchen | No | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/14765172674
2023-06-13 16:37 | Joseph | OBrien |  | 12 Oakwood | 12 Oakwood rd | wilmington | MA | 1887 | 17818444606 | Owner/Electrician |  | GFTCB240 | Breaker | x | 40 |  | 2 Pole | Eaton | Residence |  | 2023-06-09 | 2020-02-20 | 387 Washington St |  | Melsrose | MA |  | #NAME? | Whirlpool | WFE550SOH21 | no | 2 family | Kitchen | No | No | No | No
2023-06-14 16:11 | George | Papadopoulos |  | 4 Georgia dr. |  | Franklin | MA | 2038 | 5085202353 | Owner |  | Eaton BRN120DF | Breaker | NA | 20 |  | 1 Pole | Eaton | Residence |  | 2023-06-14 | 2018-08-01 | [5 empty] | New Beko refrigerator continually trips | BEKO | BFFD3624XSS |  | Single Family Home | Kitchen | No | No | Yes | Yes
2023-06-14 18:58 | Firmino | Barbosa |  | 50 Rosetta's Way |  | Bridgwater | MA | 2324 | 617-592-3477 | President |  | THQL2140GFT | Breaker | N/A | 40 |  | 2 Pole | ABB | Residence |  | 2023-02-17 | 2023-01-20 | 32 Kent Street Units 405,407,305,307 |  | Somerville | MA | 2143 | Progressive Electrical Systems installed the 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric HotPoint Range (PRE2027GB) at units 405, 407, 305, 307 (32 Kent Street Somerville MA). Once powered Progressive Electrical Systems tested the range and found that the range and GFCI were not compatible and would trip once all the burners were on. Progressive Electrical Systems tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Progressive Electric Systems will change the GFCI breaker to a standard 2 pole breaker. | HotPoint | PRE2027GB | Dedicated Circuit (Stove ONLY) | Residential Kitchen | It is the Range in the kitchen. | No | No | Yes | Yes
2023-06-14 19:18 | Firmino | Barbosa |  | 50 Rossetta's Way |  | Bridgewater | MA | 2324 | 617-592-3477 | President |  | THQL2150DFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-02-17 | 2023-01-20 | 32 Kent Street Unit 205 |  | Somerville | MA | 2143 | Progressive Electrical Systems installed the 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric Frigidaire Range (FFEF3016VWG) at unit 205 (32 Kent Street Somerville MA). Once powered Progressive Electrical Systems tested the range and found that the range and GFCI were not compatible and would trip once all the burners were on. Progressive Electrical Systems tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Progressive Electric Systems will change the GFCI breaker to a standard 2 pole breaker. | Frigidaire | FFEF3016VWG | Dedicated Circuit (Stove ONLY) | Residential Kitchen | It is the range in the kitchen | No | No | Yes | Yes
2023-06-14 19:32 | Firmino | Barbosa |  | 50 Rossetta's Way |  | Bridgewater | MA | 2324 | 617-592-3477 | President |  | THQL2150DFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-06-10 | 2023-03-15 | 32 Kent Street Units 402,302,102 |  | Somerville | MA | 2143 | Progressive Electrical Systems installed the 2 pole 50-amp GFCI Breakers (THQL2150GFT) for the electric Frigidaire Range (FFEF3016VWG) at units 402 , 302, 102, (32 Kent Street Somerville MA). Once powered Progressive Electrical Systems tested the range and found that the range and GFCI were not compatible and would trip once all the burners were on. Progressive Electrical Systems tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Progressive Electric Systems will change the GFCI breaker to a standard 2 pole breaker. | Frigidaire | FFEF3016VWG | Dedicated Circuit (Stove ONLY) | Residential Kitchen | It is the range in the kitchen | No | No | Yes | Yes
2023-06-15 07:14 | Steven | Ballard |  | 191 Clyde Street | The Country Club | Chestnut Hill | CA | 2467 | 6174563962 | Facilities Director |  | GE THQL1120GFCI | Breaker | GFCI | 20 |  | 1 Pole | ABB | Commercial |  | 2023-06-14 | 2023-05-01 | [5 empty] | Rational oven Tripped, Clubhouse 2nd Floor Function Kitchen | Rational | SCCWE62G |  | Clubhouse 2nd Floor Kitchen | Clubhouse 2nd Floor Kitchen | No | No | No | No
2023-06-15 19:17 | Firmino | Barbosa |  | 50 Rossetta's Way |  | Bridgewater | MA | 2324 | 617-592-3477 | President |  | GE THQL2140GFT | Breaker | N/A | 40 |  | 2 Pole | ABB | Residence |  | 2023-02-15 | 2023-01-20 | 32 Kent Street Unit 405 |  | Somerville | MA | 2143 | Progressive Electrical Systems installed the 2 pole 40-amp GFCI Breakers (THQL2140GFT) for the electric HotPoint Range (PRE2027GB) at unit 405, (32 Kent Street Somerville MA). Once powered Progressive Electrical Systems tested the range and found that the range and GFCI were not compatible and would trip once all the burners were on. Progressive Electrical Systems tested the circuit and confirmed that the circuit itself was not the issue and that the appliance is the cause of the breaker tripping. We reached out to the manufacturer, and they stated that the ""GFCI protection is not recommended and is likely to cause the breaker to trip. In order to correct this issue Progressive Electric Systems will change the GFCI breaker to a standard 2 pole breaker. | HotPoint | PRE2027GB | Dedicated Circuit (Stove ONLY) | Residential Kitchen | It is the Range in the kitchen. | No | No | Yes | Yes
2023-06-15 19:25 | Firmino | Barbosa |  | 50 Rosetta's Way |  | Bridgewater | MA | 2324 | 617-592-3477 | President |  | GE THQL2140GFT | Breaker | N/A | 40 |  | 2 Pole | ABB | Residence |  | 2023-02-15 | 2023-01-20 | 32 Kent Street Unit 407 |  | Somerville | MA | 2143 | Progressive Electrical Systems installed the 2 pole 40-amp GFCI Breakers¦(THQL2140GFT) for the electric HotPoint Range (PRE2027GB) at unit 407,¦(32 Kent Street Somerville MA). Once powered Progressive Electrical¦Systems tested the range and found that the range and GFCI were not¦compatible and would trip once all the burners were on. Progressive¦Electrical Systems tested the circuit and confirmed that the circuit itself was¦not the issue and that the appliance is the cause of the breaker tripping.¦We reached out to the manufacturer, and they stated that the ""GFCI¦protection is not recommended and is likely to cause the breaker to trip. In¦order to correct this issue Progressive Electric Systems will change the¦GFCI breaker to a standard 2 pole breaker. | HotPoint | PRE2027GB | Dedicated Circuit (Stove ONLY) | Residential Kitchen | It is the Range in the kitchen. | No | No | Yes | Yes
2023-06-15 19:30 | Firmino | Barbosa |  | 50 Rossetta's Way |  | Bridgewater | MA | 2324 | 617-592-3477 | President |  | GE THQL2140GFT | Breaker | N/A | 40 |  | 2 Pole | ABB | Residence |  | 2023-02-15 | 2023-01-20 | 32 Kent Street Unit 307 |  | Somerville | MA | 2143 | Progressive Electrical Systems installed the 2 pole 40-amp GFCI Breakers¦(THQL2140GFT) for the electric HotPoint Range (PRE2027GB) at unit 405,¦(32 Kent Street Somerville MA). Once powered Progressive Electrical¦Systems tested the range and found that the range and GFCI were not¦compatible and would trip once all the burners were on. Progressive¦Electrical Systems tested the circuit and confirmed that the circuit itself was¦not the issue and that the appliance is the cause of the breaker tripping.¦We reached out to the manufacturer, and they stated that the ""GFCI¦protection is not recommended and is likely to cause the breaker to trip. In¦order to correct this issue Progressive Electric Systems will change the¦GFCI breaker to a standard 2 pole breaker. | HotPoint | PRE2027GB | Dedicated Circuit (Stove ONLY) | Residential Kitchen | It is the Range in the kitchen. | No | No | Yes | Yes
2023-06-15 19:38 | Firmino | Barbosa |  | 50 Rosetta's Way |  | Bridgewater | MA | 2324 | 617-592-3477 | President |  | GE THQL2140GFT | Breaker | N/A | 40 |  | 2 Pole | ABB | Residence |  | 2023-02-15 | 2023-01-20 | 32 Kent Street Unit 305 |  | Somerville | MA | 2143 | Progressive Electrical Systems installed the 2 pole 40-amp GFCI Breakers¦(THQL2140GFT) for the electric HotPoint Range (PRE2027GB) at unit 305,¦(32 Kent Street Somerville MA). Once powered Progressive Electrical¦Systems tested the range and found that the range and GFCI were not¦compatible and would trip once all the burners were on. Progressive¦Electrical Systems tested the circuit and confirmed that the circuit itself was¦not the issue and that the appliance is the cause of the breaker tripping.¦We reached out to the manufacturer, and they stated that the ""GFCI¦protection is not recommended and is likely to cause the breaker to trip. In¦order to correct this issue Progressive Electric Systems will change the¦GFCI breaker to a standard 2 pole breaker. | HotPoint | PRE2027GB | Dedicated Circuit (Stove ONLY) | Residential Kitchen | It is the Range in the kitchen. | No | No | Yes | Yes
2023-06-15 19:48 | Firmino | Barbosa |  | 50 Rosetta's Way |  | Bridgwater | MA | 2324 | 617-592-3477 | President |  | GE THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-06-10 | 2023-03-15 | 32 Kent Street Unit 402 |  | Somerville | MA | 2143 | Progressive Electrical Systems installed the 2 pole 50-amp GFCI Breakers¦(THQL2150GFT) for the electric Frigidaire Range (FFEF3016VWG) at units¦402 (32 Kent Street Somerville MA). Once powered¦Progressive Electrical Systems tested the range and found that the range¦and GFCI were not compatible and would trip once all the burners were on.¦Progressive Electrical Systems tested the circuit and confirmed that the¦circuit itself was not the issue and that the appliance is the cause of the¦breaker tripping. We reached out to the manufacturer, and they stated that¦the ""GFCI protection is not recommended and is likely to cause the breaker¦to trip. In order to correct this issue Progressive Electric Systems will¦change the GFCI breaker to a standard 2 pole breaker.¦ | Frigidaire | FFEF3016VWG | Dedicated Circuit (Stove ONLY) | Residential Kitchen | It is the range in the kitchen | No | No | Yes | Yes
2023-06-15 19:53 | Firmino | Barbosa |  | 50 Rosetta's Way |  | Bridgewater | MA | 2324 | 617-592-3477 | President |  | GE THQL2150DFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-06-10 | 2023-03-15 | 32 Kent Street Unit 302 |  | Somerville | MA | 2143 | Progressive Electrical Systems installed the 2 pole 50-amp GFCI Breakers¦(THQL2150GFT) for the electric Frigidaire Range (FFEF3016VWG) at units¦302 (32 Kent Street Somerville MA). Once powered¦Progressive Electrical Systems tested the range and found that the range¦and GFCI were not compatible and would trip once all the burners were on.¦Progressive Electrical Systems tested the circuit and confirmed that the¦circuit itself was not the issue and that the appliance is the cause of the¦breaker tripping. We reached out to the manufacturer, and they stated that¦the ""GFCI protection is not recommended and is likely to cause the breaker¦to trip. In order to correct this issue Progressive Electric Systems will¦change the GFCI breaker to a standard 2 pole breaker. | Frigidaire | FFEF3016VWG | Dedicated Circuit (Stove ONLY) | Residential Kitchen | It is the range in the kitchen | No | No | Yes | Yes
2023-06-15 19:59 | Firmino | Barbosa |  | 50 Rosetta's Way |  | Bridgewater | MA | 2324 | 617-592-3477 | President |  | GE THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-06-10 | 2023-03-15 | 32 Kent Street Unit 102 |  | Somerville | MA | 2143 | Progressive Electrical Systems installed the 2 pole 50-amp GFCI Breakers¦(THQL2150GFT) for the electric Frigidaire Range (FFEF3016VWG) at units¦102, (32 Kent Street Somerville MA). Once powered¦Progressive Electrical Systems tested the range and found that the range¦and GFCI were not compatible and would trip once all the burners were on.¦Progressive Electrical Systems tested the circuit and confirmed that the¦circuit itself was not the issue and that the appliance is the cause of the¦breaker tripping. We reached out to the manufacturer, and they stated that¦the ""GFCI protection is not recommended and is likely to cause the breaker¦to trip. In order to correct this issue Progressive Electric Systems will¦change the GFCI breaker to a standard 2 pole breaker. | Frigidaire | FFEF3016VWG | Dedicated Circuit (Stove ONLY) | Residential Kitchen | It is the range in the kitchen¦ | No | No | Yes | Yes
2023-06-15 20:32 | Aniano | Carvalho |  | 20 Grover St | 7 | Malden | MA | 2148 | (857)233-1631 | owner |  | Siemens/QF250AP | Breaker | NA | 50 |  | 2 Pole | Siemens | Residence |  | 2023-06-14 | 2023-06-13 | 329 Harvard St #2 |  | Cambridge | MA | 2139 | Installed and wired a GFCI breaker for a stove and it was not holding, | GE | JB655SK3SS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-06-16 15:44 | Michael | Wissler |  | 672 Suffolk Street, Suite 200 |  | Lowell | MA | 1854 | 9786544500 | PM |  | GE /THQB1120GFT | Breaker | 20 AMP Single Pole | 20 |  | 1 Pole | ABB | Commercial |  | 2023-06-05 | 2023-05-22 | 585 Andover Street |  | Lawrence | MA | 1843 | Owner provided four Blodgett Zephair 100-G-ES ovens relocated from existing facility, for use in newly constructed kitchen of child care facility. When plugged in all ovens trip the breaker. Each oven has an individual circuit with a GE THQB1120GFT GFCI Breaker. Electrical Contractor has tested each circuit. Kitchen Equipment rep has verified that ovens are in good condition. Ovens had no issues in previous kitchen. Kitchen Equipment rep suggests that ovens will not operate with new GFCI Breakers. Electrical Contractor will change the breakers to standard single pole breaker. | Blodgett | Zephair 100-G-ES | None | Commercial | Kitchen | No | No | No | No
2023-06-16 15:47 | Michael | Wissler |  | 672 Suffolk Street, Suite 200 |  | Lowell | MA | 1854 | 9786544500 | PM |  | GE/THQB1120GFT | Breaker | 20 Amp Single Pole | 20 |  | 1 Pole | ABB | Commercial |  | 2023-06-05 | 2023-05-22 | 585 Andover Street |  | Lawrence | MA | 1843 | Owner provided four Blodgett Zephair 100-G-ES ovens relocated from existing facility, for use in newly constructed kitchen of child care facility. When plugged in all ovens trip the breaker. Each oven has an individual circuit with a GE THQB1120GFT GFCI Breaker. Electrical Contractor has tested each circuit. Kitchen Equipment rep has verified that ovens are in good condition. Ovens had no issues in previous kitchen. Kitchen Equipment rep suggests that ovens will not operate with new GFCI Breakers. Electrical Contractor will change the breakers to standard single pole breaker. | Blodgett | Zephair 100-G-ES | None | Commercial | Kitchen | No | No | No | No
2023-06-16 15:50 | Michael | Wissler |  | 672 Suffolk Street, Suite 200 |  | Lowell | MA | 1854 | 9786544500 | PM |  | GE/THQB1120GFT | Breaker | 20 Amp Single Pole | 20 |  | 1 Pole | ABB | Commercial |  | 2023-06-05 | 2023-05-22 | 585 Andover Street |  | Lawrence | MA | 1843 | Owner provided four Blodgett Zephair 100-G-ES ovens relocated from existing facility, for use in newly constructed kitchen of child care facility. When plugged in all ovens trip the breaker. Each oven has an individual circuit with a GE THQB1120GFT GFCI Breaker. Electrical Contractor has tested each circuit. Kitchen Equipment rep has verified that ovens are in good condition. Ovens had no issues in previous kitchen. Kitchen Equipment rep suggests that ovens will not operate with new GFCI Breakers. Electrical Contractor will change the breakers to standard single pole breaker. | Blodgett | Zephair 100-G-ES | None | Commercial | Kitchen | No | No | No | No
2023-06-16 15:53 | Michael | Wissler |  | 672 Suffolk Street, Suite 200 |  | Lowell | MA | 1854 | 9786544500 | PM |  | GE/THQB1120GFT | Breaker | 20 AMP Single Pole | 20 |  | 1 Pole | ABB | Commercial |  | 2023-06-05 | 2023-05-22 | 585 Andover Street |  | Lawrence | MA | 1843 | Owner provided four Blodgett Zephair 100-G-ES ovens relocated from existing facility, for use in newly constructed kitchen of child care facility. When plugged in all ovens trip the breaker. Each oven has an individual circuit with a GE THQB1120GFT GFCI Breaker. Electrical Contractor has tested each circuit. Kitchen Equipment rep has verified that ovens are in good condition. Ovens had no issues in previous kitchen. Kitchen Equipment rep suggests that ovens will not operate with new GFCI Breakers. Electrical Contractor will change the breakers to standard single pole breaker. | Blodgett | Zephair 100-G-ES | None | Commercial | Kitchen | No | No | No | No
2023-06-19 09:43 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C701 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 09:48 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C702 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 09:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C703 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 09:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C704 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:08 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C705 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:08 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C706 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:09 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C707 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:13 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C708 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C710 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C711 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C712 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C713 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C714 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C715 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C716 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C717 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C719 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:22 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C721 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 10:44 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C601 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C602 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:02 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C603 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:02 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C604 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:02 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C605 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:02 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C606 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:03 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C607 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:03 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C608 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:03 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C609 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:03 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C610 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:03 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C611 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:03 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C612 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:04 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C613 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:04 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C615 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:04 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C616 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:04 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C617 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:04 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C619 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:05 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C621 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:09 | Nicholas | Morency |  | 3 Winthrop Ave |  | Methuen | MA | 1826 | 9785510182 | Owner |  | L2301140204 | Breaker | Siemens panel | 50 |  | 2 Pole | Siemens | Residence |  | 2023-05-22 | 2023-05-22 | [5 empty] | We have bought 5 stoves and this breaker issue keeps happening on all appliances. Breaker was presumed fine and wiring in the plug was correct. | Frigidaire | FGIH3047VF |  | Home | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/14792873417
2023-06-19 11:27 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C501 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C502 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C503 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C504 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C505 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C506 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C507 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C508 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C509 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C510 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C511 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C512 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C513 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C514 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:29 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C515 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:29 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C516 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:29 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C517 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:29 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C519 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 11:29 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C521 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:00 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C401 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C402 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C403 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C404 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C405 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C406 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C407 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C408 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C409 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C410 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C411 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C412 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C413 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:01 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C415 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:02 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C416 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:02 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C417 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:02 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C419 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:02 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C421 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:10 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C301 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:10 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C302 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:10 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C304 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:10 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C305 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:10 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C306 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:10 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C308 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:10 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C310 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C311 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C312 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C313 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C314 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C315 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C316 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C317 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 12:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C321 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C201 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C202 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C203 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C204 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C205 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C206 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C207 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C208 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C209 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C210 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C211 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C212 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C213 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C214 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C215 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C216 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C217 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C219 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C221 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C101 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C103 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C104 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C105 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C106 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C107 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C108 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:55 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-01 | 2022-08-01 | 55 Wheeler Unit C110 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-06-19 14:55 | Diversified Funding INC | Parker Street Trust |  | 74E Parker Street. Acton, MA 01720. |  | Acton | MA | 1720 | 6177196707 | Owner |  | Siemens | Breaker | Siemens | 50 |  | 2 Pole | ABB | Residence |  | 2023-06-19 | 2023-04-05 | [5 empty] | Continuous tripping on GFCI feeding range receptacle | Hot Point | RAS 200 DMWW |  | apartment | kitchen stove | No | No | No | No
2023-06-19 15:24 | Diversified Funding INC | Parker Street Trust |  | 74N Parker Street. Acton, MA 01720. |  | Acton | MA | 1720 | 6177196707 | manager |  | Siemens | Breaker | Siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2023-06-19 | 2023-04-05 | [5 empty] | Continuous tripping on GFCI feeding range rececptacle | Hot Point | RAS 200 DMWW |  | apartment | Kitchen stove | No | No | No | No
2023-06-22 06:27 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | Lowell | MA | 1852 | 7818660616 | OWNER |  | SquareD 30A GFCI breaker/QO230GFI | Breaker | NA | 30 |  | 2 Pole | Schneider Electric | Commercial |  | 2023-06-15 | 2023-06-15 | 1001 Cambridge St |  | Cambridge | MA | 2141 | Circuit breaker will hold for a little while. But trips after a few minutes. | Turbo chef | 7109 |  | comercial | Sales area only | Yes | No | No | Yes
2023-06-22 06:28 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | Lowell | MA | 1852 | 7818660616 | owner |  | SquareD 30A GFCI breaker/QO230GFI | Breaker | NA | 30 |  | 2 Pole | Schneider Electric | Commercial |  | 2023-06-15 | 2023-06-15 | 1001 Cambridge St |  | Cambridge | MA | 2141 | Circuit breaker will hold for a little while. But trips after a few minutes. | Turbo chef | 7109 |  | comercial | Sales area only | Yes | No | No | Yes
2023-06-22 06:29 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | Lowell | MA | 1852 | 7818660616 | OWNER |  | SquareD 30A GFCI breaker/QO230GFI | Breaker | NA | 30 |  | 2 Pole | Schneider Electric | Commercial |  | 2023-06-15 | 2023-06-15 | 1001 Cambridge St |  | Cambridge | MA | 2141 | Circuit breaker will hold for a little while. But trips after a few minutes. | BUNN | IC3-DBC |  | comercial | Sales area only | Yes | No | No | Yes
2023-06-22 06:29 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | Lowell | MA | 1852 | 7818660616 | OWNER |  | SquareD 30A GFCI breaker/QO230GFI | Breaker | NA | 30 |  | 2 Pole | Schneider Electric | Commercial |  | 2023-06-15 | 2023-06-15 | 1001 Cambridge St |  | Cambridge | MA | 2141 | Circuit breaker will hold for a little while. But trips after a few minutes. | BUNN | IC3-DBC |  | comercial | Sales area only | Yes | No | No | Yes
2023-06-22 06:30 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | Lowell | MA | 1852 | 7818660616 | OWNER |  | SquareD 30A GFCI breaker/QO230GFI | Breaker | NA | 30 |  | 2 Pole | Schneider Electric | Commercial |  | 2023-06-15 | 2023-06-15 | 1001 Cambridge St |  | Cambridge | MA | 2141 | Circuit breaker will hold for a little while. But trips after a few minutes. | BUNN | ICB SH |  | comercial | Sales area only | Yes | No | No | Yes
2023-06-22 06:44 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | Lowell | MA | 1852 | 7818660616 | OWNER |  | SquareD 30A GFCI breaker/QO230GFI | Breaker | NA | 30 |  | 2 Pole | Schneider Electric | Commercial |  | 2023-06-15 | 2023-06-15 | 1001 Cambridge St |  | Cambridge | MA | 2141 | Circuit breaker will hold for a little while. But trips after a few minutes. | scherer | Espresso |  | comercial | Sales area only | Yes | No | No | Yes
2023-06-22 06:46 | Lorenzo | Arpini |  | 74 CHAPEL ST | APT 2 | Lowell | MA | 1852 | 7818660616 | ELECTRICIAN |  | SquareD 20A GFCI breaker/QO220GFI | Breaker | NA | 20 |  | 2 Pole | Schneider Electric | Commercial |  | 2023-06-15 | 2023-06-15 | 1001 Cambridge St |  | Cambridge | MA | 2141 | Circuit breaker will hold for a little while. But trips after a few minutes. | HATCO CORPORATION | ITQ8751C |  | comercial | Sales area only | Yes | No | No | Yes
2023-06-23 07:21 | Nolan | Coponen |  | 470 Williams Rd |  | Fitchburg | MA | 1420 | 603-562-8203 | Electrician |  | Gftcb240 | Breaker | Gfci | 40 |  | 2 Pole | Eaton | Residence |  | 2023-06-20 | 2023-06-23 | Kitchen |  |  |  |  | Breaker continues to trip during pre heat. | GE | JB645rk9ss |  | Single family | Kitchen | Yes | No | Yes | No
2023-06-28 09:01 | George | Hassard |  | 944 Salem Street |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Siemens 81489804 Type QPF | Breaker | 2 Pole 40AMP | 15 |  | 2 Pole | Siemens | Residence |  | 2023-05-26 | 2023-05-26 | 29 Victor St Apt 5 |  | Haverhill | MA | 1832 | Randomly trips GFCI breaker | GE | Model #JB258DM4BB Serial #AV160747Q |  | apartment | kitchen | No | No | No | No
2023-06-28 09:18 | Trevor | Hebb |  | 944 Salem St |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Siemens QPF 240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-06-26 | 2023-05-05 | 23 Victor St Unit 24 |  | Haverhill | MA | 1832 | Oven tripping within 5 minutes of turning stove on. | GE | JB258DM3BB |  | Apartment | kitchen | No | No | No | No
2023-06-28 09:29 | Trevor | Hebb |  | 944 Salem St |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Siemens | Breaker | QPF 240A | 40 | 40A | 2 Pole | Siemens | Residence |  | 2023-06-19 | 2023-10-20 | 37 Woodcock St Unit 15 |  | Haverhill | MA | 1830 | Breaker trips as soon as stove or stove top is turned on. All connections are good. | Whirlpool | WFC3150JB3 |  | Apartment | kitchen | No | No | No | No
2023-06-28 19:41 | John | rAIMO |  | BOX 762 |  | Dennis | MA | 2638 | 508.725.7259 | Electrician |  | Siemens | Breaker | GFCI | 30 |  | 2 Pole | Siemens | Residence |  | 2023-05-04 | 2023-02-23 | 33 Morning Dr |  | South Yarmouth | MA | 2664 | GFCI breaker trips when the cook top is used | Amana | ACR4303MFB4 |  | Dwelling | Kitchen | No | No | No | No
2023-06-29 10:58 | Michael | Agostino |  | 185 mystic Ave |  | Medford | MA | 2155 | 781-395-3308 | Electrician |  | AGBACOORHOOH7O5OQ-B | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/14844489096 | 2023-06-27 | 2023-06-27 | 462 Middlesex Tpk |  | Billerica | MA | 1821 | Installed the new Gfci circuit breaker , turned on the stove and the oven and circuit breaker tripped off with in a couple of minutes of stove being turned on. | Whirlpool electric stove | WFE361LVB |  | Single family house | Kitchen stove | No | Yes | No | No
2023-07-05 16:32 | Nolan | Copy |  | 1092 King Phillips Trail |  | Templeton | MA | 1468 | 603-562-8203 | Electrician |  | GFTCB240 | Breaker | 2 pole | 40 |  | 2 Pole | Eaton | Residence |  | 2023-07-04 | 2023-07-05 | [5 empty] | Trips breaker before heating up to temp. | Frigidaire | GCRE3038AFE |  | Kitchen | Kitchen range. | Yes | No | Yes | No
2023-07-07 10:07 | Brian | Collins |  | 79 Wayside Avenue |  | West Springfield | MA | 1089 | (413) 237-9129 | Project Manager |  | GFRBF-W | Breaker | Leviton 120V/20A deadfront GFCI | 20 |  | 1 Pole | Leviton | Commercial |  | 2023-06-07 | 2023-05-31 | 300 Massachusetts Ave |  | Amherst | MA | 1003 | GFCI on a dedicated 20A circuit connected to a refrigerator in a small kitchenette is tripping every time the compressor to the fridge kicks on. | LG | LTCS20020S/00 | None | Not a residence. Research building. | Small Kitchenette | No | No | No | No
2023-07-07 15:47 | Ben | Olen |  | 152 Heard St |  | Worcester | MA | 1603 | 5089631216 | Electrician |  | QF250AP | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-03-10 | 2023-01-14 | 154 myrtle st |  | Ashland | MA | 1721 | When the oven was transferring over from preheat to ready the breaker would trip. Tried various temperatures, and it happened every time. Replaced it with a regular 2pole 50amp breaker, and it's held without issues.¦ | Fridgidaire gallery | GCRE302LAFC |  | Single family home | The kitchen | No | No | No | No
2023-07-07 16:27 | Ben | Olen |  | 152 Heard St |  | Worcester | MA | 1603 | 5089631216 | Electrician |  | QF250AP | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-03-10 | 2023-01-14 | 154 myrtle st |  | Ashland | MA | 1721 | When the oven was transferring over from preheat to ready the breaker would trip. Tried various temperatures, and it happened every time. Replaced it with a regular 2pole 50amp breaker, and it's held without issues.¦ | Fridgidaire gallery | GCRE302LAFC |  | Single family home | The kitchen | No | No | No | No
2023-07-10 16:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C718 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C720 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C722 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C723 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C724 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C725 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C727 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C728 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C729 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C730 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C731 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C732 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C733 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C734 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B725 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B726 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B727 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B728 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B729 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B731 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B733 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B734 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 16:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B735 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:10 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C618 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C620 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C622 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C623 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C624 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C625 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C626 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C627 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C628 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C629 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C630 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C631 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C633 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C634 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B625 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B626 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B627 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B628 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B629 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B631 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B633 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:11 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B634 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C518 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C520 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C522 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:31 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C523 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C524 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C525 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C526 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C527 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C528 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C529 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C530 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C531 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C532 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C533 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C534 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B525 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B526 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B528 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B529 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B531 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B533 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B534 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:32 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B535 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C418 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C420 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C422 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C423 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C424 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C425 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C427 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C428 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C430 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C431 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C432 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C433 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C434 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B425 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B426 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B427 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B428 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B429 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:39 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B431 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:40 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B433 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:40 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B434 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:46 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C318 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:46 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C320 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:46 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C322 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:46 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C323 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:46 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C325 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:46 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C326 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:46 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C327 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:46 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C328 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:46 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C330 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:46 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C331 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:47 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C333 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:47 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C334 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:47 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B325 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:47 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B326 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:47 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B327 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:47 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B328 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:47 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B329 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:47 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B331 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:47 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B333 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:47 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B334 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:47 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B335 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:53 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C218 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:53 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C220 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C223 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C227 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C229 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C231 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C232 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C233 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C234 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B225 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B226 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B227 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B228 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B229 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B231 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B233 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B234 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:54 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit C118 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B125 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B126 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B127 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B129 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-10 17:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-06-01 | 2022-09-01 | 55 Wheeler Unit B131 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-07-13 10:26 | John | Raimo |  | BOX 762 |  | Dennis | MA | 2638 | 508.725.7259 | Electrician |  | Siemens/QF250 | Breaker | GFCI | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/14903703732 | 2023-05-20 | 2023-05-15 | 33 Morning Dr |  | South Yarmouth | MA | 2664 | GFCI Breaker Trips when using the cook top | Amana | ACR4303MFB4 |  | Dwelling | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/14903703748
2023-07-13 15:15 | Rob Damiano | Diversified Funding INC |  | 74-C Parker Street | Unit C | Acton | MA | 1720 | 6177196707 | Manager |  | Eaton GFTCB 240 | Breaker | n/a | 40 |  | 2 Pole | Eaton | Residence |  | 2023-07-11 | 2023-07-05 | [5 empty] | breaker tripping when using stove top and oven delay tripped approx 5-8 mins multiple trip dates | Brown Stove Works Summit Series | WEM117-IQ NJ2-65 | n/A | Kitchen | kitchen stove | No | No | No | No
2023-07-13 15:17 | Rob Damiano | Diversified Funding INC |  | 76-O | Unit O | Acton | MA | 1720 | 6177196707 | manager |  | Eaton GFTCB 240 | Breaker | n/a | 40 |  | 2 Pole | Eaton | Residence |  | 2023-07-11 | 2023-07-05 | [5 empty] | breaker tripping when using stove top and oven turned on. Delay in time after about approx 3-5 mins multiple trip dates 7/11 7/12 7/13 | Brown Stove Works Summit Series | WEM117-IQ NJ2-65 | n/A | Kitchen | kitchen stove | No | No | No | No
2023-07-17 18:26 | Steve | Laurencio |  | 32 Wildwood Drive |  | Bedford | MA | 1730 | 978 621-7221 | Owner |  | Wolf CI365TF/S | Breaker | Circuit breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-07-17 | 2023-07-17 | 7 Indian Ridge Way |  | Natick | MA |  | Circuit breaker trips when turned on. | Wolf induction cooktop | CI365TF/S |  | Single family | Kitchen | No | No | Yes | No
2023-07-19 19:08 | Steve | Laurencio |  | 7 Indian Ridge Way |  | Natick | MA | 1760 | 978 621-7221 | Electrician |  | Siemens QF250A | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2023-07-17 | 2023-07-17 | [5 empty] | Circuit breaker trips when turned on. | Wolf induction cooktop. | CI365TF/S | No | Single family | Kitchen | No | No | Yes | No
2023-07-27 18:36 | Steve | Laurencio |  | 726 Andover Street |  | Lowell | MA | 1852 | 978 621-7221 | Electrician |  | GE THQL2130 GFT | Breaker | N/A | 30 |  | 2 Pole | ABB | Residence |  | 2023-07-24 | 2023-07-24 | [5 empty] | Circuit breaker trips every couple of days. | Bosch | NIT8060SUC |  | Single family | Kitchen cooktop | No | No | No | No
2023-07-27 18:50 | Steve | Laurencio |  | 726 Andover St |  | Lowell | MA | 1852 | 978 621-7221 | Electrician |  | GE THQL2120 GFT | Breaker | N/A | 20 |  | 2 Pole | ABB | Residence |  | 2023-07-24 | 2023-07-24 | [5 empty] | Circuit trips at the end of washing or drying cycle. ¦ | Miele | Washer: TX1680WP. Heat pump dryer: WXF660 |  | Single family | Laundry machine/ heat pump dryer. | No | No | No | No
2023-07-31 14:48 | Dominic | Aquilano |  | 13 Manor Drive |  | East Sandwich | MA | 2537 | 5088784702 | Electrician |  | Eaton GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence |  | 2023-07-12 | 2023-06-01 | 28 Mashpee Neck Road |  | Mashpee | MA | 2649 | GFCI Circuit Breaker trips when electric range is turned on. | Summit | RE2411W | None | Single Family | Kitchen Electric Range | No | No | Yes | Yes
2023-07-31 15:35 | Dominic | Aquilano |  | 13 Manor Drive |  | East Sandwich | MA | 2537 | 5088784702 | Electrician |  | Eaton GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence |  | 2023-07-12 | 2023-06-01 | 28 Mashpee Neck Road |  | Mashpee | MA | 2649 | GFCI Circuit Breaker trips when electric range is turned on. | Summit | RE2411W | None | Single Family | Kitchen Electric Range | No | No | Yes | Yes
2023-07-31 16:18 | Nolan | Coponen |  | 579 NH Route 119 Unit 4 |  | Rindge | NH | 3461 | 6035628203 | Electrician |  | Eaton | Breaker | BR | 40 |  | 2 Pole | Eaton | Residence |  | 2023-07-28 | 2023-07-31 | 206 Westminster Rd |  | Princeton | NH | 3461 | Nuisance tripping during pre heat cycle. | GE | PB965YP4FS |  | Single Family | Kitchen | Yes | No | Yes | No
2023-08-01 13:16 | michael | walsh |  | 1650 Bream Dr |  | Seville | FL | 32190 | 7742835804 | Electric contractor |  | Share d 2 pole 50 | Breaker | None | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/14988421776 | 2023-08-01 | 2023-08-01 | [5 empty] | Range tripping | Samsung | 20220404 |  | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/14988421797
2023-08-01 14:19 | Edward | Mckie |  | 3 Ranlet Lane |  | Billerica | MA | 1821 | 9788075893 | Electrical contracter |  | Square D Homeline series / CECOMINOD064954 | Breaker | TIPO | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-09 | 2023-04-11 | 69 Lura Lane |  | Waltham | MA | 2451 | Breaker trips almost daily, occasionally multiple times in a row. Tripping usually occurs overnight while the range is not in use, but also occurs while using the appliance. No noticeable pattern of oven use trips breaker. Tripping began within a month of installation | Bertazzoni | MAST304INMXE |  | Single family home | Kitchen | Yes | No | No | Yes
2023-08-01 17:49 | JASON | CURRAN |  | 2 CROSS ST |  | DOUGLAS | MA | 1516 | 774-239-0488 | OWNER/MASTER ELECTRICIAN |  | QO240GFICP /â€ŽQO240GFICP | Breaker | 2POLE 40 GFCI SQUARE D QO | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-01 | 2023-07-28 | [5 empty] | Installation of brand new dedicated 40amp circuit for wall oven, when installing the 2pole 40 gfci breaker, the microwave portion of the appliance works fine, when customer goes to use the oven the breaker will then trip immediately. | frigidaire | GCWM3067ADB | NONE | SINGLE FAMILY KITCHEN | THE KITCHEN DEDICATED WALL OVEN CIRCUIT BRAND NEW. | Yes | No | Yes | Yes
2023-08-02 10:14 | Trevor | Hebb |  | 944 Salem St |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Siemens 2P40 GFCI | Breaker | NA | 50 | 50 | 2 Pole | Siemens | Residence |  | 2023-07-26 | 2023-07-26 | 52-19 Victor St |  | Haverhill | MA | 1832 | Tripping after running for a few minutes. | Whirlpool | WFC 315S0 JB3 |  | Apartment | Kitchen/stove | No | No | No | No
2023-08-03 19:11 | JASON | CURRAN |  | 2 CROSS ST |  | DOUGLAS | MA | 1516 | 774-239-0488 | OWNER/MASTER ELECTRICIAN |  | EATON , #GFTCB250CS, #786680148712 | Breaker | 2POLE 50 GFCI | 50 |  | 2 Pole | Eaton | Residence |  | 2023-06-01 | 2023-08-15 | 32 WELCH AVE. |  | RUTLAND | MA | 1543 | THE NEW RANGE IN BRAN NEW HOME WITH BRAND NEW 6/3 50AMP CIRCUIT KEEPS TRIPPING. THE RANGE WILL BE SITTING IDLE FOR HOURS THEN RANDOMLY TRIP THE GFCI BREAKER. IT WILL BE IN THE MIDDLE OF BAKING OVEN PROCESS AND WILL TRIP THE GFCI BREAKER. | FRIGIDAIRE | GCRI3058AFG | NONE | SINGLE FAMILY NEW HOME. | THE KITCHEN RANGE. | Yes | No | Yes | No
2023-08-06 15:20 | Mark | VanMolle |  | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Owner |  | GE THQL1120 DF | Breaker | Arc | 20 |  | 1 Pole | ABB | Residence |  | 2023-07-28 | 2023-07-21 | 76 North St |  | Shrewsbury | MA | 1545 | Installed a separate 20 amp circuit on a 20 amp dual function breaker to the new microwave draw. There was nuisance tripping. Replaced the breaker. There was no change. | SHP | SMD247GSAY |  | Single family | Kitchen | No | Yes | Yes | No
2023-08-08 12:23 | Sean | Matthies |  | 1667 central st |  | Stoughton | MA | 2072 | 7814929520 | Electrician |  | Homeline hom250gfic | Breaker | Gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-08 | 2023-03-24 | 99 riverside ave unit 801 |  | Medford | MA | 2155 | Women unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | Ge | Jbs60rk9ss | None | Apartment | Kitchen range circuit¦Serial fv073006q | No | No | Yes | Yes
2023-08-08 16:17 | matthew | Poole |  | 85 Townsend street |  | Pepperell | MA | 1463 | 978 505 7825 | Electrician |  | Leviton LB240-GF | Breaker | breaker | 40 |  | 2 Pole | Leviton | Residence |  | 2023-07-19 | 2023-07-19 | 66 Burlington street |  | Lexington | MA | 2420 | Breaker trips instantly | Samsung Electric Range | NE63T8951SS/AA | none | kitchen | Kitchen | No | Yes | No | Yes
2023-08-08 16:34 | Matthew | Poole |  | 85 Townsend street |  | Pepperell | MA | 1463 | 978 549 5101 | Electrician |  | Leviton LB120DFT | Breaker | breaker | 20 |  | 1 Pole | Leviton | Residence |  | 2023-07-19 | 2023-07-19 | 66 Burlington st |  | Lexington | MA | 2420 | trips when refrigerator is plugged in | Samsung Refrigerator | RF23A9071SR/AA | none | kitchen | Kitchen | Yes | Yes | No | No
2023-08-10 08:36 | Gregory | Comeau |  | 119 Garden Street |  | Cambridge | MA | 2138 | 6178390191 | Master Electrician/ Oner |  | QF240A | Breaker | none | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-09 | 2023-07-06 | [5 empty] | The breaker trips all the time when using the stove¦I tried another breaker and that did the same thing | bosch | HIIP057U/04 |  | town house | Kitchen | No | Yes | Yes | No
2023-08-10 08:42 | Gregory | Comeau |  | 119 Garden Street |  | Cambridge | MA | 2138 | 6178390191 | Master Electrician/ Oner |  | QF240A | Breaker | none | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-09 | 2023-07-06 | [5 empty] | The breaker trips all the time when using the stove¦I tried another breaker and that did the same thing | bosch | HIIP057U/04 |  | town house | Kitchen | No | Yes | Yes | No
2023-08-10 09:54 | Gregory | Zolotas |  | 94 Broadway |  | Haverhill | MA | 1832 | 978-804-8975 | Owner |  | Type qpf class a ad17600r | Breaker | Gfci 2 pole 50 | 50 |  | 2 Pole | Siemens | Residence |  | 2023-08-10 | 2018-08-10 | [5 empty] | Electric Range trips instantly during baking cycle. | LG | Fc415afs | None | Kitchen | Kitchen range | No | No | No | No | https://www.formstack.com/admin/download/file/15033037521
2023-08-10 10:04 | Sean | Matthies |  | 1667 central st |  | Stoughton | MA | 2072 | 7814929520 | Foreman electrician |  | Hom250gfic | Breaker | Gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-10 | 2023-05-04 | 99 riverside ave unit 515 |  | Medford | MA | 2155 | Women unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. ¦ | Ge | Jbs60rk9ss | None | Apartment | Kitchen¦Serial fv07008q | No | No | Yes | Yes
2023-08-10 10:37 | Trevor | Hebb |  | 944 Salem Street |  | Groveland | MA | 01834-1751 | 9783731393 | Electrician |  | QF 240A | Breaker | QPF | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-04 | 2023-08-04 | 23 Victor St Unit 14 |  | Haverhill | MA | 1832 | Trips minutes into heating. | GE | JB 2560M3 BB |  | Residential | Kitchen | No | No | No | No
2023-08-10 10:43 | Trevor | Hebb |  | 944 Salem Street |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Siemens 2P40 | Breaker | QPF | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-04 | 2023-08-04 | 31 Woodcock Street Unit 1 |  | Haverhill | MA | 1832 | Trips minutes into heating. | GE | JB2560M3BB |  | Residential | Kitchen | No | No | No | No
2023-08-10 10:55 | Trevor | Hebb |  | 944 Salem Street |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | QF 240A | Breaker | QPF | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-04 | 2023-08-04 | 27 Victor Street Unit C |  | Haverhill | MA | 1832 | Trips minutes into heating | G.E. | JB 256 OM3 BB |  | Residential | Kitchen | No | No | No | No
2023-08-10 21:19 | Marcelo | Kensy |  | 32 Cambridge Ter |  | Cambridge | MA | 2140 | 7814201311 | Electrician |  | QF240A | Breaker | Breaker | 40 |  | 2 Pole | Siemens | Residence |  | 2023-07-30 | 2023-05-05 | [5 empty] | Breaker trips about 1-2 minutes into Oven pre-heating mode. | Bosch | HEI8056U |  | 2 Bed Condo | Kitchen | No | Yes | No | No
2023-08-10 21:25 | Marcelo | Kensy |  | 32 Cambridge Ter | Unit #1 | Cambridge | MA | 2140 | 7814201311 | Electrician |  | QF240A | Breaker | Breaker | 40 |  | 2 Pole | Siemens | Residence |  | 2023-07-31 | 2023-05-03 | [5 empty] | Breaker trips about 1-2 minutes into Oven Pre heating mode | Bosch | HEI8056U |  | 2 Bed Condo | Kitchen | No | Yes | No | No
2023-08-10 21:29 | Marcelo | Kensy |  | 32 Cambridge Ter | Unit #3 | Cambridge | MA | 2140 | 7814201311 | Electrician |  | QF240A | Breaker | breaker | 40 |  | 2 Pole | Siemens | Residence |  | 2023-07-31 | 2023-05-05 | [5 empty] | Breaker trips 1-2 minutes into Oven pre heating mode. | Bosch | HEI8056U |  | 2 Bed Condo | Kitchen | No | Yes | No | No
2023-08-17 18:26 | Steve | Laurencio |  | 13 Copeland drive |  | Bedford | MA | 1730 | 978621-7221 | Electrician |  | QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-15 | 2023-08-15 | [5 empty] | Circuit breaker trips on Baking cycle. | Samsung | NVS1K6650DS/AA | No | Single family | Kitchen oven. | No | No | No | No
2023-08-18 09:56 | Matthew | Holt |  | 3 Breed Ave Unit F |  | Woburn | MA | 1801 | 6037656746 | Electrician |  | Eaton BR250 | Breaker | NO | 50 |  | 2 Pole | Eaton | Residence |  | 2023-08-15 | 2023-08-16 | 505 Sutton St |  | North Andover | MA | 1845 | Condo community new development. Reviewed wiring for shorts/ground faults none found. The following units have been replaced with standard breakers. 1102, 1110, 1405, 1407, 2206, 3109, 1103, 1109, 1104, 1312, 1414, 3312, 3305, 3101, 1406, 2104, 2306, 2205, 1412, 2202, 3208, 1205, 2405, 2109, 1104. Total of (25) Units. | Whirlpool | WFE515SOJS3 | none | Condo | Kitchen | Yes | No | Yes | No
2023-08-18 10:19 | Matthew | Holt |  | 3 Breed Ave Unit F |  | Woburn | MA | 1801 | 6037656746 | Electrician |  | Eaton BR30 | Breaker | NO | 30 | None | 2 Pole | Eaton | Residence |  | 2023-08-15 | 2023-08-16 | 505 Sutton St |  | North Andover | MA | 1845 | Condo community new development. Reviewed wiring for shorts/ground faults none found. The following units have been replaced with standard type breaker. 1104, 1406, 1414, 1103, 1404, 1405, 1110. Total (7) Units. | Whirlpool | WED5620HW2 | none | Condo | Laundry Room | Yes | No | Yes | No
2023-08-21 12:09 | Josh | Leclair |  | 9 KIDDER RD | Suite C | CHELMSFORD | MA | 01824-3398 | 9782564845 | Master Electrician / Owner |  | GFTCB260 | Breaker | N/A | 60 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15083942680 | 2023-08-21 | 2023-08-21 | 52 Montgomery Street |  | Boston | MA | 2116 | Range trips during use. | GE Appliance | JB735SP4SS | None | Single Family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/15083942694
2023-08-21 13:46 | Trevor | Hebb |  | 944 Salem Street |  | Groveland | MA | 1834 | 9783731393 | Electric Technician |  | QF240A | Breaker | QPF | 40 |  | 2 Pole | Siemens | Residence |  | 2023-05-05 | 2023-06-07 | 29 Victor St Unit 14 |  | Haverhill | MA | 1832 | Trips minutes into heating | GE | JB2560M3BB |  | Apartment | Kitchen | No | No | No | No
2023-08-21 14:13 | Trevor | Hebb |  | 944 Salem St |  | Groveland | MA | 1834 | 9783731393 | Electrical technician |  | Siemens 2 P 40 | Breaker | QPF | 40 |  | 2 Pole | Siemens | Residence |  | 2023-07-05 | 2023-08-04 | 31 Woodcock St Unit 1 |  | Haverhill | MA | 1832 | Trips minutes into heating | GE | JB2560M3BB |  | Apartment | Kitchen | No | No | No | No
2023-08-21 16:10 | Nolan | Coponen |  | 579 NH Route 119 Unit 4 |  | Rindge | NH | 3461 | 603-562-8203 | Electrician |  | GFCB240 | Breaker | Gfci | 40 |  | 2 Pole | Eaton | Residence |  | 2023-08-20 | 2023-08-21 | 316 West Princeton Rd |  | Westminster | MA | 1473 | Circuit breaker tripping during heating cycle. | Whirlpool | WFE505WoJZ3 |  | Single Family | Kitchen | Yes | No | Yes | No
2023-08-22 15:01 | Francis | Baudanza |  | Baudanza Electric Co Inc | 328 GreaT rD | Bedford | MA | 1730 | 781-275-6662 | President/owner |  | Squar D Type Hom | Breaker | type 2 pole 50 amp GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-22 | 2023-08-21 | 33 Skyview Rd |  | Lexington | MA | 2420 | As soon as the oven is plugged in it trips the GFCI breaker | Miele | HR1622-31 SN # 00/153727737 | NA | Kitchen Oven | Kitchen Oven | No | No | No | No
2023-08-23 11:09 | gideon | Vesset |  | 14 Donton Street |  | Framingham | MA | 1701 | 617-966-0233 | electrician |  | Siemens QF240A | Breaker | Breaker | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-08 | 2023-07-25 | 20 Estabrook Road |  | Lexington | MA | 2421 | GFCI tripped every time¦¦Testing done:¦1. plug was checked and worked properly¦2. the line and outlet were worked properly¦3. the range worked properly when tested with non-GFCI circuit breaker¦4. no leak on range was detected when tested with multimeter | Maytag | MER6755AAB/S |  | single room | kitchenette | No | Yes | Yes | No
2023-08-23 17:18 | Joseph | OBrien |  | 12 Oakwood | 12 Oakwood rd | wilmington | MA | 1887 | 7818444606 | Owner |  | SIEMENS TYPE QPF CLASS A | Breaker | SIEMENS | 40 |  | 2 Pole | Eaton | Residence |  | 2023-08-23 | 2023-08-22 | 170 HOLBROOK RD |  | QUINCY | MA |  | INSTANT TRIP WHEN GFCI CIRCUIT BREAKER INSTALLED. RANGE WORKING NORMAL WITH 40AMP STANDARD CIRCUIT BREAKER INSTALLED. ¦¦THIS IS A BRAND NEW 40AMP 6/3 ROMEX CIRCUIT. | LG | LREL6325F |  | KITCHEN | KITCHEN RANGE | No | No | No | No
2023-08-23 17:25 | Joseph | OBrien |  | 12 Oakwood | 12 Oakwood rd | wilmington | MA | 1887 | 7818444606 | OWNER |  | 50AMP SIEMENS | Breaker | X | 50 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-08-01 | 312 HIGH ST |  | MEDFORD | MA | 2155 | INSTANT TRIP.¦DID TAKE OUT BONDING JUMPER IN RANGE¦NEW 50AMP 6/3 ROMEX ¦WORKED NORMAL WITH 50AMP STANDARD BREAKER¦ | FRIGIDAIRE | LFEF3054TFU |  | SINGLE FAMILY | KITCHEN | No | No | No | No
2023-08-23 21:09 | Robert | Russell |  | 52 Magnolia St |  | Arlington | MA | 02474-8726 | 7816436025 | Owner / Electrician |  | Siemans / QFGA2N | Breaker | Breaker | 20 |  | 1 Pole | Siemens | Residence |  | 2023-08-01 | 2023-03-06 | 54 Norris Street |  | Canbridge | MA | 2140 | Trips repeatedly shortly after being reset. breakers have been moved around, and swapped. The longest period of time without tripping is about 24 hours. | Thermador / Refrigerator | T36FT82ONS / 03 |  | One bedroom apartment, full gut and remodeled, new panel, all new wiring. | Kitchen | No | No | No | No
2023-08-24 08:21 | Michael | Grant |  | 10 Sawmill pond Rd |  | Sharon | MA | 2021 | 978-808-2944 | Contractor |  | THQL2140GFT | Breaker | G.F.C.I | 40 |  | 2 Pole | ABB | Residence |  | 2023-08-17 | 2023-08-17 | [5 empty] | We installed a new G.E. G.F.C.I breaker to power a new induction cook top unit. When break was turned on it immediately tripped. We then tried a another new G.E. breaker it also tripped we then tried another brand of breaker and it also tripped. We where unable to get a G.F.C.I. breaker to hold, we installed a non G.F.C.I. breaker and unit hold and worked properly. | Wolf | CI304TS |  | Single family | Kitchen | Yes | No | Yes | No
2023-08-24 10:43 | Ruth | Borchers |  | 14 Lantern Lane |  | Medfield | MA | 2052 | 508-846-8990 | homeowner |  | Eaton 50A GFCI breaker/GFTCB250 | Breaker | Ground fault circuit breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-08-18 | 2023-08-08 | 14 Lantern Lane |  | Medfield | MA | 2052 | After the stove has been on for a couple of hours, the breaker trips. The stove has been on and will cook food in oven for an hour with no problems. All the wiring has been tested and it is all good. | Samsung Electric Range | DG68-01208A-02 | No | Single family | Only the range in kitchen. | No | No | No | No
2023-08-28 14:36 | John | Peterson |  | 90 center st |  | bellingham | AL | 2019 | 15089221662 | electrician |  | gftcb250 | Breaker | eaton | 50 |  | 2 Pole | Eaton | Residence |  | 2023-08-26 | 2023-08-26 | [5 empty] | as soon as stove is turned on trips after 3min | frigidaire | fgih3047vfd |  | single family | kitchen stove | Yes | No | Yes | Yes
2023-08-29 06:49 | Chad | Tatro |  | 679C MOHAWK TRAIL |  | SHELBURNE FALLS | MA | 1370 | 4136256356 | Project Manager |  | GE THQL2150GFT | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-08-24 | 2023-08-24 | 132 Northampton Rd |  | Amherst | MA |  | Turn oven/range on. Using only 1 burner GFI trips in roughly 30 seconds. This took place in apartments 105,106,107,108,109 and 110. No further apartments were tested since every range tripped | Peerless- Premier | ECK100BP01 | None | Apartment | Kitchen range | No | No | No | No
2023-09-01 14:32 | Bill | Aleman |  | 130 Glen Ellen Blvd |  | Millis | MA | 2054 | 5083845900 | Operations Manager |  | Cutler Hammer | Breaker | Cutler Hammer | 20 |  | 1 Pole | Eaton | Residence |  | 2023-08-29 | 2023-01-01 | [5 empty] | LG washing machine on a 20 amp dual function cutler hammer brown breaker nuisance trips multiple times a week. Customer would like it changed to a non GFI breaker. | LG | WM3700HWA/03 |  | Single Family Home | Basement where washer and panel are located | Yes | No | Yes | Yes
2023-09-05 07:35 | Steve | Laurencio |  | 32 Ann Lee Rd |  | Harvard | MA | 1451 | 978621-7221 | Electrician |  | Siemens QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-25 | 2023-08-25 | [5 empty] | Circuit breaker trips when stove is plugged into outlet. | Wolf | 1R36550ST |  | Single family | Kitchen | No | No | No | No
2023-09-07 10:41 | Roy | Brooks |  | 7 Surrey Road |  | Sherborn | MA | 1702 | 617-823-0037 | Licensed Electrician |  | Eaton/GFCB Model number GFTCB250 | Breaker | Eaton | 50 |  | 2 Pole | Eaton | Residence |  | 2023-08-30 | 2023-08-30 | 7 Surrey Road |  | Sherborn | MA |  | Breakers trips each time oven comes on | Wolf Appliance | IR36550/S/T |  | Kitchen | Kitchen oven | No | No | Yes | Yes
2023-09-07 19:40 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B701 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:40 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B702 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:40 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B703 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:40 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B705 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B706 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B707 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B708 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B709 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B710 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B711 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B713 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B715 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B717 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B718 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B719 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B720 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B721 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B722 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B723 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:41 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 15 | 40 | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B724 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B601 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B602 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B603 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B605 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B606 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B607 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B608 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B609 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B610 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B611 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B613 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B615 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B617 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B618 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B619 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B620 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B621 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:50 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B623 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:51 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B624 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:56 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B622 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B501 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B502 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B503 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B505 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B506 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B507 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B508 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B509 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B510 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B511 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B513 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B515 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B517 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B518 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B520 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:58 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B521 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B522 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B523 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 19:59 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B524 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:04 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B401 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:04 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B402 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:04 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B403 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:04 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B405 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:04 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B406 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:04 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B407 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:05 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B408 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:05 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B409 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:05 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B410 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:05 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B411 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:05 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B413 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:05 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B415 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:05 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B417 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:05 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B418 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:06 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B419 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:06 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B421 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:06 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B422 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:07 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B423 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:07 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B424 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:13 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B301 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:13 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B302 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:13 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B303 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:13 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B305 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:13 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B306 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:13 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B307 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B308 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B309 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B310 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B311 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B313 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B315 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B317 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B318 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B319 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B320 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B321 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B322 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B323 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:14 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B324 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:20 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B201 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:20 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B202 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:20 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B203 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:20 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B205 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:20 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B206 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:20 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B207 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B208 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B209 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B210 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B211 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B213 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B215 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B217 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B218 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B219 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B220 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B221 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B222 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B223 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:21 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B224 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B102 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B103 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B105 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B106 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B108 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B109 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B110 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B111 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B113 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:28 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B115 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:29 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B117 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:29 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B118 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:29 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B119 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:29 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B120 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:29 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B121 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:29 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B122 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:29 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B123 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:29 | Kyle | Brunelle |  | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2022-12-01 | 55 Wheeler Unit B124 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-09-07 20:50 | Marcelo | Kensy |  | 32 Cambridge Ter | Unit #1 | Cambridge | MA | 2140 | 7814201311 | Electrician |  | G120DFN | Breaker | Breaker | 20 |  | 1 Pole | Siemens | Residence |  | 2023-09-03 | 2023-05-01 | [5 empty] | Trips after seconds cooking | Bosch | HMV3053U |  | Condo | Kitchen | No | Yes | No | No
2023-09-07 20:54 | Marcelo | Kensy |  | 32 Cambridge Ter | Unit #3 | Cambridge | MA | 2140 | 7814201311 | Electrician |  | G120DFN | Breaker | Breaker | 20 |  | 1 Pole | Siemens | Residence |  | 2023-08-05 | 2023-05-01 | [5 empty] | Trips minutes into cooking | BOSCH | HMV3053U |  | CONDO | Kitchen | No | Yes | No | No
2023-09-07 22:26 | Water | Laguerre |  | 12 Clematis Rd |  | Medford, MA | MA | 2155 | 17812198534 | Electrician Contractor |  | Siemens | Breaker | AFC/GFCI | 20 |  | 1 Pole | Siemens | Residence |  | 2023-08-16 | 2023-08-16 | 5 Milton St |  | Cambridge | MA | 2140 | After installing the AFC/GFCI breaker (Siemens ) Every time we try to connect the microwave, it trips the breaker. Only a regular breaker keeps the microwave ON. | Microwave Wirpool | WML75011HZ10 | NONE | RESIDENTIAL | ONLY the microwave circuit | No | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/15170789352
2023-09-11 07:17 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 774 218 4288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 104 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen Oven/stove top | No | No | No | No
2023-09-11 07:24 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 107 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen oven/stove top | No | No | Yes | Yes
2023-09-11 07:31 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 114 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-11 07:35 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 115 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-11 07:54 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 119 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-11 08:04 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 205 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-11 08:13 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 207 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-11 15:20 | Ryan | LaBrache |  | 1 Summer Street |  | Watertown | MA | 2472 | 6179248866 | Owner |  | THQB1120GFT | Breaker | Bolt on | 20 |  | 1 Pole | ABB | Commercial |  | 2023-09-08 | 2023-06-14 | 46 Pleasant Street |  | Cambridge | MA | 2138 | Ejection pump will not hold on a GFI. | Liberty Pumps | P382LE51 |  | Womens Center | Basement Bathroom | No | No | No | No
2023-09-12 06:38 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 214 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-12 06:41 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 215 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-12 06:44 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 217 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-12 06:46 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 307 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-12 06:50 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 319 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove TOp | No | No | Yes | Yes
2023-09-12 06:53 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 323 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove TOp | No | No | Yes | Yes
2023-09-12 06:56 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 402 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-12 06:59 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 55 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-12 07:02 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | COnstruction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 529 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-12 07:06 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 123 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-12 08:11 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell st unit 125 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-12 08:18 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 216 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-12 08:22 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 406 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-12 08:25 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 505 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS |  | Apartment | Kitchen Oven/Stove top | No | No | Yes | Yes
2023-09-12 08:28 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 120 Whitwell St Unit 524 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-12 19:27 | ALAN | GILLIGAN |  | 22 HYDE STREET |  | QUINCY | MA | 2169 | 617-293-2562 | ELECTRICAL CONTRACTOR |  | SIEMENS - BREAKER - L2206231120 | Breaker | N/A | 60 |  | 2 Pole | Siemens | Residence |  | 2023-09-08 | 2023-09-08 | 367 HAYWARD MILL ROAD |  | CONCORD | MA | 1742 | INSTANT TRIP ONCE BREAKER IS TURNED ON. BONDING BETWEEN NEUTRAL & GROUND HAS BEEN REMOVED FROM APPLIANCE. | BOSCH | HIS8655U | NO | SINGLE FAMILY HOME | KITCHEN STOVE | Yes | No | Yes | No
2023-09-13 11:48 | Jacob | Viveiros |  | 10 Conduit St |  | Acushnet | MA | 2743 | 508-995-3826 | Licensed Electrician/Assistant Project Manager |  | Siemens | Breaker | N/A | 50 |  | 1 Pole | ABB | Residence |  | 2023-06-21 | 2023-06-27 | 20 Willis Ave |  | Medford | MA |  | Range trips GFI protected breaker constantly when turned on. | Premier | EFK1020P | None | Multi-Family Apartment, Single unit affected out of six | Kitchen range tripped GFCI protected circuit multiple times, requiring a standard breaker to be installed. | No | No | No | No
2023-09-14 10:29 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 106 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 10:36 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 113 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen/Stove Top | No | No | Yes | Yes
2023-09-14 10:45 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 127 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 10:54 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 304 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 11:00 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 309 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 11:08 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 324 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 11:35 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 425 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 11:38 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 103 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 11:41 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 121 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 11:45 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 204 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 11:47 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 221 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 11:50 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 227 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 11:52 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 318 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 11:59 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 322 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:02 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 521 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove top | No | No | Yes | Yes
2023-09-14 12:05 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 116 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:08 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 122 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:13 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 208 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:15 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 325 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:17 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 409 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:20 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 415 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:22 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 416 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:25 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 225 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:27 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 306 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS |  | Apartment | Kitchen oven/stove top | No | No | Yes | Yes
2023-09-14 12:30 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 313 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:33 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 417 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS |  | Apartment | Kitchen Oven/Stove TOp | No | No | Yes | Yes
2023-09-14 12:38 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 422 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:40 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2024-06-01 | 110 Whitwell St Unit 108 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:42 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 209 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:45 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 224 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:47 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 424 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:49 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 512 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:52 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 514 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-14 12:55 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 321 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 07:41 | Domenic | Vitone |  | 86 Underwood Ave |  | West Newton | MA | 2465 | 6178387070 | Electrician |  | QF240A | Breaker | plug in type | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-08-31 | 524 California St |  | Newtonville | MA | 2460 | stove tripped when burners heated up | GE | JB645RKBSS |  | House | Kitchen Stove | No | No | Yes | Yes
2023-09-15 08:58 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 102 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 09:04 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 101 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 09:07 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 105 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 09:10 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 109 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 09:14 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 117 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 09:19 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 118 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 09:22 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 124 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 09:26 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 128 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 09:44 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 129 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/ Stove Top | No | No | Yes | Yes
2023-09-15 09:47 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 202 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 09:53 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 201 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 09:58 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 203 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 10:04 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 206 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 10:07 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 211 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 10:10 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 212 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 10:14 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 213 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 10:18 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 218 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 10:21 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 219 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove top | No | No | Yes | Yes
2023-09-15 10:28 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 222 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 10:31 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 223 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/ Stove Top | No | No | Yes | Yes
2023-09-15 10:34 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 226 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 11:09 | Trevor | Hebb |  | 944 Salem St |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Siemens | Breaker | N/a | 50 |  | 1 Pole | Siemens | Residence |  | 2023-08-12 | 2023-09-13 | 27 Victor St Unit 2 |  | Haverhill | MA |  | Burners tripping ground fault at normal amps | GE | JB25GDM3BB |  | Apartment | Kitchen | No | No | No | No
2023-09-15 11:19 | Trevor | Hebb |  | 944 Salem St |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | QF240A | Breaker | QPF | 40 |  | 2 Pole | Siemens | Residence |  | 2023-07-03 | 2023-08-04 | 27 Victor St Unit 6 |  | Haverhill | MA |  | Trips minutes into heating | GE | JB256OM3BB |  | Apartment | Kitchen | No | No | No | No
2023-09-15 11:22 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 228 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 11:27 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/a | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell ST Unit 229 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 11:31 | Domenic | Vitone |  | 86 Underwood Ave |  | West Newton | MA | 2465 | 6178387070 | Electrician |  | QF240A | Breaker | stab in | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-08-30 | 524 California St |  | Newtonville | MA | 2460 | stove trips when in use | GE | JB645RKBSS |  | house | kitchen stove | No | No | Yes | Yes
2023-09-15 11:46 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 302 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 11:49 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 301 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 12:10 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 303 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 12:16 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 305 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 12:35 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 308 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 12:44 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 311 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 12:50 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 312 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 12:55 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 314 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 13:10 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 315 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 13:13 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 316 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 13:18 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 317 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 13:22 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 326 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/ Stove Top | No | No | Yes | Yes
2023-09-15 13:25 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 328 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 13:29 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 327 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 13:33 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 329 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 13:37 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 401 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 13:43 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 404 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 13:47 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 403 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 13:51 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 405 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 13:55 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 408 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-15 14:34 | William | Santiago |  | 72B Concord st |  | North Reading | MA | 1864 | 781-315-3972 | General Superintendent |  | Leviton/LB120-DFT | Breaker | AFCI/GFCI | 20 |  | 1 Pole | Leviton | Commercial |  | 2023-09-06 | 2023-07-07 | 20 Island Park |  | Lawrence | MA | 1840 | Samsung frig trips the GFCI after sometime being On or sometimes instantly. This happens in 5 ADA units. | Samsung | RS28A500ASR |  | ADA rooms | 5 Handicap units. the frigs are tripping the GFCI breaker. Also tried a faceless gfci device and it also trips that. | Yes | No | Yes | Yes
2023-09-16 12:25 | peter | cucinotta |  | 26 Boyd Cir |  | Marlborough | MA | 1752 | 5085234699 | Electrical Contractor |  | Bosch/ Model #HIIP057U | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2023-08-16 | 2023-07-07 | 8 Monadnock Road |  | Arlington | MA | 2476 | The 2 pole 50amp GFCI circuit breaker trips within 5 minutes of the oven being turned on. | Bosch | HIIP057U | N/A | Single family | Kitchen | Yes | Yes | Yes | No
2023-09-16 12:41 | peter | cucinotta |  | 26 Boyd Cir |  | Marlborough | MA | 1752 | 5085234699 | Electrical contractor |  | Siemens/ Q120DFN | Breaker | N/A | 20 |  | 1 Pole | Siemens | Residence |  | 2023-07-13 | 2023-07-13 | 8 Monadnock Road |  | Arlington | MA | 2476 | The Bosch refrigerator tripped every breaker that powered it with in a couple of hours regardless of the branch circuit that it was plugged into. | Bosch | B36CT80SNS | N/A | single family home | Kitchen | Yes | Yes | Yes | No
2023-09-16 12:51 | peter | cucinotta |  | 26 Boyd Cir |  | Marlborough | MA | 1752 | 5085234699 | Electrical contractor |  | Siemens | Breaker | N/A | 20 |  | 1 Pole | Siemens | Residence |  | 2023-07-13 | 2023-07-13 | 8 Monadnock Road |  | Arlington | MA | 2476 | The Bosch refrigerator trips the circuit breaker regards of the dual function protected circuit that it is plugged into. | Bosch | B36CT80SNS | N/A | Single family home | Kitchen | Yes | Yes | Yes | No
2023-09-16 17:05 | Timothy | MacGregor |  | 61 Gratuity Road |  | Groton | MA | 1450 | 9785024520 | Owner / President |  | GFTC250 | Breaker | None available | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15212129843 | 2023-09-07 | 2023-09-07 | 1010 Memorial Drive 2A |  | Cambridge | MA | 2138 | Breaker Tripping as soon as circuit breaker was turned on.¦Replaced CB with another new 2 pole 50 GFCI CB and tripped immediately.¦ | Frigidaire | FGIH3047VFD |  | Condo | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/15212129856
2023-09-18 11:13 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 407 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 11:16 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 411 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 11:19 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 412 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 11:23 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 413 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 11:26 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell st Unit 414 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 11:29 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 418 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 11:32 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 419 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 11:35 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 421 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 11:38 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 423 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 11:42 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 426 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 11:45 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 428 |  |  |  |  | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 11:48 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 427 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 11:50 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 429 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 12:45 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 502 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS |  | Apartment | Kitchen Oven/stove Top | No | No | Yes | Yes
2023-09-18 12:47 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 501 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 12:50 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 504 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 12:52 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 503 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 12:55 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 506 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 13:23 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 508 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 13:25 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 507 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 13:27 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 509 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 13:29 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 511 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 13:32 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 513 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 13:34 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 516 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 13:36 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 517 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 13:39 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 518 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 13:41 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 519 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 13:50 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 522 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 13:53 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell ST Unit 523 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 13:56 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 526 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 13:59 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 525 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 14:42 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St 528 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-18 14:45 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-09-01 | 2023-06-01 | 110 Whitwell St Unit 527 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen Oven/Stove Top | No | No | Yes | Yes
2023-09-20 10:42 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 101 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF30116VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-20 12:01 | Jason | Toppin |  | 168 Ragged Hill Rd |  | West Brookfield | MA | 1585 | 4138960798 | Electrician |  | Eaton GFTCB250 | Breaker | Eaton pigtail GFTCB250 | 50 |  | 2 Pole | Eaton | Residence |  | 2023-09-20 | 2023-09-01 | 6 Conrad Circle |  | Easthampton | MA | 1027 | GFCI 2 pole 50 amp breaker will keep tripping randomly on the customer when they are operating their Stove. All electrical wiring is good and the appliance company has looked at the brand new stove twice to confirm that everything is working properly. The GFCI breaker is just not working with this stove as it should and causing it to trip randomly at inconvenient times. | Frigidair | GCRI3058AFG | Na | Condo | Range in Kitchen | No | No | Yes | No
2023-09-20 12:16 | Adriano | De Mello |  | 14 Bramble Hill Rd |  | Methuen | MA | 1844 | 978-221.0743 | Electrician |  | Type QPF | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15231812147 | 2023-09-19 | 2023-09-19 | 21 Eliot Rd |  | Lexington | MA | 2421 | It trips as soon as we turn on the cooktop ¦And the manufacturer manual says its not recommended to use with GFCI | Wolf Appliance, Inc | CI36560C/B |  | Kitchen | It's a induction cooktop | No | No | Yes | No | https://www.formstack.com/admin/download/file/15231812160
2023-09-20 13:13 | Josh | Leclair |  | 9 Kidder Rd | STE C | Chelmsford | MA | 1824 | 9782564845 | Master Electrician / Owner |  | QF250AP | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15232353327 | 2023-09-19 | 2023-08-15 | 4 Wildwood Lane |  | Burlington | MA | 1803 | Breaker trips when oven is in use. Seems to happen at ~400. deg. | Whirlpool | WFE525S0JZ0 | none | Single Family | Kitchen | No | No | No | No
2023-09-21 07:42 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 30A 10KA | Breaker | N/A | 30 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit 104 |  | Quincy | MA | 2169 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JTS3000SNSS |  | Apartment | Wall Oven | No | No | Yes | Yes
2023-09-21 07:45 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 30A 10KA | Breaker | N/A | 30 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit 205 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JTS3000SNSS |  | Apartment | Kitchen Wall Oven | No | No | Yes | Yes
2023-09-21 07:48 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 30A 10KA | Breaker | N/A | 30 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit 405 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JTS3000SNSS |  | Apartment | Kitchen Wall Oven | No | No | Yes | Yes
2023-09-21 07:51 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 30A 10KA | Breaker | N/A | 30 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit 505 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JTS3000SNSS |  | Apartment | Kitchen Wall Oven | No | No | Yes | Yes
2023-09-21 07:53 | Timothy | Whalley |  | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 30A 10KA | Breaker | N/A | 30 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit 504 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JTS3000SNSS |  | Apartment | Kitchen Wall Oven | No | No | Yes | Yes
2023-09-21 09:04 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | not sure | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 102 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | APartment | Kitchen | No | No | Yes | No
2023-09-21 09:10 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 103 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 09:13 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 104 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 09:16 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 107 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 09:19 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 1 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 109 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 09:22 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 110 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 09:25 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 111 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. RE-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 09:29 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 114 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 09:33 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 115 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins.¦Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 09:36 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 116 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | APARTMENT | Kitchen | No | No | Yes | No
2023-09-21 09:54 | Paul | Bergeron Jr |  | 20 Burncoat Terrace |  | Worcester | MA | 1605 | 508-735-7245 | Owner |  | GFTCB230 | Breaker | Breaker | 30 |  | 2 Pole | Eaton | Residence |  | 2023-07-27 | 2023-07-21 | 204 Weld Street |  | West Roxbury | MA | 2132 | Installed 30A for dryer and it trips instantly | Alliance | Ade3srgs173tw01 |  | Single family | Basement dryer | No | Yes | No | No
2023-09-21 09:56 | Paul | Bergeron Jr |  | 20 Burncoat Terrace |  | Worcester | MA | 1605 | 508-735-7245 | Owner |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-07-27 | 2023-07-21 | 204 Weld Street |  | West Roxbury | MA | 2132 | Installed 50A for range and it trips instantly | Frigidaire | Fgis3065pfe |  | Single family | Kitchen range | No | Yes | No | No
2023-09-21 10:20 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 118 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 10:23 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 119 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 10:26 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 120 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 10:29 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 122 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 10:33 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 125 Maple Lane |  | Medway | MA | 2053 | GFCI breaker immediately upon installation. Installed regular breaker - ran stove for 30 mins. Re-installed breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 10:36 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 124 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately. upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 10:44 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 127 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 10:46 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 133 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 10:49 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 135 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 10:51 | Roy | Brooks |  | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner/Electrician |  | Square D QO | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-16 | 2023-08-16 | 129 Maple Lane |  | Medway | MA | 2053 | GFCI breaker tripped immediately upon installation. Installed regular breaker, ran stove for 30 mins. Re-installed GFCI breaker and it continued to trip. | GE | FFEF3016VFW |  | Apartment | Kitchen | No | No | Yes | No
2023-09-21 11:38 | Tom | Land |  | 11 Lincoln Circle |  | Andover | MA | 1810 | 6173040661 | Owner |  | EATON GFTCB250CS | Breaker | n/a | 50 | n/a | 2 Pole | Eaton | Residence |  | 2023-09-21 | 2023-09-20 | [5 empty] | Brand New 50 AMP circuit for range. Multiple uses in 24 hour period 3-4 tripping incidents | Samsung Induction Range | #NE63B8211SS | n/a | kitchen | kitchen range receptacle for new Samsung induction range | No | Yes | No | No
2023-09-21 14:15 | Robert | O Mahony |  | 174 Sheri Ln, South Weymouth, MA 02190 |  | South Weymouth | MA | 2190 | 6174156345 | President |  | Leviton LB250-GS | Breaker | na | 50 |  | 2 Pole | Leviton | Residence |  | 2023-09-18 | 2023-09-18 | 64 Hill St |  | Lexington | MA |  | When the condenser stops running the GFCI breaker instantaneously trips | ECOER | EODA18H-4860 | no | single family home | First floor | Yes | No | Yes | No
2023-09-21 14:18 | Robert | O Mahony |  | 174 Sheri Ln, South Weymouth, MA 02190 |  | South Weymouth | MA | 2190 | 6174156345 | President |  | Leviton LB250-GS | Breaker | na | 50 |  | 2 Pole | Leviton | Residence |  | 2023-09-18 | 2023-09-18 | 64 Hill St |  | Lexington | MA |  | Wall oven trips instantaneously once powered up | Miele | JJW3830LM100 | no | single family | Kitchen | Yes | No | Yes | No
2023-09-21 14:35 | Robert | O Mahony |  | 174 Sheri Ln, South Weymouth, MA 02190 |  | South Weymouth | MA | 2190 | 6174156345 | president |  | LB250-GS | Breaker | na | 50 |  | 2 Pole | Leviton | Residence |  | 2023-09-18 | 2023-09-18 | 64 Hill St |  | Lexington | MA |  | Cooktop trips instantaneously once powered up | Miele | JIC4536XB | no | single family | Kitchen | Yes | No | Yes | No
2023-09-21 21:48 | Richard | Chase |  | 16 Fermanagh St. |  | Haverhill | MA | 1835 | (781) 589-0262 | Electrician |  | Eaton GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-09-14 | 2023-09-14 | 320 Dodge St. |  | Beverly | MA | 1915 | Circuit breaker trips instantaneously. Will not reset with appliance plugged in. Appliance does not require a connection of the grounded (white) conductor. The appliance functions properly with a standard 2 pole 50 ampere circuit breaker. | Wolf | IR36550/S/T | None | Single family | Kitchen | No | No | No | No
2023-09-22 07:52 | Richard | Chase |  | 16 Fermanagh St. |  | Haverhill | MA | 1835 | (781) 589-0262 | Electrician |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-09-14 | 2023-09-14 | 320 Dodge St. |  | Beverly | MA | 1915 | Circuit breaker tripped as soon as it was turned on. Appliance is connected to a dedicated circuit, with a 4-wire cord and receptacle. Connections were all checked a second time. Appliance has no grounded (white) conductor connections, per instructions. No actual fault current detected. | Wolf | IR36550/S/T | None | Single family | Kitchen | No | No | No | No
2023-09-25 09:28 | Jason | Toppin |  | 168 Ragged Hill Rd |  | West Brookfield | MA | 1585 | 4138960798 | Electrician |  | Eaton GFTCB250 | Breaker | Eaton pigtail GFTCB250 | 50 |  | 2 Pole | Eaton | Residence |  | 2023-09-20 | 2023-09-01 | 6 Conrad Circle |  | Easthampton | MA | 1027 | GFCI 2 pole 50 amp breaker will keep tripping randomly on the customer when they are operating their Stove. All electrical wiring is good and the appliance company has looked at the brand new stove twice to confirm that everything is working properly. The GFCI breaker is just not working with this stove as it should and causing it to trip randomly at inconvenient times. | Frigidair | GCRI3058AFG | Na | Condo | Range in Kitchen | No | No | Yes | No
2023-09-25 12:53 | James | McCormack |  | 1 Cobblers Lane |  | IPSWICH | MA | 1938 | 9784710544 | Owner |  | QF250A | Breaker | Circuit Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-09-10 | 2023-09-11 | 929 Haverhill St |  | Rowley | MA | 1969 | Stove trips circuit breaker periodically | GE Appliances | JB655SK7SS |  | Single Family | Kitchen | No | No | No | No
2023-09-25 13:43 | Jimmy | Aguilar |  | 27 Wolcott Rd |  | Lynn | MA | 1902 | 6175948257 | Journeyman Electrician |  | QF250A | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2023-06-20 | 2023-06-16 | 291 N MAIN ST. |  | SHARON | MA | 2067 | BREAKER WOULD TRIPP WHEN OVEN WAOULD BE SET FOR PREHEAT. | BOSCH | HBL8753UC/05 |  | ONLY SPEED OVEN COMBINATION | KITCHEN | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/15254312718
2023-09-25 17:01 | Nalbo | Campos |  | 38 Garland St |  | Everett | MA | 2149 | 6172598501 | President (Power Fact Electric, Inc) |  | Siemens QF250A | Breaker | QPF | 50 | none | 2 Pole | Siemens | Residence |  | 2023-09-15 | 2023-09-15 | 223 Aspinwall Ave |  | Brookline | MA | 2445 | Circuit breaker will trip immediately upon turning any of the burner's knob on (it will not trip while plugged in with just the front ""LCD"" display on). This appliance was delivered with an already installed plug-in cord NEMA 14-50P | FISHER & PAYKEL | OR36SC16X1 | NONE | Single family dwelling | Kitchen | No | No | Yes | No | https://www.formstack.com/admin/download/file/15255683898
2023-09-25 17:40 | Jon | Roland |  | 364 Massachusetts Ave |  | Boxborough | MA | 1719 | 978-844-3519 | Homeowner |  | Eaton, I believe but do not see it stamped or marked (new GFCI breaker) | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2023-09-22 | 2023-09-15 | 364 Massachusetts Ave |  | Boxborough | MA | 1719 | Breaker trips as soon as stove is powered up | Wolf | IR36550/S/T | None, dedicated to range | Single family | Kitchen | No | No | Yes | Yes
2023-09-26 16:18 | Charles | Perfetuo |  | PO Box 709 |  | Norwell | MA | 2061 | 781-659-7826 | Electrician |  | Square D Homeline HOM250GFI | Breaker | None | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-20 | 2023-09-20 | 10 Camelot Drive |  | Hingham | MA | 2043 | The appliance would intermittently trip the breaker. | Wolf | IR36550/S/T |  | Kitcchen | Dedicated circuit for the appliance. | No | Yes | No | Yes
2023-09-26 16:23 | CHARLES | PERFETUO |  | P.O. BOX 709 |  | NORWELL | MA | 2061 | 7816597826 | Electrician |  | Square D Homeline 120PDF | Breaker | None | 20 |  | 1 Pole | Schneider Electric | Residence |  | 2023-09-19 | 2023-09-12 | 10 Camelot Dr |  | Hingham | MA | 2043 | Once the machine is plugged into the receptacle it trips the breaker. | LG | WM4000HWA | No | Laundry room | Washer machine is a dedicated circuit. | No | Yes | No | No
2023-09-26 20:21 | Eric | Bongini |  | 40 unkamet drive |  | Pittsfield | MA | 01201-1704 | 4132810572 | President at Bongini Electric LLC |  | Square D QO230gfci | Breaker | na | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2023-07-15 | 2023-07-11 | 83 Cone Rd. |  | Middlefield | MA | 1243 | We have 2 identical ovens in this kitchen, both ovens work fine under preheat conditions, when preheat is done ovens trip within 10-15 minutes. | Wolf | SO30TM/S/TH |  | Kitchen Oven | Kitchen | No | No | No | No
2023-09-26 20:33 | Eric | Bongini |  | 40 unkamet drive |  | Pittsfield | MA | 01201-1704 | 413 281 0572 | President at Bongini Electric LLC |  | Square D HOM230gfci | Breaker | na | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2023-07-15 | 2023-07-11 | 83 Cone Rd |  | Middlefield | MA | 1243 | We have 2 identical cooktops in kitchen, both working fine under minimal load, when more than one burner is activated the breakers trip. | THE | CIT30YWBB |  | Kitchen Cooktops | Kitchen | No | No | No | No
2023-09-27 15:06 | Trevor | Hebb |  | 944 Salem St |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | AD-910 | Breaker | GFCI | 15 |  | 2 Pole | Siemens | Residence |  | 2023-08-10 | 2023-09-22 | 2 Schoolhouse Rd |  | Gloucester | MA | 1930 | Tripping under heat, no signs of bad connection | GE | jb645r12655 |  | Residential | Kitchen | No | No | No | No
2023-09-27 15:43 | Ryan | LaBrache |  | 1 Summer Street |  | Watertown | MA | 2472 | 6179248866 | electrician |  | QF250A | Breaker | Stab In | 50 |  | 2 Pole | Siemens | Residence |  | 2023-09-27 | 2023-09-21 | 42 Carroll St |  | Watertown | MA | 2472 | 2 Pole 50amp GFI cb trip when stove is turned on | frigidaire | FCFI3083ASA |  | single family | Kitchen | No | No | No | No
2023-09-27 15:58 | Trevor | Hebb |  | 944 Salem St |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Siemens 2p50 | Breaker | QPF | 50 |  | 2 Pole | Siemens | Residence |  | 2023-07-11 | 2023-09-27 | 30 Victor St Unit 7 |  | Haverhill | MA |  | Tripping at pre heat¦ | GE | JB256DM3BB | N/a | Residential | Kitchen | No | No | No | No
2023-09-27 17:01 | Frank | OReilly |  | 49 Lexington st. |  | Burlington | MA | 1803 | 781-862-1071 | Electrician |  | 176461. S-a qs250a gfci breaker 50A 2p 120/240v | Breaker | None | 50 |  | 2 Pole | Siemens | Residence |  | 2023-09-26 | 2023-09-21 | 175 Dudley Rd |  | Bedford | MA | 1730 | Tripped seconds after convection bake was started. Reset and tripped again. Cooktop works fine. | Bosch | HII8057U |  | Single family home | Kitchen | No | No | Yes | No
2023-09-29 09:02 | Chris | Polny | 11660 | 325 Hopping Brook |  | Holliston | MA | 1746 | 7742178986 | VP Electrical Operations |  | SQ D Homeline | Breaker | NA | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-09-26 | [5 empty] | When range in unplugged and breaker is energized, the circuit and receptacle are in perfect working order, the moment the range is plugged in the GFCI trips the breaker instantly and will not reset until the appliance in unplugged.¦NOTE: THE BONDING STRAP INSIDE THE APPLIANCE HAS BEEN REMOVED PROPERLY. | BOSCH ELECTRIC FREE STANDING INDUCTION RANGE # HIS8655U | HIS8655U |  | Dwelling | Range | No | No | No | No |  | https://www.formstack.com/admin/download/file/15275912145
2023-09-29 11:16 | Jonathan | Sonis | 0 | 38 maple street |  | concord | MA | 1742 | 6173144412 | installer |  | 40 amp | Breaker | seimens | 40 |  | 1 Pole | ABB | Residence |  | 2023-09-27 | 2023-05-24 | [5 empty] | trips out as soon as oven is turned on | wall oven | cts70dp2ns1 |  | kitchen | trips as soon as turned on | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15276660426
2023-09-30 12:53 | Kirk | Enstrom | 52757 | 259 Highland Av |  | Arlington | MA | 2476 | 857 2055188 | Owner |  | Siemens | Breaker | - | 50 |  | 2 Pole | Siemens | Residence |  | 2023-07-13 | 2023-07-13 | - |  |  |  |  | Breaker immediately trips. 240 v cord & plug heater does not trip the breaker | Bosch | Benchmark model HIIP057U. | N/a | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15280876607
2023-10-03 21:58 | Jonathan | Campbell | 21684 | 129 Tiffany Road |  | Norwell | MA | 2061 | 610-513-4115 | Homeowner |  | QO250CP | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-06-27 | 2023-06-22 | [5 empty] | Our existing oven/range started tripping after the new (compliant) breaker was installed. We were told that we had to buy a new appliance. We bought a new one, and to the specifications recommended by the contracted electrician, but that one also tripped. | Whirlpool | WGE745C0FS05 |  | Single-family home | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15296357690
2023-10-04 12:08 | Ryan | LaBrache | 22042 | 1 Summer Street |  | Watertown | MA | 2472 | 6179248866 | owner |  | QFGA2 | Breaker | stab in | 20 |  | 1 Pole | Siemens | Residence |  | 2023-10-03 | 2023-09-01 | 75 Cambridge Parkway |  | Cambridge | MA | 2138 | Dual Function was fripping the Fridge | Thermador | T36BT915NS |  | condo | kitchem | No | No | No | No |  | https://www.formstack.com/admin/download/file/15298921666
2023-10-04 13:11 | Masis | Cinar | 53399 | 33 Hersom St |  | Watertown | MA | 2472 | 6174016932 | Owner |  | Ac5PA022204648 | Breaker | B53399 | 20 |  | 1 Pole | Siemens | Residence |  | 2023-09-30 | 2023-09-30 | 33 Hersom St |  | Watertown | MA | 2472 | Soon as the compressor kicks on it trips the breaker, manufacturer doesn't recommend using GFCI circuit. | Fisher & Paykel | HC-C601 | None | Single family | Kitchen Fridge | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/15299344073 | https://www.formstack.com/admin/download/file/15299344074
2023-10-04 13:40 | Masis | Cinar | 53399 | 33 Hersom St | 96 Holworthy St | Watertown | MA | 2472 | 6174016932 | Owner |  | Ac5PA022204648 | Breaker | None | 20 |  | 1 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15299539644 | 2023-09-30 | 2023-09-30 | 96 Holworthy St |  | Cambridge | MA | 2138 | Soon as the compressor kicks on it trips the breaker, manufacturer doesn't recommend using GFCI circuit. | Fisher & Paykel | HC-C601 | None | Single family | Kitchen fridge only. | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/15299539658 | https://www.formstack.com/admin/download/file/15299539659
2023-10-04 14:55 | Chris | Stevens | 20665 | PO Box 1101 | Hanson | Ma | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 6 Unit A Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the¦CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15300044104
2023-10-04 15:03 | Chris | Stevens | 20665 | PO Box 1101 | Hanson | Ma | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 6 Unit A Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the¦CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15300096993
2023-10-04 15:11 | Chri | S | 20665 | PO Box 1101 |  | hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 6 Unit B Vynebrook Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the¦CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes
2023-10-04 15:13 | Chris | Stevens | 20665 | PO Box 1101 |  | hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 6 Unit C Vynebrook Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the¦CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes
2023-10-04 15:14 | Chris | Stevens | 20665 | PO Box 1101 |  | hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 6 Unit D Vynebrook Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the¦CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes
2023-10-05 10:54 | Randy | Valerio | 22263 | 117 Central St | B-10 | Acton | MA | 1720 | 781-486-1194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-11-21 | 2022-11-21 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | No | No
2023-10-05 11:00 | Randy | Valerio | 22263 | 117 Central St | B-03 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-11-23 | 2022-11-23 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | No | No
2023-10-05 11:03 | Randy | Valerio | 22263 | 117 Central St | A-08 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-01-19 | 2022-01-19 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15304242700
2023-10-05 11:06 | Randy | Valerio | 22263 | 117 Central St | B-07 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-01-19 | 2022-01-19 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | No | No
2023-10-05 11:09 | Randy | Valerio | 22263 | 117 Central St | D-09 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-03-14 | 2022-03-14 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | No | No
2023-10-05 11:12 | Randy | Valerio | 22263 | 117 Central St | E-03 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-01-26 | 2022-01-26 | [5 empty] | Stove trips when being used | Frigidaire | FFFEF3011LBD |  | Apartment | Kitchen | No | No | No | No
2023-10-05 11:14 | Randy | Valerio | 22263 | 117 Central St | E-07 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-01-26 | 2022-01-26 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | No | No
2023-10-05 11:16 | Randy | Valerio | 22263 | 117 Central St | D-03 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-05-25 | 2022-05-25 | [5 empty] | Stove trips when bring used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | No | No
2023-10-05 11:18 | Randy | Valerio | 22263 | 117 Central St | C-12 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-03-24 | 2022-03-24 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | No | No
2023-10-05 11:21 | Randy | Valerio | 22263 | 117 Central St | F-09 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-03-24 | 2022-03-24 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | No | No
2023-10-05 11:23 | Randy | Valerio | 22263 | 117 Central St | B-04 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-06-18 | 2022-06-18 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | Apartment | kitchen | No | No | No | No
2023-10-05 11:25 | Randy | Valerio | 22263 | 117 Central St | F-08 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-08-23 | 2022-08-23 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | No | No
2023-10-05 11:27 | Randy | Valerio | 22263 | 117 Central St | F-04 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-06-18 | 2022-06-18 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | Apartment | Kitchen | No | No | No | No
2023-10-05 11:29 | Randy | Valerio | 22263 | 117 Central St | C-07 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-06-18 | 2022-06-18 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | Apartment | kitchen | No | No | No | No
2023-10-05 11:31 | Randy | Valerio | 22263 | 117 Central St | A-01 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-08-23 | 2022-08-23 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 11:33 | Randy | Valerio | 22263 | 117 Central St | D-10 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-08-23 | 2022-08-23 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 11:35 | Randy | Valerio | 22263 | 117 Central St | A-07 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-10-15 | 2022-10-15 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 11:37 | Randy | Valerio | 22263 | 117 Central St | A-02 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-08-30 | 2022-08-30 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 11:46 | Randy | Valerio | 22263 | 117 Central St | F-10 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-10-15 | 2022-10-15 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 12:06 | Randy | Valerio | 22263 | 117 Central St | F-01 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-11-07 | 2022-11-07 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011lBD |  | apartment | kitchen | No | No | No | No
2023-10-05 12:08 | Randy | Valerio | 22263 | 117 Central St | E-09 | Acton | MA | 1720 | 7814861194 | Property manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-11-07 | 2022-11-07 | [5 empty] | Stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 12:10 | Randy | Valerio | 22263 | 117 Central St | F-12 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-11-07 | 2022-11-07 | [5 empty] | stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 12:12 | Randy | Valerio | 22263 | 117 Central St | F-06 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2022-12-10 | 2022-12-10 | [5 empty] | stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 12:14 | Randy | Valerio | 22263 | 117 Central St | A-12 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-04-10 | 2023-04-10 | [5 empty] | stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 12:16 | Randy | Valerio | 22263 | 117 Central St | B-01 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-04-10 | 2023-04-10 | [5 empty] | stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | Kitchen | No | No | No | No
2023-10-05 12:24 | Randy | Valerio | 22263 | 117 Central St | C-11 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-06-10 | 2023-06-10 | [5 empty] | stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 12:26 | Randy | Valerio | 22263 | 117 Central St | E-06 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-14 | 2023-08-14 | [5 empty] | stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 12:28 | Randy | Valerio | 22263 | 117 Central St | B-09 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-09-27 | [5 empty] | stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 12:30 | Randy | Valerio | 22263 | 117 Central St | F-03 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-14 | 2023-08-14 | [5 empty] | stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 12:32 | Randy | Valerio | 22263 | 117 Central St | B-02 | Acton | MA | 1720 | 7814861194 | Property Manager |  | HOM240GFI | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-09-27 | [5 empty] | stove trips when being used | Frigidaire | FFEF3011LBD |  | apartment | kitchen | No | No | No | No
2023-10-05 21:00 | Aaron | DeAngelo | 13228 | 79 3rd Ave |  | Lowell | MA | 1854 | 9787647435 | Electrician |  | Siemens 0129639 e82617 | Breaker | GFI | 50 | 50 | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15307590302 | 2023-10-04 | 2023-10-04 | [5 empty] | Would run for a short period of time and then trip. New wire, new breaker, oven properly bonded | Samsung | NE59M4320SS | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/15307590315 | https://www.formstack.com/admin/download/file/15307590316
2023-10-05 21:07 | Aaron | DeAngelo | 13228 | 79 3rd Ave |  | Lowell | MA | 1854 | 9787647435 | Electrician |  | 0129639E82617 | Breaker | Gfi | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | 5 Newcastle rd |  | Peabody | MA |  | Would run for short period of time and then trip. New wire and new breaker. Oven properly bonded | Samsung | NE59M4320SS | None | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15307610357
2023-10-07 21:12 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-10 | 2023-05-22 | 99 Riverside Ave Unit 110 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen ¦Serial GV1B0192Q | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15314875569
2023-10-07 21:16 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-05-16 | 99 Riverside Ave Unit 210 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen ¦Serial GV107319Q | No | No | Yes | Yes
2023-10-07 21:19 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Siemens | Residence |  | 2023-09-12 | 2023-05-22 | 99 Riverside Ave Unit 211 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen ¦Serial FV079922Q | No | No | Yes | Yes
2023-10-07 21:21 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-12 | 2023-02-04 | 99 Riverside Ave Unit 213 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial AV127527Q | No | No | Yes | Yes
2023-10-07 21:24 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-12 | 2023-05-17 | 99 Riverside Ave Unit 214 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126649Q | No | No | Yes | Yes
2023-10-07 21:26 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-03-11 | 99 Riverside Ave Unit 301 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS | ` | Apartment | Kitchen¦Serial AV110846Q | No | No | Yes | Yes
2023-10-07 21:28 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFCI | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-02-04 | 99 Riverside Ave Unit 311 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV110760Q | No | No | Yes | Yes
2023-10-07 21:31 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-05-15 | 99 Riverside Ave Unit 312 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV110761Q | No | No | Yes | Yes
2023-10-07 21:33 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-05-15 | 99 Riverside Ave Unit 313 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV130186Q | No | No | Yes | Yes
2023-10-07 21:35 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-05-15 | 99 Riverside Ave Unit 314 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-ZT028393Q | No | No | Yes | Yes
2023-10-07 21:37 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-05-16 | 99 Riverside Ave Unit 315 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV107446Q | No | No | Yes | Yes
2023-10-07 21:39 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-02-14 | 99 Riverside Ave Unit 316 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JB655SKBSS |  | Apartment | Kitchen¦Serial-AV071548Q | No | No | Yes | Yes
2023-10-07 21:46 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-05-05 | 99 Riverside Ave Unit 401 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV074965Q | No | No | Yes | Yes
2023-10-07 21:48 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-05-05 | 99 Riverside Ave Unit 406 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9ss |  | Apartment | Kitchen¦Serial-FV104921Q | No | No | Yes | Yes
2023-10-07 21:51 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-05-09 | 99 Riverside Ave Unit 408 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV130190Q | No | No | Yes | Yes
2023-10-07 21:54 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-05-09 | 99 Riverside Ave Unit 412 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV110659Q | No | No | Yes | Yes
2023-10-07 21:56 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-05-09 | 99 Riverside Ave Unit 413 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | APartment | Kitchen¦Serial-AV110842Q | No | No | Yes | Yes
2023-10-07 21:59 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-05-10 | 99 Riverside Ave Unit 414 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV110656Q | No | No | Yes | Yes
2023-10-07 22:01 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-12 | 2023-05-10 | 99 Riverside Ave Unit 405 |  | medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | kitchen¦Serial-GV074968Q | No | No | Yes | Yes
2023-10-07 22:05 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-02-16 | 99 Riverside Ave Unit 1401 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JB655SKBSS |  | Apartment | Kitchen¦Serial-AV127510Q | No | No | Yes | Yes
2023-10-07 22:07 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-02-16 | 99 Riverside Ave Unit 1402 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JB655SKBSS |  | Apartment | Kitchen¦Serial-AV071546Q | No | No | Yes | Yes
2023-10-07 22:09 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-02-16 | 99 Riverside Ave Unit 1403 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JB655SKBSS |  | Apartment | Kitchen¦Serial-AV071549Q | No | No | Yes | Yes
2023-10-07 22:11 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-02-16 | 99 Riverside Ave Unit 1405 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JB655SKB66 |  | Apartment | Kitchen¦Serial-AV127518Q | No | No | Yes | Yes
2023-10-09 09:51 | Donovan | Electric Co. inc. | 13020 | 127 Milton St |  | Dedham | MA | 2026 | 7813260050 | PM |  | QF250A | Breaker | none | 50 |  | 1 Pole | Siemens | Residence |  | 2023-02-10 | 2023-02-01 | 118 Old Colony Ave |  | Quincy | MA | 2170 | Apon the first use of the ovens the GFCI breaker tripped right away. We contacted the electrical inspector, and he gave us a possible solution. he advised us to install a non GFCI breaker and run the oven and broiler for about 30 minutes to burn off the oil on the elements then reinstall the GFCI breaker. this remedy worked for a few days but is not solving the issue. These ovens are still tripping every day. there are a total of 38 units that are tripping and some of them are 40B units that need working ovens. the building owner has been in contact with the supplier and manufacture of the electric ranges and have gotten no help from them. It should also be known that we have replaced the GFCI breakers as well and the issue still persist. | GE | JB645DK8BB | None | 40B | 38 rooms of apartment Building some of which are 40B units and some are standard income ¦ | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15318916984
2023-10-09 12:49 | William | McGrath | 10999 | 916 Pleasant Street | Suite 20 | Norwood | MA | 2062 | 781-769-2747 | Master Electrician |  | GETHQL2140GFT | Breaker | NO | 40 |  | 2 Pole | ABB | Residence |  | 2023-10-09 | 2023-10-09 | 7 KONET RD |  | FOXBOROUGH | MA | 2035 | Cook top trips GFI breaker as soon as it is energized. Checked all connections and grounding - all OK ¦Tried swapping GFI breaker with different breaker but had the same issue. Had manufacturer come out to do service call and they couldn't find any issues. They installed another replacement cook top unit - same brand and model and that also trips breaker | MIELE | KM6370 | NO | KITCHEN | NONE | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15320028798
2023-10-10 11:43 | Chris | Polny | 11660 | 325 Hopping Brook |  | Holliston | MA | 1746 | 7742178986 | VP Electrical Operations |  | BRLAFGF120 | Breaker | N/A | 20 |  | 1 Pole | Eaton | Residence |  | 2023-10-06 | 2018-07-09 | 106 Myrtle St |  | Norfolk | MA | 2056 | Fridge is tripping breaker repeatedly. Clients have had to throw out food several times. Appliance company has tested fridge there a reno issues | Samsung | RSHDPNSR |  | Single family | Kitchen Fridge | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15325255698
2023-10-11 13:50 | Ryan | Cleary | 15503 | 98 Brewster Drive |  | Norwood | MA | 2062 | 585-729-0954 | Owner |  | Eaton Cutler Hammer GFCB230 | Breaker | . | 30 |  | 2 Pole | Eaton | Residence |  | 2023-10-05 | 2023-09-19 | [5 empty] | The dryer is nuisance tripping, gets about 3/4 cycle and trips. Also trips when the dryer is not in use. | Maytag Dryer | MED7230HW |  | Laundry Room residential | Laundry Room | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15332057132
2023-10-11 14:04 | Marcelo | Kensy | 21996 | 32 Heritage rd |  | Billerica | MA | 1821 | 7814201311 | Owner |  | GE THQL2140GFT | Breaker | Breaker | 40 |  | 2 Pole | ABB | Residence |  | 2023-09-09 | 2023-09-09 | [5 empty] | Tried 2 new breakers, same result. It trips right away when range gets plugged in, no continuity measured between all 4 prongs of cord. We did run the range on a regular breaker to clear possible ""build up moisture from shipping"" and still same result. | Bosch | HIS8655U/05 |  | Single Family | Range only (Kitchen) | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/15332227631
2023-10-12 13:16 | John | Vespa | 17144 | 250 Milton st |  | Dedham | MA | 2026 | 617 325 1151 | Owner |  | QF250A | Breaker | N/A | 30 |  | 2 Pole | Siemens | Residence |  | 2023-10-11 | 2023-10-11 | 41 School st Unit #1 |  | Boston | MA | 2130 | Dryer, 30 amp circuit. Appliance trips immediately, checked circuit (ok). Contacted manufacturer, they know about the issue. Dryers are manufactured for states without GFCI requirement and have no problems. | Whirlpool | WED5605MW |  | 2 Family | Laundry room | Yes | No | Yes | Yes
2023-10-12 14:47 | steve | sirois | 36882 | 862 MAIN ST |  | wakefield | MA | 1880 | 17816323363 | owner |  | qf240a | Breaker | 240 | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-12 | 2023-10-02 | 87 warwick ave |  | waltham | MA | 2451 | trips at warm up of oven | ge cafe | chs900p2m6s1 | no | single family home | kitchen oven | No | No | No | No |  | https://www.formstack.com/admin/download/file/15338340425
2023-10-12 15:30 | PETER | MCGOWAN | 14890 | 260 MASSACHUSETTS ave |  | BOXBORO | MA | 1719 | 9782632971 | general manager |  | GFTCB250 | Breaker | EATON | 50 |  | 2 Pole | Eaton | Residence |  | 2023-09-24 | 2023-09-20 | 53 CURTIS ST |  | FRAMINGHAM | MA | 1719 | TURNED CONVECTION SETTING ON AND BREAKER TRIPS | WHIRLPOOL | WFE775HOHZ |  | SINGLE FAMILY DWELLING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15338615855
2023-10-13 05:55 | Marcelo | Kensy | 21996 | 16 Lincoln St |  | Belmont | MA | 2478 | 7814201311 | Electrician |  | GE THQL2140GFT | Breaker | Breaker | 40 |  | 2 Pole | ABB | Residence |  | 2023-09-09 | 2023-09-09 | [5 empty] | Tried 2 new breakers, same result. It trips right away when range gets plugged in, no continuity measured between all 4 prongs of cord. We did run the range on a regular breaker to clear possible ""build up moisture from shipping"" and still same result. | Bosch | HIS8655U/05 |  | Single Family | Kitchen (Range only) | No | No | No | No |  | https://www.formstack.com/admin/download/file/15341132912
2023-10-13 12:38 | Jessica | Brewer | 17118 | 25 Hunting St | #2 | Cambridge | MA | 2141 | 9172072077 | Owner |  | Siemens | Breaker | n/a | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-12 | 2023-10-11 | [5 empty] | Tripped only a few minutes after top oven runs | General Electric | CH5950P4m6W2 |  | home | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15342973530
2023-10-13 21:53 | sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-12 | 2023-04-25 | 99 Riverside Ave Unit 501 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV096281Q | No | No | Yes | Yes
2023-10-13 21:56 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-04-26 | 99 Riverside Ave Unit 502 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV096250Q | No | No | Yes | Yes
2023-10-13 21:57 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | GE | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-04-26 | 99 Riverside Ave Unit 504 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | kitchen¦Serial-GV082832Q | No | No | Yes | Yes
2023-10-13 22:00 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-04-26 | 99 Riverside Ave Unit 505 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-VT060076Q | No | No | Yes | Yes
2023-10-13 22:02 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-12 | 2023-05-01 | 99 Riverside Ave Unit 511 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV074957Q | No | No | Yes | Yes
2023-10-13 22:03 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-05-02 | 99 Riverside Ave Unit 512 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV107311Q | No | No | Yes | Yes
2023-10-13 22:05 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-05-02 | 99 Riverside Ave Unit 513 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV107318Q | No | No | Yes | Yes
2023-10-13 22:07 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-04-18 | 99 Riverside Ave Unit 601 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV073009Q | No | No | Yes | Yes
2023-10-13 22:09 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-04-18 | 99 Riverside Ave Unit 602 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV09G237Q | No | No | Yes | Yes
2023-10-13 22:11 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-04-19 | 99 Riverside Ave Unit 603 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | JBS60RK9SS | Kitchen¦Serial-FV10450SQ | No | No | Yes | Yes
2023-10-13 22:12 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-02-01 | 99 Riverside Ave Unit 605 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-ZT0S1466Q | No | No | Yes | Yes
2023-10-13 22:15 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-04-19 | 99 Riverside Ave Unit 606 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV072970Q | No | No | Yes | Yes
2023-10-16 17:38 | David | Hamner | 40074 | 187 Longfellow Rd |  | Waltham | MA | 2453 | 617-293-7185 | Owner |  | GFTCB250 | Breaker | GFI | 50 |  | 2 Pole | Eaton | Residence |  | 2023-09-07 | 2023-08-18 | 7 Ashcroft Rd |  | Newton | MA | 2461 | When using the burner on the stove top and oven is on is when it trips. | Bosch | HEI8056U/06 |  | House | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15355186032
2023-10-16 20:45 | Isledge | Ronzoni | 56995 | 5 PHILLIPS POND |  | NATICK | MA | 1760 | 6178994894 | Electrician |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2023-10-16 | 2023-10-16 | [5 empty] | As soon as we connected the manufactured installed cord to the single receptacle outlet the GFCI trips. | Miele electrical range | HR 1622-2i |  | Single family | Kitchen electric range | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15355939476
2023-10-17 09:00 | PAUL | GRAY | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6177040893 | PROJECT MANAGER |  | SIEMENS/QF250P | Breaker | BREAKER | 50 |  | 2 Pole | Siemens | Residence |  | 2023-09-14 | 2023-09-13 | 130 CHESTNUT HILL AVE |  | BRIGHTON/BOSTON | MA | 2135 | WHEN CONTRACTOR STARTS UP STOVE IT TEST BREAKER TRIPS, WE SWAPED OUT TO DIFFERENT BREAKER AND STILL TRIPS. THESE GE UNITS RECENTLY MANUFACTURED ARE NOT COMPATIBLE WITH GFCI REATED BREAKERS. | GE - AMANA | AACR4303MFW |  | UNIT APARTMENTS | APARTMENT UNIT KITCHENS | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15357652796
2023-10-17 10:38 | Steven | Doherty | 31894 | PO Box 215 |  | Sturbridge | MA | 1566 | 15083661119 | Electrician/Owner |  | QO240GFI | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-10 | 2023-08-10 | [5 empty] | Breaker trips within 5 minutes of unit being plugged in and energized | Bertazzoni | PROF304INSXT | none | Single Family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15358267236
2023-10-17 11:03 | Steven | Doherty | 31894 | PO Box 215 |  | Sturbridge | MA | 1566 | 15083661119 | Electrician/Owner |  | QF230A | Breaker | na | 30 |  | 2 Pole | Siemens | Residence |  | 2023-10-03 | 2023-10-03 | [5 empty] | Breaker trips within 2 minutes of energizing circuit | LG Electronics | DLE3600 | none | single family | Laundry | No | No | No | No
2023-10-17 11:05 | Steven | Doherty | 31894 | PO Box 215 |  | Sturbridge | MA | 1566 | 15083661119 | electrician/owner |  | CHGFTCCB250 | Breaker | na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-12 | [5 empty] | Breaker trips within 5 minutes of cooktop being used, longer for oven | Electrolux | FGIH3047VFE | none | single family | Kitchen | No | No | No | No
2023-10-17 17:25 | Frederick | Hart | 27115 | PO Box 3093 |  | North Attleboro | MA | 2761 | 508-699-7143 | Electrician |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-02 | 2023-10-02 | 169 Granite Street |  | Medfield | MA | 2052 | Tripped when energized. | Frigidaire | FPIC3677RF |  | Single Family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15360967016
2023-10-18 10:57 | Marcelo | Kensy | 21996 | 16 Lincoln St |  | Belmont | MA | 2478 | 7814201311 | Electrician |  | GE THQL1120DFP | Breaker | Breaker | 20 |  | 1 Pole | ABB | Residence |  | 2023-09-03 | 2023-09-01 | [5 empty] | Tripped multiple times at various times into cooking. Replace breaker, still happened. | Toshiba | EM131A5C-SS |  | Single Family | Kitchen, Microwave only | No | No | No | No
2023-10-18 21:00 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-04-20 | 99 Riverside Ave Unit 608 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV073011Q | No | No | Yes | Yes
2023-10-18 21:02 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-04-20 | 99 Riverside Ave Unit 609 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | apartment | kitchen¦serial-FV096280Q | No | No | Yes | Yes
2023-10-18 21:04 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-02-01 | 99 Riverside Ave Unit 613 |  | Medford | MA | 2155 | `Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9ss |  | apartment | kitchen¦serial-ZT0S1469Q | No | No | Yes | Yes
2023-10-18 21:06 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-04-24 | 99 Riverside Ave Unit 614 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS | ` | Apartment | Kitchen¦Serial-GV050253Q | No | No | Yes | Yes
2023-10-18 21:08 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-04-24 | 99 Riverside Ave Unit 615 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV050251Q | No | No | Yes | Yes
2023-10-18 21:11 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-03-27 | 99 Riverside Ave Unit 701 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | FV072994Q |  | Apartment | Kitchen¦Serial-FV072994Q | No | No | Yes | Yes
2023-10-18 21:13 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-03-27 | 99 Riverside Ave Unit 703 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV072994Q | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15368100090
2023-10-18 21:14 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-04-21 | 99 Riverside Ave Unit 704 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV072995Q | No | No | Yes | Yes
2023-10-18 21:16 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-04-04 | 99 Riverside Ave Unit 705 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV073010Q | No | No | Yes | Yes
2023-10-18 21:18 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-04-27 | 99 Riverside Ave Unit 706 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV073017Q | No | No | Yes | Yes
2023-10-18 21:20 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-04-10 | 99 Riverside Ave Unit 707 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV06234Q | No | No | Yes | Yes
2023-10-18 21:22 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-04-11 | 99 Riverside Ave Unit 708 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV96302Q | No | No | Yes | Yes
2023-10-18 21:24 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-04-04 | 99 Riverside Ave Unit 711 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV073014Q | No | No | Yes | Yes
2023-10-18 21:26 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-12 | 2023-04-12 | 99 Riverside Ave Unit 712 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV096305Q | No | No | Yes | Yes
2023-10-18 21:29 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-04-12 | 99 Riverside Ave Unit 713 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV104939 | No | No | Yes | Yes
2023-10-19 09:51 | John | O'Leary | 13600 | 17 Jay st |  | Braintree | MA | 2184 | 6178759873 | Electrical contractor/ Owner |  | Square D/ Hom240GFI | Breaker | Square D | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/15369974869 | 2023-10-18 | 2023-10-18 | 90 Verndale st Apt1 |  | Brookline | MA | 2445 | Conduction oven trips each time I hook it up to the square D 40 amp 2 pole GFCI breaker. It holds a charge with the 40 amp standard 240 square D breaker. | Samsung | NE63T8951SS |  | Kitchen | Stove/ conduction oven | No | No | No | No | https://www.formstack.com/admin/download/file/15369974899 | https://www.formstack.com/admin/download/file/15369974902
2023-10-19 09:58 | John | O'Leary | 13600 | 17 Jay st |  | Braintree | MA | 2184 | 6178759873 | Electrical contractor/ Owner |  | Square D/ Hom240GFI | Breaker | Square D | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/15370014756 | 2023-10-18 | 2023-10-18 | 90 Verndale st Apt1 |  | Brookline | MA | 2445 | Conduction oven trips each time I hook it up to the square D 40 amp 2 pole GFCI breaker. It holds a charge with the 40 amp standard 240 square D breaker. | Samsung | NE63T8951SS |  | Kitchen | Stove/ conduction oven | No | No | No | No | https://www.formstack.com/admin/download/file/15370014777 | https://www.formstack.com/admin/download/file/15370014781
2023-10-20 16:34 | Edward | Teehan | 2217 | 2 Russett Road |  | Bedford | MA | 1730 | 7817604990 | Owner |  | Frigidaire FCF13083ASA | Breaker | Siemens | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-19 | 2023-10-06 | 70 Egerton Street |  | Arlington | MA | 2474 | Tripping when using oven. does not trip with cook top | Frigidaire | FCF13083ASA |  | Townhouse | Kitchen Range | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15377886269
2023-10-21 17:02 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-04-12 | 99 Riverside Ave Unit 713 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV104939 | No | No | Yes | Yes
2023-10-21 17:05 | Sean | Matthies | 54034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-04-13 | 99 Riverside Ave Unit 714 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV072989Q | No | No | Yes | Yes
2023-10-21 17:07 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-04-13 | 99 Riverside Ave Unit 715 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV127543Q | No | No | Yes | Yes
2023-10-21 17:09 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-04-21 | 99 Riverside Ave Unit 716 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV096237Q | No | No | Yes | Yes
2023-10-21 17:12 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-20 | 99 Riverside Ave Unit 803 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV096236Q | No | No | Yes | Yes
2023-10-21 17:14 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-24 | 99 Riverside Ave Unit 808 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV104896Q | No | No | Yes | Yes
2023-10-21 17:17 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-03-22 | 99 Riverside Ave Unit 809 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV096515Q | No | No | Yes | Yes
2023-10-21 17:18 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-03-24 | 99 Riverside Ave Unit 811 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV039054Q | No | No | Yes | Yes
2023-10-21 17:21 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-02-01 | 99 Riverside Ave Unit 813 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-ZT028329Q | No | No | Yes | Yes
2023-10-21 17:22 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-03-22 | 99 Riverside Ave Unit 815 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV104916Q | No | No | Yes | Yes
2023-10-21 17:26 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-12 | 2023-03-16 | 99 Riverside Ave Unit 901 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen ¦Serial-DV135928Q | No | No | Yes | Yes
2023-10-21 17:28 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-16 | 99 Riverside Ave Unit 903 |  | Medford | MA | 2155 | Residents throughout the complex unable to use stove as when it is turned on it trips the gfci. Checked connections and ensured the bonding strap has been removed. Performed burn off procedure per ge recommendations on many stoves but did not work. Manufacturer claimed to have fixed issue prior to purchase of these units. | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV104506Q | No | No | Yes | Yes
2023-10-21 17:56 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-16 | 99 Riverside Ave Unit 904 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. A representative from the general contractor went through the units and could not find one that did not trip the breaker at some point when he was trying them by turning them on nor from the records kept by the building management from resident complaints. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker¦ | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV135357Q | No | No | Yes | Yes
2023-10-22 10:25 | Richard | Chase | 21093 | P.O. Box 8112 |  | Haverhill | MA | 1835 | (781) 589-0262 | Electrician/Proprietor |  | M2306030480 | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-08-31 | 2023-08-31 | 93 Pleasant St. |  | North Andover | MA | 1845 | This breaker was installed to service an electric range. The circuit breaker would trip whenever the range changed cycles from a preheat to a heat mode. Several breakers were tried under several different conditions. The breaker would not trip under a preheat mode, nor would it trip when the oven was warm enough to go directly into heating mode. Only when the oven was cold, and the cycle needed to change from preheat to heat would each circuit breaker trip. | General Electric | P2S930YP |  | 2-Family | Range circuit in kitchen of unit 93 Pleasant St. No work was done in neighboring unit. | No | No | No | No
2023-10-22 13:29 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Electrical Contractor |  | Siemens 30-amp 2 pole GFCI | Breaker | none | 30 |  | 2 Pole | Siemens | Residence |  | 2023-10-12 | 2023-09-25 | 900 Mass Ave. |  | Lexington | MA |  | Installed a 30-amp GFCI. breaker on a new wall oven. After a minute or so the breaker continuously trips. | Cafe 30"" | CTC912P2NS1 |  | Single family | Kitchen. | No | Yes | Yes | Yes
2023-10-22 23:15 | Alex | Papadopoulos | 56292 | 26 Pratts Junction rd |  | STERLING | MA | 1564 | 7815075395 | Owner |  | QF250A | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-05 | 2023-10-05 | 13 Knowles Rd |  | Worcester | MA | 1602 | Range trips gfci breaker when pre-heating. All associated wiring, breaker, receptacle, boxes, appliance cord, and appliance are new. ¦¦Checked wiring. checked appliance cord. made sure ground strap was removed from oven and checked oven connections. checked receptacle and panel connections. replaced breaker with another gfci breaker. Tripping still occurs only when pre-heating. ¦¦Replaced breaker with non gfci breaker and no tripping occurs | Fridgidair | GCFI3060BFA | None | Single family home | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15383920332
2023-10-23 08:50 | Ron | Record | 17401 | 100 Sanborn Lane |  | Reading | MA | 1867 | 800-974-2451 | Electrician |  | HOM250GFIC | Breaker | GFCI Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-13 | 2023-10-04 | 238 Lowell St |  | Lexington | MA | 2420 | Homeowner unable to use stove, when oven is turned on it trips the GFI within seconds. Ensured bonding strap has been removed and ran through tests from manufacturer to no avail. Tried a second breaker to satisfy homeowner. | GE Cafe' Induction Double Oven Smart Range. | CHS950P2MS1 | none | Single family | Kitchen stove only | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/15385143174
2023-10-23 18:28 | David | Hamner | 40074 | 187 Longfellow Rd |  | Waltham | MA | 2453 | 6172937185 | Owner |  | Square D Homeline 484006004 | Breaker | GFI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-08 | 2023-07-12 | 175 Washington Street |  | Reading | MA | 1867 | Breaker trips when stove and over are on. | Bosch | HEIP056U/04 |  | Single family home | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15388969841
2023-10-24 08:46 | Raymond | Ostroski | 16764 | 100 Trade Center Suite G700 Woburn MA |  | Woburn | MA | 1801 | 781-858-6939 | owner |  | CHN240GF | Breaker | 2 Pole Circuit Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2023-10-16 | 2023-10-16 | 2 Cardinal Way |  | Methuen | MA | 1844 | Trips when oven is turned on | Kitchenaid | KOSE500ESS |  | Residential | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15391240500
2023-10-24 09:04 | Raymond | Ostroski | 16764 | 34 Fardon St, , Billerica | 34 Fardon St. | BILLERICA | MA | 1821 | 17818586939 | Owner |  | CHN240GF | Breaker | 2 Pole Circuit Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2023-10-16 | 2023-10-16 | 4 Cardinal Way |  | Methuen | MA | 1844 | Trips when oven is turned on | Kitchenaid | KOSE500ESS |  | Residential | Kitchen | No | No | Yes | No
2023-10-24 09:17 | Raymond | Ostroski | 16764 | 34 Fardon St, , Billerica | 34 Fardon St. | BILLERICA | MA | 1821 | 17818586939 | Owner |  | CHN240GF | Breaker | 2 Pole Circuit Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2023-10-16 | 2023-10-16 | 6 Cardinal Way |  | Methuen | MA | 1844 | Trips when oven is turned on | Kitchenaid | KOSE500ESS |  | Residential | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15391389962
2023-10-24 09:24 | Raymond | Ostroski | 16764 | 34 Fardon St |  | BILLERICA | MA | 1821 | 17818586939 | Owner |  | CHN240GF | Breaker | 2 Pole Circuit Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2023-10-16 | 2023-10-16 | 4 Cardinal Way |  | Methuen | MA | 1844 | Trips when oven is turned on | Kitchenaid | KOSE500ESS |  | Residential | Kitchen | No | No | Yes | No
2023-10-24 09:35 | Raymond | Ostroski | 16764 | 34 Fardon St | 34 Fardon St. | Billerica | MA | 1821 | 17818586939 | Owner |  | CHN240GF | Breaker | 2 Pole Circuit Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2023-10-16 | 2023-10-16 | 6 Cardinal Way6 |  | Methuen | MA | 1844 | Trips when oven is turned on | Kitchenaid | KOSE500ESS |  | Residential | Kitchen | No | No | Yes | No
2023-10-24 11:43 | Kelley | A Cronin | 11989 | Massachusetts | 68 Windsor Avenue | Acton | MA | 1720 | 19782635339 | Director |  | Siemins/L2206181178 | Breaker | Siemins | 50 |  | 1 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15392354185 | 2023-09-11 | 2022-08-16 | 390A Great Road, unit 3 |  | Acton | MA | 1720 | Any time the oven is turned on | GE | JBS60DK8BB |  | kitchen | The Stove and oven can not be used | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15392354198
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A701 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15394800505
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A702 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15394800951
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A703 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15394801253
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A705 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A707 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A709 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A711 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A712 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A713 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A714 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A715 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A717 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A719 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A721 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:44 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A723 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:47 | Steele | Kott | 14225 | 54 Pomeroy St |  | Easthampton | MA | 1027 | 413-527-3760 | Electrician and owner of Steele's Electrical Service Inc. |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-18 | 2023-10-16 | 30 Orchard St. |  | Amherst | MA | 1002 | Induction stove trips GFCI breaker as soon as it's turned on. Burners and oven trip breaker. All new install, wire reinspected all ok, outlet reinspected all ok, cord and cord connections reinspected all ok, tried changing out GFCI breaker twice. All three breakers trip. Appliance repair found no obvious problems in and with stove. | AGA Elise | AEL361IN | None | Kitchen stove. | No room just equipment. (Stove) | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15394819457
2023-10-24 17:52 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A602 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:52 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A603 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:52 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A605 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:52 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A607 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:53 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A609 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:53 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A610 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:53 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A612 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:53 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A613 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:53 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A614 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:53 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A615 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:53 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A616 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:53 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A617 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:53 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A619 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:53 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A621 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:53 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A624 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:53 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A625 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:53 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A626 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:55 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A623 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:58 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A501 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:58 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A502 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:58 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A503 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:58 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A505 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:58 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A507 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:59 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A509 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:59 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A510 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:59 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A511 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 17:59 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A512 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:00 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A513 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:00 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A514 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:00 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A515 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:00 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A516 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:00 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A517 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:01 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A519 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:01 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A521 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:01 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A523 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:01 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A525 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:01 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A526 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:05 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A401 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:05 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A402 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:06 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A403 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:06 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A405 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:06 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A407 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:06 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A409 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:06 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A410 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:07 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A411 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:07 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A412 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:07 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A413 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:07 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A414 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:07 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A415 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:07 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A416 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:08 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A419 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:08 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A421 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:08 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A423 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:08 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A424 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:08 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A425 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:09 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A426 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:09 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A427 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:12 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A301 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:12 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A302 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:12 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A303 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:14 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A305 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:15 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A309 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:15 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A310 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:15 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A311 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:15 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A312 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:15 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A313 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:15 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A314 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:15 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A315 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:16 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A316 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:16 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A317 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:16 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A319 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:16 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A323 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:16 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A324 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:16 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A325 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:17 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A326 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:17 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A327 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:17 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A321 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:21 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A201 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:21 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A203 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:21 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A207 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:22 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A212 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:22 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A214 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:22 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A218 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:22 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A219 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:22 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A224 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:22 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A226 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:22 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A229 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:23 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A111 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:23 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A113 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:23 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A115 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:23 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A117 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:23 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A121 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:23 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A123 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:23 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A125 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-24 18:24 | Kyle | Brunelle | 2291 | One Adams Place | 859 Willard Street | Quincy | MA | 2169 | 9784081149 | Construction Manager |  | US2:QF240A | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-01 | 2023-04-01 | 55 Wheeler Unit A127 |  | Cambridge | MA | 2138 | Apartment kitchen oven's (GE JS645SLSS) heating element starts and after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-10-25 08:38 | Ryan | LaBrache | 22042 | 1 Summer Street |  | Watertown | MA | 2472 | 6179248866 | Electrician |  | QF230A | Breaker | stabin | 30 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-09-27 | 10 Hilliard St |  | Cambridge | MA | 2138 | Dryer run for 2 mins and trip the GFI CB | Electrolux | EIED50LIW2 |  | multi family | Master bathroom/ laundry room | No | No | Yes | Yes
2023-10-25 15:59 | Francisco | Toste | 34419 | 32 Fairbanks Road |  | Raynham | MA | 2767 | 5084007384 | Electrician |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-23 | 2023-10-20 | 33 Washington Ave |  | Cambridge | MA | 2140 | Plug stove in trips during startup. | Miele | HR1622-3I |  | Condo | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15400023577
2023-10-25 20:07 | Mark | Raposo | 20105 | 1453 MORTON AVE |  | New Bedford | MA | 2745 | 5089225240 | Owner/master electrician |  | Siemens | Breaker | snap in | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-19 | 2023-08-21 | 550 Liberty Street, unit 3604 |  | Braintree | MA | 2184 | Nuisance trip during appliance operation. | unknown/ wall oven | unknown / wall oven | None | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15401212166
2023-10-27 14:06 | JOHN | MCKANAS | 20939 | 38 Main St |  | Saugus | MA | 1906 | 7815211910 | owner |  | CH230GFT | Breaker | none | 30 |  | 2 Pole | Eaton | Residence |  | 2023-10-27 | 2023-10-26 | 26 Phoebe Street |  | METHUEN | MA | 1844 | wall oven preheating then trips breaker after about 5 minutes. | Jen-Air | JJW3430LL |  | TOWNHOUSE | KITCHEN | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15410887027
2023-10-27 14:10 | JOHN | MCKANAS | 20939 | 38 Main St |  | Saugus | MA | 1906 | 7815211910 | owner |  | CH230GFT | Breaker | none | 30 |  | 2 Pole | Eaton | Residence |  | 2023-10-27 | 2023-10-26 | 26 Phoebe Street |  | METHUEN | MA | 1844 | wall oven preheating then trips breaker after about 5 minutes. | Jen-Air | JJW3430LL |  | TOWNHOUSE | KITCHEN | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15410907246
2023-10-27 14:29 | JOHN | MCKANAS | 20939 | 38 Main St |  | Saugus | MA | 1906 | 17817273531 | owner |  | CH230GFT | Breaker | none | 30 |  | 2 Pole | Eaton | Residence |  | 2023-10-26 | 2023-10-26 | 36 Phoebe St |  | METHUEN | MA | 1844 | breaker trips after 5 minutes during preheating of oven | Jen-Air | JJW3430LL |  | TOWNHOUSE | KITCHEN | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15411022597
2023-10-27 14:35 | JOHN | MCKANAS | 20939 | 38 Main St |  | Saugus | MA | 1906 | 17817273531 | OWNER |  | CH230GFT | Breaker | NONE | 30 |  | 2 Pole | Eaton | Residence |  | 2023-10-26 | 2023-10-26 | 32 Phoebe Street |  | METHUEN | MA | 1844 | breaker trips after about 5 mins during preheating of oven | KitchenAid | K0SE500ESS |  | Townhouse | Kitchen | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15411061504
2023-10-29 10:22 | Ryan | Cassidy | 52581 | 199 Elm St |  | Blackstone | MA | 1504 | 508 212 5735 | Journeyman Electrician |  | Siemens QPF2 GFCI Circuit Breaker | Breaker | none | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15415827574 | 2023-10-20 | 2023-10-17 | [5 empty] | Range will stay on for about 1 minute and then kicks off.¦- Installed standard 240v breaker for about an hour to burn off moisture / oils -- GFCI breaker still will not hold¦ | Bosch | HEI8046U |  | Single Family | Range is in Kitchen, unable to cook or use brand new appliance due to nuisance GFCI tripping.¦ | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15415827586
2023-10-29 10:31 | Ryan | Cassidy | 52581 | 199 Elm St |  | Blackstonee | MA | 1504 | 508 212 5735 | Journeyman Electrician |  | Siemens QPF2 GFCI Circuit Breaker | Breaker | none | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15415845360 | 2023-10-20 | 2023-10-17 | 8 Zachary Ln |  | Franklin | MA | 2038 | Range will stay on for about 1 minute and then kicks off.¦- Installed standard 240v breaker for about an hour to burn off moisture / oils -- GFCI breaker still will not hold¦ | Bosch | HEI8046U | none | Single Family | Range is in Kitchen, unable to cook or use brand new appliance due to nuisance GFCI tripping.¦ | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15415845374
2023-10-29 10:40 | Ryan | Cassidy | 52581 | 199 Elm St |  | Blackstone | MA | 1504 | 508 212 5735 | Journeyman Electrician |  | Siemens QPF2 GFCI Circuit Breaker | Breaker | none | 30 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15415863447 | 2023-10-20 | 2023-10-17 | 8 Zachary Rd |  | Franklin |  | 2038 | Oven will kick off after 30 seconds. ¦¦- Installed standard 240v breaker for about an hour to burn off moisture / oils -- GFCI breaker still will not hold¦ | Bosch | HBL8453UC | none | Single Family | Oven is in Kitchen, unable to cook or use brand new appliance due to nuisance GFCI tripping.¦¦¦ | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15415863461
2023-10-31 11:53 | Joseph | A Silverio | 17118 | 32 Franklin St | 17 Park Rd | Lowell, MA | MA | 1854 | 19788514900 | Electrician |  | Eaton Model #GFTCB250CS | Breaker | n/a | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-27 | 2023-10-26 | 273 Barker Ave Unit #3 Lowell MA 01854 |  | Lowell | MA | 1854 | burners of stove heat up 1-2 burners when oven is turned on multiple tripping occurances | GE HOTPOINT | RBS360DM 2BB |  | apartment kitchen | kitchen stove tripping on NEW circuit GFCI protected | No | No | No | No |  | https://www.formstack.com/admin/download/file/15426305484
2023-10-31 13:40 | Thomas | Durkin | 39000000000000000 | 3 Russell St no.2 | Russell St | Waltham | MA | 2453 | 1 617 435 4721 | pres. |  | Eaton BR GFCI GFTCB250 | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2023-09-04 | 2023-09-01 | 158 miles standish Rd |  | Marlborough | ME | 1752 | I have had a problem with every oven I have put on a gfci breaker. in this case as soon as they tried to cook in the oven the breaker tripped.. | GE Stove | M-JB630DF4BB | 2nd Stove Frigidaire m# GCRE3060AFJ | Home | Kitchen- Oven | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15427064146
2023-10-31 13:49 | Bjorn | Jakobsen | 15503 | 11 Deerfield Drive |  | Medfield | MA | 2052 | 617-671-8455 | Customer |  | Cutler Hammer GFTCB230 | Breaker | . | 30 |  | 2 Pole | Eaton | Residence |  | 2023-10-25 | 2023-10-25 | [5 empty] | GFCI breaker trips as soon as you start a cycle on the dryer. GFCI breaker holds when you plug it in and lights up but when your start it to run, it trips. | Alliance Laundry System LLC | ADEE9RYS177TW01 | None | Single Family | Laundry Room Dryer | No | No | No | No |  | https://www.formstack.com/admin/download/file/15427130378
2023-10-31 20:40 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-03-17 | 99 Riverside Ave Unit 905 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV058676Q | No | No | Yes | Yes
2023-10-31 20:42 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-12 | 2023-03-17 | 99 Riverside Ave Unit 906 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV096517Q | No | No | Yes | Yes
2023-10-31 20:43 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-12 | 2023-03-17 | 99 Riverside Ave Unit 907 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV002479Q | No | No | Yes | Yes
2023-10-31 20:45 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-27 | 99 Riverside Ave Unit 908 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV096516Q | No | No | Yes | Yes
2023-10-31 20:47 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-05-01 | 99 Riverside Ave Unit 909 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV079919Q | No | No | Yes | Yes
2023-10-31 20:49 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-17 | 99 Riverside Ave Unit 910 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV013356Q | No | No | Yes | Yes
2023-10-31 20:50 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-21 | 99 Riverside Ave Unit 911 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV104638Q | No | No | Yes | Yes
2023-10-31 20:52 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HO250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-21 | 99 Riverside Ave Unit 912 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apaertment | Kitchen¦Serial-FV104582Q | No | No | Yes | Yes
2023-10-31 20:54 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-21 | 99 Riverside Ave Unit 913 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV096513Q | No | No | Yes | Yes
2023-10-31 20:56 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-20 | 99 Riverside Ave Unit 914 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV096518Q | No | No | Yes | Yes
2023-10-31 20:58 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-20 | 99 Riverside Ave Unit 915 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV104583Q | No | No | Yes | Yes
2023-10-31 21:00 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-21 | 99 Riverside Ave Unit 916 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV104639Q | No | No | Yes | Yes
2023-10-31 21:03 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-03-10 | 99 Riverside Ave Unit 1001 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV094087Q | No | No | Yes | Yes
2023-10-31 21:05 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-03-10 | 99 Riverside Ave Unit 1002 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV094028Q | No | No | Yes | Yes
2023-10-31 21:07 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-03-14 | 99 Riverside Ave Unit 1003 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV044720Q | No | No | Yes | Yes
2023-10-31 21:09 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-03-10 | 99 Riverside Ave Unit 1004 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV013246Q | No | No | Yes | Yes
2023-11-01 21:13 | ALAN | GILLIGAN | 11296 | 22 hyde st |  | quincy | MA | 2169 | 61729325632 | OWNER/ELECTRICIAN |  | BEKO-PRIR34452SS | Breaker | NO | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-24 | 2023-10-24 | 91 KENWOOD STREET |  | DORCHESTER | MA | 2124 | BREAKER TRIPS IMMEDIATELY UPON ACTIVATION | BEKO | PRIR34452SS |  | KITCHEN | KITCHEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/15435358451
2023-11-03 09:50 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 611 | Kitchen | Yes | No | Yes | No
2023-11-03 09:54 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 614 | Kitchen | Yes | No | Yes | No
2023-11-03 09:55 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 511 | Kitchen | Yes | No | Yes | No
2023-11-03 09:55 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 411 | Kitchen | Yes | No | Yes | No
2023-11-03 09:56 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 311 | Kitchen | Yes | No | Yes | No
2023-11-03 09:56 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 211 | Kitchen | Yes | No | Yes | No
2023-11-03 09:57 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 630 | Kitchen | Yes | No | Yes | No
2023-11-03 09:57 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 638 | Kitchen | Yes | No | Yes | No
2023-11-03 09:57 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 641 | Kitchen | Yes | No | Yes | No
2023-11-03 10:14 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 538 | Kitchen | Yes | No | Yes | No
2023-11-03 10:14 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 541 | Kitchen | Yes | No | Yes | No
2023-11-03 10:15 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 430 | Kitchen | Yes | No | Yes | No
2023-11-03 10:15 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 438 | Kitchen | Yes | No | Yes | No
2023-11-03 10:15 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 441 | Kitchen | Yes | No | Yes | No
2023-11-03 10:15 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 330 | Kitchen | Yes | No | Yes | No
2023-11-03 10:16 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 338 | Kitchen | Yes | No | Yes | No
2023-11-03 10:16 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 341 | Kitchen | Yes | No | Yes | No
2023-11-03 10:16 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 230 | Kitchen | Yes | No | Yes | No
2023-11-03 10:17 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 241 | Kitchen | Yes | No | Yes | No
2023-11-03 10:17 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 141 | Kitchen | Yes | No | Yes | No
2023-11-03 10:17 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 656 | Kitchen | Yes | No | Yes | No
2023-11-03 10:17 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 664 | Kitchen | Yes | No | Yes | No
2023-11-03 10:18 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 555 | Kitchen | Yes | No | Yes | No
2023-11-03 10:18 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 564 | Kitchen | Yes | No | Yes | No
2023-11-03 10:18 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-11-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 455 | Kitchen | Yes | No | Yes | No
2023-11-03 10:19 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-10-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 464 | Kitchen | Yes | No | Yes | No
2023-11-03 10:19 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-10-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 355 | Kitchen | Yes | No | Yes | No
2023-11-03 10:20 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-10-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 356 | Kitchen | Yes | No | Yes | No
2023-11-03 10:20 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-10-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 364 | Kitchen | Yes | No | Yes | No
2023-11-03 10:20 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-10-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 255 | Kitchen | Yes | No | Yes | No
2023-11-03 10:20 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-10-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 256 | Kitchen | Yes | No | Yes | No
2023-11-03 10:21 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-10-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 264 | Kitchen | Yes | No | Yes | No
2023-11-03 10:21 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-10-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 155 | Kitchen | Yes | No | Yes | No
2023-11-03 10:21 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-10-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 156 | Kitchen | Yes | No | Yes | No
2023-11-03 10:21 | D&D Electrical Contractors | D&D Electrical Contractors | 1594 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | Faith Milicevic Assistant Project Manager |  | Siemens Q250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-24 | 2023-10-24 | 40 William St. |  | Wellesley | MA | 2481 | Nuisance tripping | Whirlpool | WEE515SOLS2 |  | Apartment unit 164 | Kitchen | Yes | No | Yes | No
2023-11-03 10:46 | M. | Pupkin | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-02 | 2023-11-03 | 1079 Comm Ave #216 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15443505713
2023-11-03 10:49 | Motti | Electric Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-02 | 2023-11-03 | 1079 Comm Ave #218 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15443527460
2023-11-05 19:18 | David | Ferreira | 23573 | 3 Pine Hill Ave |  | Chelmsford | MA | 1824 | 9789684144 | OWNER |  | 0119952 E82617 | Breaker | NO | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-25 | 2023-09-26 | 3 miles cir. |  | andover | MA | 1810 | We replaced old 3 wire circuit to a brand new 4 wire circuit and new extension cord, together with this new 50a 2pole gfci breaker, and every time customer use the stove it will trip after a little while, cooktop works fine, only stove that she has problems with. | SAMSUNG | NE58K9430SS |  | Single family house | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15451756701
2023-11-06 14:04 | Joe | Silverio | 17118 | 32 Franklin St |  | Lowell | MA | 1854 | 978514900 | Electrician |  | EATON | Breaker | 50 AMP | 15 |  | 2 Pole | Eaton | Residence |  | 2023-11-04 | 2023-10-30 | 84 Winthrop Ave |  | Lowell | MA | 1851 | GFCI tripping after 15-20 minutes with stove burners on and oven preheat | GE oven/stove | JB64fDK9WW |  | Kitchen | kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/15455898882
2023-11-06 16:49 | Christopher | Veliotis | 14765 | 13 Crabapple Dr. |  | Berkley | MA | 2779 | 508-326-6413 | Owner |  | GFTCB240 | Breaker | Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2023-11-01 | 2023-10-26 | 17 Eddy St. |  | Mansfield | MA | 2048 | GFCI breaker protecting a double wall oven having multiple nuisance tripping episodes. Replaced breaker with another GFCI breaker of the same brand with no changes to the nuisance tripping. Wall oven is hard wired and all elements of the branch circuit have been checked and confirmed to be adequate. | General Electric | PTD7000SN5SS | None | Single family dwelling | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15457085302
2023-11-07 13:17 | Jack | Griffin | 418 | 26 Joanna Dr |  | South Yarmouth | MA | 2664 | 978-479-2521 | Owner |  | Square d qo | Breaker | None | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-07 | 2023-08-30 | 81 Seaview |  | Chatham | MA |  | Trips after it reaches temperature. | Thermador | Pods302w/04 |  | House | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15462708210
2023-11-08 12:11 | Thomas | Durkin | 390000000000000 | 3 Russell St no.2 | Russell St | Waltham | MA | 2453 | 17818943713 | press |  | Eaton BR GFTCB250 | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2023-09-04 | 2023-09-01 | 158 Mile Standish Rd |  | Marlborough | MA | 1752 | As soon as oven is turned on the breaker tripped.. | Frigidaire Stove | GCRE3060AF |  | Home | Kitchen- Stove | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15468809612
2023-11-08 19:14 | David | Hamner | 40074 | 187 Longfellow Rd |  | Waltham | MA | 2453 | 617-293-7185 | Owner |  | 0105521E82617 | Breaker | GFI | 50 |  | 2 Pole | Siemens | Residence |  | 2023-11-06 | 2023-10-31 | 20 George Street |  | Belmont | MA | 2478 | When the oven is on only heats up half way and breaker trips. | GE Cafe | CES700P2M3S1 |  | House | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15471537328
2023-11-09 13:10 | Joseph | Fortin | 20860 | 14 Winthrop St |  | Rehoboth | MA | 2769 | 7745658142 | Vice President |  | LB240-G | Breaker | breaker | 40 |  | 2 Pole | Leviton | Residence |  | 2023-10-10 | 2023-10-10 | Madison Residential Development - 1 Green Island Blvd, Worcester, MA 01610 |  | Worcester | MA | 1610 | Every time the oven starts to heat up the breaker trips. | GE | JB645RKSS | none | 168 out of 228 residential apartments | The kitchen range. | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15476000354
2023-11-09 13:41 | Kennith | Sparrow | 20580 | 151 Mystic Ave #2 |  | Medford | MA | 2155 | 781-648-7771 | Owner |  | Eaton CLGF240 | Breaker | plug in | 40 |  | 2 Pole | Eaton | Residence |  | 2023-11-08 | 2023-11-03 | [5 empty] | Tripping over night possible internal electronics | Frigidaire Gallery Stove | GCRI3058AFH | no | 2 Family house | Kitchen Stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/15476206571
2023-11-09 14:00 | Kennith | Sparrow | 20580 | 151 Mystic Ave #2 |  | Medford | MA | 2155 | 7816487771 | Owner |  | Eaton | Breaker | Plug in | 40 |  | 2 Pole | Eaton | Residence |  | 2023-11-08 | 2023-11-03 | 30 Hopkins rd 2nd fl |  | Arlington | MA | 2474 | Tripping over night possible internal electronics | Frigidaire Gallery Stove | GCR13058AFH | no | 2 Family House | Kitchen Stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/15476343094
2023-11-09 17:01 | Joseph | Fortin | 20860 | 14 Winthrop St |  | Rehoboth | MA | 2769 | 7745658142 | Vice President |  | LB240-G | Breaker | breaker | 40 |  | 2 Pole | Leviton | Residence |  | 2023-09-15 | 2023-09-15 | Pinehills 2 - 64 Station Drive |  | Plymouth | MA | 2360 | Every time the oven starts to heat up the breaker trips. | Whirlpool | WEE515S0LS | none | 5 out of 84 residential apartments | The kitchen range. | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15477606939
2023-11-11 10:56 | David | Schwab | 24755 | 18 east line road |  | Vineyard Haven | MA | 2539 | 5086486015 | Owner |  | LB120-DFT | Breaker | Breaker | 20 |  | 1 Pole | Leviton | Residence |  | 2023-11-01 | 2023-11-03 | 6 Vincent way |  | vineyard haven | MA | 2568 | Breaker trips randomly on ground fault | Grundfos | Grundfos CMBE |  | Basement | Grundfos water booster pump | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15485258220
2023-11-13 11:48 | RAY | Ostroski | 16764 | 34 Fardon Rd |  | Billerica | MA | 1862 | 7818380703 | Owner |  | chn240gf | Breaker | na | 40 |  | 1 Pole | Eaton | Residence |  | 2023-11-13 | 2023-11-13 | 7 cardinal way |  | Methuen | MA | 1844 | GFCI does not hold with oven running | Kitchenaid | kose500ess |  | single family | kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15492420521
2023-11-13 11:53 | RAY | Ostroski | 16764 | 34 Fardon Rd |  | Billerica | MA | 1862 | 7818380703 | owner |  | CHN240GF | Breaker | n/a | 40 |  | 2 Pole | Eaton | Residence |  | 2023-11-13 | 2023-11-13 | 5 cardinal way |  | Methuen |  | 1844 | breaker does not hold with oven running | kitchenaid | kose500ess |  | single family | kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15492454623
2023-11-13 11:55 | RAY | Ostroski | 16764 | 34 Fardon Rd |  | Billerica | MA | 1862 | 7818380703 | Owner |  | CHN240GF | Breaker | n/a | 40 |  | 2 Pole | Eaton | Residence |  | 2023-11-13 | 2023-11-13 | 3 cardinal way |  | Methuen | MA | 1844 | breaker does not hold when oven is running | kitchenaid | kose500ess |  | single family | kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15492472693
2023-11-13 11:57 | RAY | Ostroski | 16764 | 34 Fardon Rd |  | Billerica | MA | 1862 | 7818380703 | Owner |  | CHN240GF | Breaker | n/a | 40 |  | 2 Pole | Eaton | Residence |  | 2023-11-13 | 2023-11-13 | 1 cardinal way |  | Methuen | MA | 1844 | breaker does not hold when oven is running | kitchenaid | kose500ess |  | single family | kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15492488502
2023-11-13 18:56 | Jared | Eaton | 1157 | 1240 Broadwa |  | Haverhill | MA | 1832 | 19784207429 | Business owner |  | Siemens QF250A | Breaker | Plug in type | 15 | 50 | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15495364905 | 2023-11-01 | 2023-11-01 | 56 Carter st |  | Newburyport | MA | 1950 | The circuit breaker trips out immediately after it has been switched to the on position. | Wolf | IR36550/S/T | N/A | Single family | Kitchen range | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/15495364919 | https://www.formstack.com/admin/download/file/15495364920
2023-11-14 11:11 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15498786551 | 2023-03-10 | 2023-01-12 | 21 West 2nd St #607 |  | Boston | MA | 2127 | range top would work but once the oven was turned on, the gfci would trip in the process of the oven preheating. breaker only had a 8A load. | Blomberg | 7732187984 21 101506 09 |  | Apartment | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15498786572 | https://www.formstack.com/admin/download/file/15498786574
2023-11-14 11:16 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15498822411 | 2023-03-13 | 2023-01-12 | 21 West 2nd St #603 |  | Boston | MA | 2127 | range top would work but once the oven was turned on, the gfci would trip in the process of the oven preheating. breaker only had a 8A load. | Blomberg | 7732187984 21 101517 |  | Apartment | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15498822424 | https://www.formstack.com/admin/download/file/15498822425
2023-11-14 12:07 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15499193745 | 2023-03-12 | 2023-01-12 | 21 West 2nd St #601 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | 7732187984 22 100138 01 |  | Apartment | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15499193761 | https://www.formstack.com/admin/download/file/15499193762
2023-11-14 12:12 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15499229793 | 2023-03-10 | 2023-01-12 | 21 West 2nd St #511 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | 7732187984 22 100113 01 |  | Apartment | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15499229816 | https://www.formstack.com/admin/download/file/15499229819
2023-11-14 12:19 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15499286636 | 2023-03-10 | 2023-01-12 | 21 West 2nd St #408 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | 7732188007 21 100913 12 |  | Apartment | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15499286649 | https://www.formstack.com/admin/download/file/15499286650
2023-11-14 12:25 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15499324138 | 2023-03-10 | 2023-01-12 | 21 West 2nd St #407 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | 772187984 21 101503 09 |  | Apartment | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15499324151 | https://www.formstack.com/admin/download/file/15499324152
2023-11-14 12:31 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB230 | Breaker | N/A | 30 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15499374801 | 2023-03-12 | 2023-01-12 | 21 West 2nd St #403 |  | Boston | MA | 2127 | The oven would trip the GFCI on the breaker durn the preheat process every time. | GE | JKS3000SN1SS |  | Apartment | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15499374814 | https://www.formstack.com/admin/download/file/15499374815
2023-11-14 12:35 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15499399938 | 2023-03-09 | 2023-01-10 | 21 West 2nd St #401 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | 7732187984 21 101193 09 |  | Apartment | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15499399951 | https://www.formstack.com/admin/download/file/15499399952
2023-11-14 12:39 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15499428342 | 2023-03-14 | 2023-01-12 | 21 West 2nd St #306 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | 7732188007 21 100903 12 |  | Apartment | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15499428355 | https://www.formstack.com/admin/download/file/15499428356
2023-11-14 12:43 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15499456611 | 2023-03-09 | 2023-01-12 | 21 West 2nd St #304 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | 7732188007 22 100253 05 |  | Apartment | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15499456624 | https://www.formstack.com/admin/download/file/15499456625
2023-11-14 13:10 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15499646813 | 2023-03-04 | 2023-01-12 | 21 West 2nd St #309 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | 7732187984 21 101518 09 |  | Apartment | Kitchen appliance | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15499646826 | https://www.formstack.com/admin/download/file/15499646827
2023-11-14 13:15 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB230 | Breaker | N/A | 30 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15499682702 | 2023-03-14 | 2023-01-12 | 21 West 2nd St #303 |  | Boston | MA | 2127 | The oven would trip the GFCI in the process of the preheating of the oven each time. | GE | JKS3000SN1SS |  | Apartment | Kitchen appliance | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15499682715 | https://www.formstack.com/admin/download/file/15499682716
2023-11-14 13:19 | Justin | Allen | 54522 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15499710127 | 2023-03-16 | 2023-01-12 | 21 West 2nd St #301 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | 7732187984 22 100061 01 |  | Apartment | Kitchen appliance | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15499710140 | https://www.formstack.com/admin/download/file/15499710141
2023-11-14 13:58 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15499986816 | 2023-03-14 | 2023-01-12 | 21 West 2nd St #211 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | 772187984 21 101510 09 |  | Apartment | Kitchen appliance | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15499986829
2023-11-14 14:05 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15500033108 | 2023-03-11 | 2023-01-12 | 21 West 2nd St #209 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | 7732187984 21 101511 09 |  | Apartment | kITCHEN APPLIANCE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15500033121 | https://www.formstack.com/admin/download/file/15500033122
2023-11-14 14:09 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15500061669 | 2023-03-10 | 2023-01-12 | 21 West 2nd St #208 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | 7732138007 22 100271 05 |  | Apartment | Kitchen appliance | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15500061683 | https://www.formstack.com/admin/download/file/15500061684
2023-11-14 14:19 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15500134487 | 2023-03-10 | 2023-01-12 | 21 West 2nd St #204 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | BERU30422ss |  | Apartment | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15500134500 | https://www.formstack.com/admin/download/file/15500134501
2023-11-14 14:27 | Justin | Allen | 54524 | 372 w greenville rd |  | Scituate | RI | 2857 | 401-258-7240 | Journeyman |  | Eaton GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15500190873 | 2023-03-16 | 2023-01-12 | 21 West 2nd St #201 |  | Boston | MA | 2127 | The range top would work fine but the oven would trip the GFI durn the preheating of the oven at only a 8A load. | Blomberg | 7732187984 21 101496 09 |  | Apartment | Kitchen appliance | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15500190886 | https://www.formstack.com/admin/download/file/15500190887
2023-11-14 20:37 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-03-10 | 99 Riverside Ave Unit 1005 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126299Q | No | No | Yes | Yes
2023-11-14 20:38 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-03-10 | 99 Riverside Ave Unit 1006 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126320Q | No | No | Yes | Yes
2023-11-14 20:40 | sean | Matthies | 23034 | 31 Norman Avenue |  | West Bridgewater | MA | 2379 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-03-13 | 99 Riverside Ave Unit 1007 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV044721Q | No | No | Yes | Yes
2023-11-14 20:42 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-13 | 99 Riverside Ave Unit 1008 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV117777Q | No | No | Yes | Yes
2023-11-14 20:43 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-13 | 99 Riverside Ave Unit 1009 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV094015Q | No | No | Yes | Yes
2023-11-14 20:45 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-12 | 2023-03-14 | 99 Riverside Ave Unit 1010 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV093937Q | No | No | Yes | Yes
2023-11-14 20:47 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-15 | 99 Riverside Ave Unit 1013 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV094071Q | No | No | Yes | Yes
2023-11-14 20:49 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-15 | 99 Riverside Ave Unit 1014 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV135358Q | No | No | Yes | Yes
2023-11-14 20:51 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-15 | 99 Riverside Ave Unit 1015 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | Ge | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV135355Q | No | No | Yes | Yes
2023-11-14 20:54 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-03-06 | 99 Riverside Ave Unit 1102 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JSB60RK9SS |  | Apartment | Kitchen¦Serial-DV126368Q | No | No | Yes | Yes
2023-11-14 20:56 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-03-06 | 99 Riverside Ave Unit 1103 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9ss |  | Apartment | Kitchen¦Serial-DV1263J8Q | No | No | Yes | Yes
2023-11-14 20:57 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-03-06 | 99 Riverside Ave Unit 1104 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126313Q | No | No | Yes | Yes
2023-11-14 20:59 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-03-06 | 99 Riverside Ave Unit 1105 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126354Q | No | No | Yes | Yes
2023-11-14 21:01 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-03-06 | 99 Riverside Ave Unit 1106 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126369Q | No | No | Yes | Yes
2023-11-14 21:02 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman Electrician |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-02-01 | 99 Riverside Ave Unit 1107 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | APartment | Kitchen¦Serial-AV127528Q | No | No | Yes | Yes
2023-11-15 07:39 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President / PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the Electric Stove will start to heat up but after a few minutes will trip the GFCI circuit ¦breaker. | GE | GE JB645RK9SS | N/A | Kitchen | This is a common issue in all (103) Independent Living Apartments. This applies to the Kitchen Electric Stove only in these Independent Living Apartments.¦¦The other residential appliances in the Independent Living Apartments do not appear to have this same GFCI tripping issue. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15504100090
2023-11-15 09:00 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 1 Unit A Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504380671
2023-11-15 09:03 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 1 Unit B Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504397967
2023-11-15 09:06 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 1 Unit C Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504411009
2023-11-15 09:09 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 1 Unit D Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504425236
2023-11-15 09:16 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 2 Unit A Vynebrook Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504456994
2023-11-15 09:19 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 2 Unit B Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504469845
2023-11-15 09:22 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 2 Unit C Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504487075
2023-11-15 09:25 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 2 Unit D Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504501368
2023-11-15 09:30 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 3 Unit A Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504524119
2023-11-15 09:32 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 3 Unit B Vynebooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504535369
2023-11-15 09:33 | Chris | Stevens | 2665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 3 Unit C Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504545432
2023-11-15 09:35 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 3, Unit D Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504553686
2023-11-15 09:38 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 4, Unit A Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504572044
2023-11-15 09:40 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 4, Unit B Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504581810
2023-11-15 09:42 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 4, Unit C Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504591108
2023-11-15 09:44 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 4, Unit D Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504600364
2023-11-15 09:47 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 5, Unit A Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504615088
2023-11-15 09:48 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 5, Unit B Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504678681
2023-11-15 09:50 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 5, Unit C Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504688893
2023-11-15 09:52 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 5, Unit D Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504698631
2023-11-15 09:56 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 7, Unit A Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504722870
2023-11-15 10:00 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 7, Unit B Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504743226
2023-11-15 10:01 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 7, Unit C Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504752961
2023-11-15 10:03 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 7, Unit D Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504761142
2023-11-15 10:06 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 8, Unit A Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504778300
2023-11-15 10:08 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 8, Unit B Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504794120
2023-11-15 10:10 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 8, Unit C Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504805324
2023-11-15 10:12 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 8, Unit D Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504814647
2023-11-15 10:15 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 9, Unit A Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504833066
2023-11-15 10:16 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 9, Unit B Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504843226
2023-11-15 10:18 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 9, Unit C Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504853681
2023-11-15 10:20 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 9, Unit D Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504864167
2023-11-15 10:22 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 10, Unit A Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | Yes | No | Yes |  | https://www.formstack.com/admin/download/file/15504879849
2023-11-15 10:24 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 10, Unit B Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504892341
2023-11-15 10:25 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 10, Unit C Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504903108
2023-11-15 10:27 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 10, Unit D Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504914374
2023-11-15 10:30 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 11, Unit A Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504931461
2023-11-15 10:31 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 11, Unit B Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504942388
2023-11-15 10:33 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 11, Unit C Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504951097
2023-11-15 10:35 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 11, Unit D Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504960310
2023-11-15 10:37 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 12, Unit A Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504975165
2023-11-15 10:38 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 12, Unit B Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504984551
2023-11-15 10:40 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 12, Unit C Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15504992749
2023-11-15 10:41 | Chris | Stevens | 20665 | PO Box 1101 |  | Hanson | MA | 2341 | 7815340433 | Partner |  | Siemens, QF250a | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2023-10-04 | 2023-10-04 | Building 12, Unit D Vynebrooke Village |  | Lexington | MA | 2421 | The stove trips right away when the stove is turned on. Tried resetting the CB many times, but it will not hold. | Peerless-Premier | EAKL0HOP |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15505003041
2023-11-15 10:42 | John | Vespa | 17144 | 250 Milton St |  | Dedham | MA | 2026 | 617 325 1151 | Owner |  | QBGFT2050 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2023-08-21 | 2023-07-26 | 20 Woodlawn Rd |  | Boston | MA | 2130 | Induction stove nuisance tripping | Bertazonni | PRD3041NMXV |  | single family | kitchen/stove | Yes | No | Yes | No
2023-11-15 11:30 | John | Vespa | 17144 | 250 Milton st |  | Dedham | MA | 2026 | 617 325 1151 | Owner |  | QF250A | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-13 | 2023-05-10 | 211 Melrose st |  | Newton | MA | 2466 | Stove nuisance tripping | Bosch | HIIP057U |  | Single Family | Kitchen/Stove | Yes | No | Yes | No
2023-11-15 11:40 | William | Harland | 17432 | PO Box |  | Littleton | MA | 01460-0094 | (978) 486-8154 | President |  | GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15505404194 | 2023-10-25 | 2023-10-25 | 32 Lake Warren Drive |  | Littleton | MA | 1460 | GFCI breaker tripped within 90 seconds upon energizing. Regular breaker installed and stove run for 3 hours in an attempt to clear out possible contaminants. New GFCI breaker reinstalled and tripped again within 10 minutes. Regular breaker reinstalled and Inspector of Wires notified. (He will get a copy of this report) | Electrolux Home Products Inc | GCRI3058AFH |  | Single family dwelling | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/15505404207 | https://www.formstack.com/admin/download/file/15505404208
2023-11-15 14:06 | Chris | Polny | 11660 | 325 Hopping Brook |  | Holliston | MA | 1746 | 7742178986 | VP Electrical Operations |  | BRLAFGF | Breaker | na | 20 |  | 1 Pole | Eaton | Residence |  | 2023-08-09 | 2018-07-09 | [5 empty] | Fridge has been tripping breaker repeatedly, clients have had to throw food out multiple times due to this. Appliance company tested fridge and found no issues. | Equipment Manufacturer* Samsung | RS22HDHPNSR |  | Single | Kitchen Fridge | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15506396238
2023-11-16 18:06 | William | McGrath | 10999 | 916 Pleasant Street | Suite 20 | Norwood | MA | 2062 | 781-769-2747 | Master Electrician |  | GETHQL2150GFT | Breaker | 0 | 50 |  | 2 Pole | ABB | Residence |  | 2023-10-09 | 2023-10-09 | 7 KONET RD |  | FOXBOROUGH | MA | 2035 | Cook top trips GFI breaker as soon as its energized. Checked all connections and grounding. All OK¦Tried swapping GFI breaker with different breaker, but had the same issue. Had manufacturer come out to do service call and they couldn't find any issues. They installed another replacement cook top, same brand and model and that also trips breaker. | MIELE | KM6370 |  | Single Family Kitchen | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15513855111
2023-11-17 09:05 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #210 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15516143535
2023-11-17 09:08 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #215 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 09:09 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #321 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 09:10 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #603 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 09:11 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #602 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15516174619
2023-11-17 09:12 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #520 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 09:14 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #225 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 09:15 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #607 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 09:16 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #403 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 11:10 | Joshua | Leclair | 22548 | 9 Kidder Rd | Suite C | CHELMSFORD | MA | 01824-3398 | 9782564845 | Master Electrician / Owner |  | QF240AP | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-11-17 | 2023-10-26 | 24 Terrence Ave |  | Clinton | MA | 1510 | Breaker trips when oven is in use.¦ | GE CAFE RANGE | CHS900P2M681 | none | Single Family | Kitchen | No | No | No | No
2023-11-17 13:26 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #624 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:26 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #623 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:27 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #622 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:28 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #621 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:29 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #620 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:30 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #619 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:31 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #618 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:31 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #617 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:33 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #616 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:34 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #615 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:34 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #614 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:35 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #613 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:36 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #612 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:36 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #611 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:38 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #610 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:38 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #609 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:39 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #608 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:42 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #606 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:43 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #605 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:44 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #604 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 13:44 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #601 466 River Str. |  | Mattapan | MA | 2126 | WHEN GE RANGE TURNS ON, THE EQUIPMENT TRIPS THE GFCI BREAKER INSTALLED | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-17 14:41 | Chris | Polny | 11660 | 325 Hopping Brook |  | Holliston | MA | 1746 | 7742178986 | VP Electrical Operations |  | GFTCB240 | Breaker | NA | 40 |  | 2 Pole | Eaton | Residence |  | 2023-11-16 | 2023-11-16 | 39 Nadeau Dr |  | Wrentham | MA |  | Breaker tripping immediately after running new circuit to existng stove | Whirlpool | WFE540H0ES0 |  | Single family | Only kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/15518220664
2023-11-18 09:28 | David | Briley | 23397 | 135 ELM ST | 2 | AMESBURY | MA | 1913 | 6179215506 | Owner |  | Frigidaire | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-15 | 2023-10-01 | [5 empty] | GFCI breaker constantly trips when oven temp is over 400 degrees | Frigidaire | GCFE3060BFA |  | Single Family | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15520817501
2023-11-20 07:35 | Nick | Taormina | 14918 | 5 Heritage Way |  | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street |  | Beverly | MA | 1915 | Breaker trips with oven use. Has occurred continuously since installation. Has been reset multiple times and each time it needs to be reset, it takes multiple attempts for breaker to hold. | GE | JB645RKSS | NA | Apartment | Kitchen | Yes | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15526223399
2023-11-20 07:51 | Nick | Taormina | 14918 | 5 Heritage Way |  | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street |  | Beverly | MA | 1915 | Breaker trips with oven use. Has occurred continuously since installation. Has been reset multiple times and each time it needs to be reset, it takes multiple attempts for breaker to hold. | GE | JB645RKSS | NA | Apartment | Kitchen | Yes | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15526262373
2023-11-20 08:01 | Nick | Taormina | 14918 | Roy Spittle Electric | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | NA | 50 | NA | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 203 |  | Beverly | MA | 1915 | Multiple trips during preheat of oven on multiple occasions. | GE | JB645RKSS | NA | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15526289406
2023-11-20 08:05 | Nick | Taormina | 14918 | Roy Spittle Electric | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | NA | 50 | NA | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 213 |  | Beverly | MA | 1915 | Multiple trips during preheat of oven on multiple occasions. | GE | JB645RKSS | NA | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15526300928
2023-11-20 08:10 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1915 | 978-283-2299 | President |  | GFTCB250 | Breaker | NA | 50 | NA | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 213 |  | Beverly | MA | 1915 | Multiple trips during preheat on multiple occasions with oven use. | GE | JB645RKSS | NA | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15526316013
2023-11-20 08:31 | Nick | Taormina | 14918 | Roy Spittle Associates |  | Beverly | MA | 1915 | 978-283-2299 | President |  | GFTCB250 | Breaker | NA | 50 | NA | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 204 |  | Beverly | MA | 1915 | Multiple trips when Oven is preheating on multiple occasions. | GE | JB645RKSS | NA | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15526384459
2023-11-20 09:05 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 303 |  | Gloucester | MA | 1915 | Multiple trips with oven use on multiple occasions | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15526516177
2023-11-20 09:14 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 149 Rantoul Street Unit 307 |  | Beverly | MA | 1915 | Multiple trips on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15526555390
2023-11-20 09:22 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | NA | 50 | NA | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street |  | Beverly | MA | 1915 | Breaker tripped multiple times during oven use on multiple occasions since installation | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 09:28 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | NA | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 309 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions with oven use during preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 09:42 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 312 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 09:49 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | NA | 50 | NA | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul street Unit 313 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | NA | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 09:55 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 315 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions with oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 10:01 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul street Unit 301 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 10:06 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 316 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions with oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 10:24 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 318 |  | Beverly | MA | 1915 | Breaker tripped multiples on multiple occasions with oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 10:29 | Motti Electric Co | Pupkin | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Avei #211 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15526952841
2023-11-20 10:31 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Avei #212 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15526964371
2023-11-20 10:32 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Avei #212 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15526970615
2023-11-20 10:33 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Avei #213 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15526980170
2023-11-20 10:34 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 321 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions when oven preheating | Ge | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 10:34 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Avei #214 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15526987054
2023-11-20 10:37 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Avei #215 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527001577
2023-11-20 10:37 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Avei #218 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527005910
2023-11-20 10:37 | Nick | Taormina | 14918 | Roy Spittle associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 322 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 10:38 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Avei #219 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527009300
2023-11-20 10:39 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #220 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527014374
2023-11-20 10:39 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #221 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527017269
2023-11-20 10:40 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #222 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527022114
2023-11-20 10:41 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #311 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527025793
2023-11-20 10:41 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #312 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527029110
2023-11-20 10:41 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucest | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 323 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 10:42 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #313 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527032582
2023-11-20 10:42 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #314 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527034297
2023-11-20 10:43 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #315 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527036294
2023-11-20 10:43 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #316 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527038238
2023-11-20 10:43 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #317 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527040049
2023-11-20 10:44 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #318 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527041764
2023-11-20 10:44 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #319 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527043520
2023-11-20 10:44 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #320 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527045525
2023-11-20 10:45 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #321 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527047306
2023-11-20 10:45 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #322 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527050614
2023-11-20 10:46 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #412 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527056118
2023-11-20 10:46 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #413 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527058294
2023-11-20 10:47 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #414 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527062298
2023-11-20 10:47 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #415 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527064443
2023-11-20 10:48 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #416 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527065997
2023-11-20 10:48 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #417 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527068001
2023-11-20 10:48 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #418 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527070354
2023-11-20 10:48 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #419 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527071947
2023-11-20 10:49 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #420 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527073428
2023-11-20 10:49 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #421 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527075104
2023-11-20 10:49 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #422 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527076334
2023-11-20 10:50 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #514 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527082778
2023-11-20 10:50 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #515 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527085053
2023-11-20 10:51 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #516 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527086326
2023-11-20 10:51 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #517 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527088250
2023-11-20 10:51 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #518 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527090955
2023-11-20 10:52 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #519 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527092651
2023-11-20 10:52 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #520 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527094190
2023-11-20 10:52 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #521 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527095523
2023-11-20 10:52 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #522 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527096836
2023-11-20 10:53 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #523 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527097906
2023-11-20 10:53 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #524 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527099109
2023-11-20 10:53 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #525 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527101098
2023-11-20 10:53 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #526 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527101854
2023-11-20 10:54 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #527 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527104214
2023-11-20 10:54 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #528 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527108203
2023-11-20 10:55 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-15 | 2023-11-15 | 1079 Comm Ave #529 |  | Boston | MA | 2215 | GFCI trips when oven turns on. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527109040
2023-11-20 11:27 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 501 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 11:30 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-282-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 503 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 11:35 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 1 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 504 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 11:39 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 505 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 11:42 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 511 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 11:46 | Nick | Taormina | 14918 | Roy Spittle Associate | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-11-20 | 140 Rantoul Street Unit 513 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15527433827
2023-11-20 11:50 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | NA | 15 |  | 1 Pole | ABB | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 501 |  | Beverly | MA | 1930 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 11:53 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street -email receipt test |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 11:58 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 506 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 12:03 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul StreetUnit 509 |  | Beverly | MA | 1915 | Breakers tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 12:06 | Nick | Taormina | 14918 | Roy Spittle Associate | 5 Heritage Way | Gloucest | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 512 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 12:10 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 1 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 516 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 14:30 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 1 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 516 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 14:37 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | ABB | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 604 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 14:41 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 605 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 14:45 | Nick | Taormina | 14918 | Roy Spittle Associate | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | Gft | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 606 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 14:52 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 607 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 14:58 | Nick | Taormina | 14918 | Roy Spittle Associate | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 608 |  | Beverly | MA | 1930 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 15:05 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 609 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 15:08 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 610 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 15:12 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 610 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 15:16 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 101 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15528759261
2023-11-20 15:19 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 105 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 16:22 | Nick | Taormina | 14918 | Roy spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Unit 322 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 16:23 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 105 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 16:26 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 421 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | Yes | Yes | No
2023-11-20 16:30 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-07-01 | 140 Rantoul Street Unit 410 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-20 17:06 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Electrical Contractor |  | Eaton | Breaker | none | 40 |  | 2 Pole | Eaton | Residence |  | 2023-11-10 | 2023-11-09 | [5 empty] | Installed a 2 pole 40 amp gfci breaker on the wall oven. After the oven reaches 100 degrees the breaker trips. | Kitchenaid | KOCE507ESS04 |  | Single family | Kitchen. | No | Yes | Yes | No
2023-11-20 22:09 | Frederic | Hartwell | 12019 | 60 N. Whitney St. |  | Amherst | MA | 1002 | (413) 478-9432 | President |  | General Electric THQL2150GFT | Breaker | none | 50 |  | 2 Pole | Industrial | Residence |  | 2023-08-28 | 2023-08-14 | 26 Davenport Way |  | Greenfield | MA | 1301 | The GFCI breaker was reset and remained energized with the range turned on but no heating el-ements active. The four induction cooktop positions were reported by the owners as functioning as expected, and appeared as such during the inspection. Energizing the heating element in the range, however, resulted in the breaker tripping after 58 seconds. The owners reported this be-havior had been constant, with the breaker tripping over a range of relatively short intervals, since they moved in and began using the range. The owners reported they had complained to the appli-ance vendor, whose response that ""the AFCI breaker was defective"" primarily revealed that the appliance vendor was unqualified to comment.¦¦The inspection proceeded to open the electrical connection compartment to check termination and cord-connection details. The equipment grounding connection, as well as the other connec-tions, were all properly landed and torqued. The cord connection used a standard connector that had smooth metal flanges that bottomed on the enclosure interior. The connector engaged the ca-ble jacket very close to its end; out of an abundance of caution the cable jacket was advanced and re-secured about â…œ-inch into the compartment to avoid any future problem. The branch cir-cuit is wired with 75Â°C SER Aluminum 4-wire cable that includes an 8 AWG Aluminum equip-ment grounding conductor. Both the circuit breaker and the terminating receptacle were/are listed and marked for the use of 75Â°C terminations, which for aluminum conductors is a required quali-fication given the 50A circuit rating, and there was no evidence of damage to the cable. The equipment grounding conductor was properly terminated in the panelboard. The equipment grounding return path was therefore judged to meet all NEC/MEC requirements. Under Rule 11, this finding together with the nuisance tripping qualifies the application to excuse compliance with GFCI requirements. Accordingly, the GFCI circuit breaker was replaced with a convention-al circuit breaker of the same manufacture, also marked for 75Â°C terminations. The range was re-turned to service, and was operating normally as the inspection concluded. ¦¦NOTE: THIS FORM DOES NOT ALLOW THE SELECTION OF GENERAL ELECTRIC AS THE GFCI MANUFACTURER. THAT FIRM IS A MAJOR MANUFACTURER OF GFCI CIRCUIT BREAKERS, AND THIS IS A MAJOR DEFICIENCY. ¦ | Frigidaire | GCR13058AF |  | Single Family House | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15530575317
2023-11-22 10:09 | Jacqueline | Gorman | 17235 | 380 Turnpike Street |  | South Easton | MA | 2346 | 508-643-0334 | Owner |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-15 | 194 Rumford Avenue UNIT #1 |  | Mansfield | MA | 2048 | Nuisance tripping. | Frigidaire | FCFE3062AB |  | Single Family Dwelling | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15537942492
2023-11-22 10:15 | Jacqueline | Gorman | 17235 | 380 Turnpike Street |  | South Easton | MA | 2375 | 508-643-0334 | Owner |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-15 | 194 Rumford Avenue UNIT #2 |  | Mansfield | MA | 2048 | Nuisance tripping | Frigidaire | FCFE3062AB |  | Single family dwelling | Kitchen | No | No | Yes | No
2023-11-22 10:18 | Jacqueline | Gorman | 17235 | 380 Turnpike Street |  | South Easton | MA | 2375 | 508-643-0334 | Onwer |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-15 | 194 Rumford Avenue UNIT #3 |  | Mansfield | MA | 2048 | Nuisance tripping | Frigidaire | FCFE3062AB |  | single family dwelling | kitchen | No | No | Yes | No
2023-11-22 10:20 | Jacqueline | Gorman | 17235 | 380 Turnpike Street |  | South Easton | MA | 2375 | 5086430334 | Onwer |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-15 | 194 Rumford Avenue UNIT #4 |  | Mansfield | MA | 2048 | Nuisance tripping | Frigidaire | FCFE3062AB |  | single family dwelling | kitchen | No | No | Yes | No
2023-11-22 10:23 | Jacqueline | Gorman | 17235 | 380 Turnpike Street |  | South Easton | MA | 2375 | 5086430334 | Owner |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-15 | 194 Rumford Avenue UNIT #5 |  | Mansfield | MA | 2048 | Nuisance tripping | Frigidaire | FCFE3062AB |  | single family dwelling | kitchen | No | No | Yes | No
2023-11-22 10:24 | Jacqueline | Gorman | 17235 | 380 Turnpike Street |  | South Easton | MA | 2375 | 5086430334 | Owner |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-15 | 194 Rumford Avenue UNIT #6 |  | Mansfield | MA | 2048 | Nuisance tripping | Frigidaire | FCFE3062AB |  | single family dwelling | kitchen | No | No | Yes | No
2023-11-22 10:27 | Jacqueline | Gorman | 17235 | 380 Turnpike Street |  | South Easton | MA | 2375 | 5086430334 | Onwer |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-15 | 194 Rumford Avenue UNIT #7 |  | Mansfield | MA | 2048 | Nuisance tripping | Frigidaire | FCFE3062AB |  | single family dwelling | kitchen | No | No | Yes | No
2023-11-22 10:29 | Jacqueline | Gorman | 17235 | 380 Turnpike Street |  | South Easton | MA | 2375 | 5086430334 | Owner |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-15 | 194 Rumford Avenue UNIT #7 |  | Mansfield | MA | 2048 | Nuisance tripping | Frigidaire | FCFE3062AB |  | single family dwelling | kitchen | No | No | Yes | No
2023-11-22 10:31 | Jacqueline | Gorman | 17235 | 380 Turnpike Street |  | South Easton | MA | 2375 | 5086430334 | Onwer |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-15 | 194 Rumford Avenue UNIT #8 |  | Mansfield | MA | 2048 | Nuisance tripping | Frigidaire | FCFE3062AB |  | single family dwelling | kitchen | No | No | Yes | No
2023-11-27 12:17 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemends/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit 201187 Sumner St. |  | Boston | MA | 2128 | When Range Turns on, the equipment trips the Breaker installed. | Premier | ECK001OP01 |  | Apartment | It is in the Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15555782705
2023-11-27 16:01 | Nick | Taormina | 14918 | 5 Heritage Way |  | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 507 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions with oven use during preheat. | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-27 16:06 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 106 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-27 16:09 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 108 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-27 16:15 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucestershire | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | ABB | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 208 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-27 16:18 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 209 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15559764091
2023-11-27 16:22 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 212 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions on oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-27 16:26 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 214 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-27 16:30 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 217 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15559845979
2023-11-27 16:36 | Nick | Taormina | 14918 | Roy Spittle | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 218 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Breaker tripped multiple times on multiple occasions during oven preheat | Yes | No | Yes | No
2023-11-28 07:27 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | UNIT#202 187 Sumner St. |  | Boston | MA | 2128 | When the Range turns on the equipment trips the GFCI breaker installed | Premier | GT025317Q |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15562563621
2023-11-28 08:33 | Ryan | LaBrache | 22042 | 1 Summer Street |  | Watertown | MA | 2472 | 617-924-8866 | Owner |  | GFTCB230 | Breaker | Stabin | 30 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2022-11-01 | 20 Malden St |  | Watertown | MA | 2472 | Dual Fuel Oven would only run for 20min | G.E. | C2S900P4M1W2 |  | Single Family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15562792663
2023-11-28 10:27 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #218 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-28 10:29 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #408 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-28 10:30 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #410 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-28 10:34 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #422 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-28 10:35 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #425 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-28 10:39 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #528 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-28 10:40 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #527 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-28 10:41 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #526 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-28 10:42 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | breaker | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #525 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-11-28 12:03 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | OWNER |  | AD-910 | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-03 | 2023-08-01 | 181 EAST ROAD |  | ALFORD | MA |  | Breaker trips after one minute of usage. | Frigidaire | FCFE2425AS |  | Residence apartment over garage. | Kitchen | No | No | No | No
2023-11-28 12:24 | ANDREW | GALLIONE | 22639 | 10 RAINBOW TER | UNIT F | Danvers | MA | 1923 | 9789980414 | OWNER |  | GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-27 | 2023-11-27 | 30 Crystal Drive |  | Stoneham | MA | 2180 | New construction home with all new wiring. 6/3 Romex branch circuit ran for double oven. Upon installation and wiring GFCI breaker tripped immediately. Ground path was verified and was determined not field wiring faults exist. | Thermador | PO302W/03 |  | 1 Family Dwelling | Kitchen. Branch circuits is dedicated for ovens | No | No | No | No | https://www.formstack.com/admin/download/file/15564269676 | https://www.formstack.com/admin/download/file/15564269677
2023-11-28 12:44 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | OWNER |  | SQUARE D HOMELINE AD-910 | Breaker | N/A | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-10 | 2023-10-23 | 209 SHERWOOD DRIVE |  | BECKET | MA |  | Would trip after some time of dryer use even with jumper removal. | Samsung | DV48H7400EW/A2 |  | Single Family | Laundry Room | No | No | No | No
2023-11-28 12:50 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | OWNER |  | SQUARE D QO230 | Breaker | N/A | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-09 | 2023-11-09 | 17 STEVENS LAKE ROAD |  | MONTEREY | MA |  | Breaker would not hold, kept tripping. | WOLF | DF30450S/P/LP |  | Single Family | Kitchen | No | No | No | No
2023-11-28 13:01 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | Owner |  | DP CH TAN | Breaker | N/A | 30 |  | 2 Pole | Eaton | Residence |  | 2023-08-31 | 2023-08-31 | 9 HERON POINT ROAD |  | MONTEREY | MA |  | Would not hold, kept tripping. | WOLF | SO30TM/S/TH |  | Single Family | Kitchen | No | No | No | No
2023-11-28 13:10 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | Owner |  | SQ-D HO 230 | Breaker | N/A | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2023-04-20 | 2023-04-24 | 330 LIESURE LEE ROAD |  | LEE | MA |  | Would not hold, kept tripping. | WHIRLPOOL | WOS51EC7HS |  | Single Family | Kitchen | No | No | No | No
2023-11-28 13:13 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | Owner |  | SQ-D HO 240 | Breaker | N/A | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2023-04-20 | 2023-04-24 | 330 LEISURE LEE ROAD |  | LEE | MA |  | Would not hold, kept tripping. | BOSCH | HDI8056U |  | Single Family | Kitchen | No | No | No | No
2023-11-28 13:26 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | Owner |  | ITE 30 | Breaker | n/a | 30 | n/a | 2 Pole | Siemens | Residence |  | 2023-06-05 | 2023-06-09 | 857 EAST STREET |  | LENOX | MA |  | Breaker does not hold, kept tripping. | GE | PHP7030DTBB |  | Single Family | Kitchen | No | No | No | No
2023-11-28 13:29 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | Owner |  | ITE 30 | Breaker | N/A | 30 |  | 2 Pole | Siemens | Residence |  | 2023-06-05 | 2023-06-09 | 857 EAST STREET |  | LENOX | MA |  | Breaker does not hold, kept tripping. | GE | JKD5000DNBB |  | Single Family | Kitchen | No | No | No | No
2023-11-28 15:53 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 219 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat¦ | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-28 15:57 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 221 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-28 16:05 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 222 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheating | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-28 16:13 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage way | Gloucester | MA | 1930 | 978-283-2399 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 223 |  | Beverly | MA | 1930 | Kitchen | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-28 16:17 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-07-01 | 140 Rantoul Street Unit 224 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-11-29 08:41 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #203 187 Sumner St. |  | Boston | MA | 2128 | When The Range turns on the equipment trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569076093
2023-11-29 08:44 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #205 187 Sumner St. |  | Boston | MA | 2128 | When the range turns on the equipment trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569090592
2023-11-29 08:48 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #301 187 Sumner St |  | Boston | MA | 2128 | When the range turns on the equipment trips the GFCI breaker installed | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569108050
2023-11-29 08:52 | Paul | Gray | 17521 | 39 Johnston Rd |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #302 187 Sumner St. |  | Boston | MA | 2128 | When the range turns on the equipment trips the GFCI breaker installed. | Premier | ECK100OP01 |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569122993
2023-11-29 10:21 | Paul | Gray | 17521 | 39 Johnston Rd |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #303 187 Sumner St. |  | Boston | MA | 2128 | When the range turns on the equipment trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569639446
2023-11-29 10:24 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #304 187 Sumner St |  | Boston | MA | 2128 | When the range turns on the equipment trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569660225
2023-11-29 10:27 | Paul | Gray | 17521 | 39 Johnston Rd |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #306 187 Sumner St. |  | Boston | MA | 2128 | When the range is turned on it trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569677665
2023-11-29 10:30 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #401 187 Sumner St. |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | Premier | ECK100OP01 |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569699248
2023-11-29 10:33 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #402 187 Sumner St |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed | Premier | ECK100OP01 |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569716747
2023-11-29 10:35 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #403 187 Sumner St. |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569733252
2023-11-29 10:38 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MD | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #405 187 Sumner St. |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569753592
2023-11-29 10:42 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #406 187 Sumner St. |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569777249
2023-11-29 10:55 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #501 187 Sumner St |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | Premier | ECK100OP01 |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569869384
2023-11-29 11:08 | Paul | Gray | 17521 | 39 Johnston Rd |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 1 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #501 187 Sumner St |  | Boston | MA | 2128 | When the range is turned on, the equipment trips the GFCI breaker installed. | Premier | ECK100OP01 |  | Apartment | Kitchen unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15569956941
2023-11-29 17:12 | Aaron | Richards | 20822 | 34 Favorite Ln |  | East Longmeadow | MA | 1028 | 413-896-9295 | owners |  | Cutler Hammer 2 pole 40 & 50 | Breaker | none | 40 |  | 2 Pole | Eaton | Residence |  | 2023-11-28 | 2023-11-23 | [5 empty] | Range & oven both trip within 1 minute of preheating. | Eaton | GFC TB250 |  | New House | Kitchen Appliance | Yes | No | No | No | https://www.formstack.com/admin/download/file/15572657276
2023-11-29 17:16 | Aaron | Richards | 20822 | 34 Favorite Lane |  | East Longmeadow | MA | 1028 | 413-896-9295 | owner |  | Cutler Hammer 2 pole 40 & 50 | Breaker | none | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15572679850 | 2023-11-28 | 2023-11-23 | [5 empty] | Range & oven both trip within 1 minute of preheating. | Eaton | GFC TB240 |  | New House | Kitchen Appliance | Yes | No | No | No | https://www.formstack.com/admin/download/file/15572679862
2023-11-29 17:22 | Aaron | Richards | 20822 | 34 Favorite Lane |  | East Longmeadow | MA | 1028 | 413-896-9295 | owner |  | Cutler Hammer 2 pole 50 | Breaker | none | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15572713518 | 2023-11-28 | 2023-11-23 | [5 empty] | range trips within 1 minute of preheating. | Frigidaire | GCFE 3060BFA | none | New House | Kitchen Appliance (range) | Yes | No | No | No | https://www.formstack.com/admin/download/file/15572713531
2023-11-29 17:24 | Aaron | Richards | 20822 | 34 Favorite Lane |  | East Longmeadow | MA | 1028 | 413-896-9295 | owner |  | Cutler Hammer 2 pole 40 | Breaker | none | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15572726378 | 2023-11-28 | 2023-11-23 | [5 empty] | micro/oven trips within 1 minute of preheating. | Frigidaire | GCWM 3067AFB | none | New House | Kitchen Appliance (micro/oven) | Yes | No | No | No | https://www.formstack.com/admin/download/file/15572726391
2023-11-30 07:46 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #502 |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | Premier | ECK100OP01 |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15575014230
2023-11-30 07:50 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #503 187 Sumner St. |  | Boston | MA | 2128 | When the range turns on the equipment trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15575025581
2023-11-30 07:53 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #505 187 Sumner St |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15575037087
2023-11-30 07:57 | Paul | Gray | 17521 | 39 Johnston Rd |  | Dorchester | MA | 2128 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #506 187 Sumner St. |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15575047394
2023-11-30 07:59 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #601 187 Sumner St |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | Premier | ECK100OP01 |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15575057717
2023-11-30 08:03 | Paul | gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #602 187 Sumner St |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | Premier | ECK100OP01 |  | Apartment | Kitchen unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15575071082
2023-11-30 08:41 | Paul | Gray | 17521 | 39 johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #603 187 Sumner St |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15575219588
2023-11-30 08:44 | Paul | Gray | 17521 | 39 Johnston Rd |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #605 187 Sumner St |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15575232398
2023-11-30 08:47 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #606 187 Sumner St. |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | General Electric | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15575243866
2023-11-30 08:49 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #701 187 Sumner St. |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | Premier | ECK100OP01 |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15575256802
2023-11-30 08:53 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 617-822-0244 | President |  | Siemens/QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-07 | 2023-05-17 | Unit #702 187 Sumner St. |  | Boston | MA | 2128 | When the range is turned on the equipment trips the GFCI breaker installed. | Premier | JS645DLWW |  | Apartment | Kitchen Unit | Yes | No | Yes | Yes
2023-11-30 11:13 | Christopher | Hersey | 10876 | 12 Lewis Court |  | Hingham | MA | 2043 | 7817833786 | Electrician/owner |  | Eaton GFTCB250 | Breaker | None | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-15 | 2023-11-15 | 7 Saw Mill Pond Rd |  | Hingham | MA | 2043 | Every time we turn on breaker it tripped. When we put regular 2 pole breaker on it holds. | Wolf Cooktop | CIT365TS | No | Single family home | Kitchen cooking | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/15576469120
2023-11-30 14:46 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB645RK9SS | N/A | Independent Living Unit Kitchen | This issue occurs in the kitchen of independent living unit 1401. This issue only applies to the electric stove in these apartments. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578051855
2023-11-30 15:10 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 1402 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578228825
2023-11-30 15:14 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 1403 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578256464
2023-11-30 15:17 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 1404 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578271716
2023-11-30 15:19 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578287850
2023-11-30 15:22 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 1406 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578303166
2023-11-30 15:24 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 1407 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578318015
2023-11-30 15:26 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 1408 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578331613
2023-11-30 15:28 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 1409 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578347373
2023-11-30 15:31 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 1410 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578364658
2023-11-30 15:33 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 1411 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578379556
2023-11-30 15:35 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 1412 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578392534
2023-11-30 15:37 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 1413 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578404645
2023-11-30 15:38 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 1414 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578417073
2023-11-30 15:43 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2414 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578446551
2023-11-30 15:45 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2413 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578458915
2023-11-30 15:47 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 1412 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578473333
2023-11-30 15:49 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | NA | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2412 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578489043
2023-11-30 15:51 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2411 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578503240
2023-11-30 15:53 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2410 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578516555
2023-11-30 15:55 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2409 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578532224
2023-11-30 15:57 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2408 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578545850
2023-11-30 15:59 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2407 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578559387
2023-11-30 16:00 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | GE JB646RK9SS | This is an issue in the kitchen of independent living unit 2406 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578571690
2023-11-30 16:02 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2405 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578584968
2023-11-30 16:04 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2404 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578597990
2023-11-30 16:06 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2403 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578610719
2023-11-30 16:08 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2402 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578622636
2023-11-30 16:10 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-02 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2401 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578638200
2023-11-30 16:13 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2415 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578654844
2023-11-30 16:14 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2416 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578667161
2023-11-30 16:17 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2417 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578682391
2023-11-30 16:18 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2418 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578693452
2023-11-30 16:21 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2419 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578713189
2023-11-30 16:23 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2420 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578722913
2023-11-30 16:25 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2421 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578735668
2023-11-30 16:27 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2422 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578746960
2023-11-30 16:28 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2423 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578757933
2023-11-30 16:30 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2424 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578771581
2023-11-30 16:32 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2425 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578784459
2023-11-30 16:34 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2426 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578794460
2023-11-30 16:36 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 2427 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15578807916
2023-12-01 13:31 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 342 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655JK355 |  | AFFORDABLE HOUSING APARTMENTS | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15583492107
2023-12-01 13:43 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRCICIAN |  | GFTCB250 | Breaker | BREAKER | 15 |  | 2 Pole | Eaton | Residence |  | 2023-10-10 | 2023-10-11 | 334 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING APARTMENTS | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15583565615
2023-12-01 13:47 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 326 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING APARTMENTS | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15583597200
2023-12-01 13:51 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 320 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15583623055
2023-12-01 13:56 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 316 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15583650520
2023-12-01 14:02 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 314 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING APAPRTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15583690267
2023-12-01 14:06 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 312 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15583712751
2023-12-01 14:14 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 308 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15583759404
2023-12-01 14:18 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 306 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15583783722
2023-12-01 14:21 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 304 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15583806471
2023-12-01 14:32 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3431 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15583874611
2023-12-01 14:34 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3430 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15583887223
2023-12-01 14:36 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3429 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15583898004
2023-12-01 14:38 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3428 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15583908327
2023-12-01 14:39 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3427 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15583916901
2023-12-01 14:48 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3426 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15583968502
2023-12-01 14:50 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3425 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15583980943
2023-12-01 14:52 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3424 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15583993128
2023-12-01 14:53 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3423 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584004622
2023-12-01 14:55 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3422 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584015152
2023-12-01 14:57 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3421 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584027040
2023-12-01 14:59 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3420 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584037367
2023-12-01 15:00 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3419 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584047559
2023-12-01 15:02 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3418 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584059984
2023-12-01 15:04 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3417 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584070074
2023-12-01 15:06 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3416 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584080765
2023-12-01 15:07 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3415 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584091222
2023-12-01 15:10 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3401 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584107146
2023-12-01 15:12 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3402 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584120047
2023-12-01 15:13 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3403 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584132035
2023-12-01 15:15 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3404 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584145220
2023-12-01 15:17 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3405 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584158874
2023-12-01 15:19 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3406 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584171520
2023-12-01 15:21 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | n/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3407 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584182736
2023-12-01 15:22 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3408 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/15584194837
2023-12-01 15:24 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | n/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3409 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584205163
2023-12-01 15:26 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3410 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584219340
2023-12-01 15:28 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | Ge | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3412 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584235523
2023-12-01 15:30 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | n/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3413 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584248174
2023-12-01 15:30 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 108 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584251448
2023-12-01 15:32 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 3414 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584260077
2023-12-01 15:34 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 132 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584272250
2023-12-01 15:38 | MICHAEL | ONEIL | 26465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIANGFTCB250 |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 134 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING APARTMENTS | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584300958
2023-12-01 15:41 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 136 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584322083
2023-12-01 15:48 | MICHAEL | ONEIL | 26465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-11-11 | 138A HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584366994
2023-12-01 15:49 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | n/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4414 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584368476
2023-12-01 15:50 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4413 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584377687
2023-12-01 15:52 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4412 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584386872
2023-12-01 15:53 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 40 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4411 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584394759
2023-12-01 15:54 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4410 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584404154
2023-12-01 15:56 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4409 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584413094
2023-12-01 15:57 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4408 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584423930
2023-12-01 15:59 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JTS3000SN2SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4407 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584435365
2023-12-01 16:00 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 138B HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLEHOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584442485
2023-12-01 16:01 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | PResident/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | JTS3000SN2SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4406 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584445432
2023-12-01 16:03 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4405 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584454319
2023-12-01 16:04 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4403 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584463765
2023-12-01 16:04 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 140A HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584466008
2023-12-01 16:06 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4402 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584474630
2023-12-01 16:07 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-07-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4401 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584483478
2023-12-01 16:08 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-20 | 140B HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584487966
2023-12-01 16:10 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4415 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584499086
2023-12-01 16:12 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4416 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584507900
2023-12-01 16:13 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4417 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584517525
2023-12-01 16:14 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICICAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 141A HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584521115
2023-12-01 16:15 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4418 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584528817
2023-12-01 16:16 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 141B HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDBALE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584537266
2023-12-01 16:17 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4419 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584538160
2023-12-01 16:18 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4420 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584546548
2023-12-01 16:19 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICANGFYCB250 |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 139A HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLEHOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584554731
2023-12-01 16:19 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584554814
2023-12-01 16:21 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | Ge | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4422 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584563186
2023-12-01 16:23 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4423 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584571276
2023-12-01 16:23 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 139B HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584573879
2023-12-01 16:24 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4424 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584580424
2023-12-01 16:26 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4425 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584589404
2023-12-01 16:27 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 131 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584595501
2023-12-01 16:28 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4426 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584605334
2023-12-01 16:30 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 111 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584611535
2023-12-01 16:30 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4427 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584613564
2023-12-01 16:31 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4428 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584620970
2023-12-01 16:32 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 113 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KICTHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584624678
2023-12-01 16:33 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4429 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584630500
2023-12-01 16:35 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 95 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584638618
2023-12-01 16:35 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4430 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584639448
2023-12-01 16:36 | Eli | Florence | 17500 | 290 Pine Street |  | Canton | MA | 2332 | 7817697110 | President/PM |  | QPF GFCI 5mA 2P 240V 50A 10KA | Breaker | N/A | 50 | N/A | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 20 Hill Street |  | Woburn | MA | 1801 | When turned on the electric stove will start to heat up but after a few minutes will trip the GFCI circuit breaker. | GE | GE JB646RK9SS | N/A | Independent Living Kitchen | This is an issue in the kitchen of independent living unit 4431 of the Delaney at the Vale. This applies to only the electric stove in the kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15584647318
2023-12-01 16:37 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-11 | 93 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15584652178
2023-12-04 07:51 | Bryan | Dollard | 23498 | 472 West Broadway | 101B suite 4 | SOUTH BOSTON | MA | 2127 | 17812667291 | President |  | GFTCB260 | Breaker | N/A | 60 |  | 2 Pole | Eaton | Residence |  | 2023-11-26 | 2023-10-02 | 726 East Eight St Apt 1 |  | SOUTH BOSTON | MA | 2127 | Turn on oven for pre-heat. Breaker trips 5 seconds later | Thermador | MEDMC301WS |  | APT | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15591585916
2023-12-04 07:55 | Bryan | Dollard | 23498 | 472 West Broadway | 101B suite 4 | SOUTH BOSTON | MA | 2127 | 17812667291 | President |  | GFTCB260 | Breaker | NA | 60 |  | 2 Pole | Eaton | Residence |  | 2023-11-26 | 2023-10-02 | 726 East Eight St Apt 2 |  | SOUTH BOSTON | MA | 2127 | Turn on pre- heat, Breaker trips with in 5 seconds | Thermador | MEDMC301WS |  | apt | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15591597437
2023-12-04 07:58 | Bryan | Dollard | 23498 | 472 West Broadway | 101B suite 4 | SOUTH BOSTON | MA | 2127 | 17812667291 | President |  | GFTCB260 | Breaker | NA | 60 |  | 2 Pole | Eaton | Residence |  | 2023-11-26 | 2023-10-02 | 726 East Eight St Apt 3 |  | SOUTH BOSTON | MA | 2127 | Turn on pre heat, breaker trips 5 seconds later. | Thermador | MEDMC301WS |  | APT | kITCHEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/15591606551
2023-12-04 08:03 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #517 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is in the kitchen in this unit | Yes | No | Yes | Yes
2023-12-04 08:06 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | President |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #523 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is in the kitchen in this unit | Yes | No | Yes | Yes
2023-12-04 08:06 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #522 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is in the kitchen in this unit | Yes | No | Yes | Yes
2023-12-04 08:08 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #521 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is in the kitchen in this unit | Yes | No | Yes | Yes
2023-12-04 08:09 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #518 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is in the kitchen in this unit | Yes | No | Yes | Yes
2023-12-04 08:09 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #516 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is in the kitchen in this unit | Yes | No | Yes | Yes
2023-12-04 08:10 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #515 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is in the kitchen in this unit | Yes | No | Yes | Yes
2023-12-04 08:11 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #514 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is in the kitchen in this unit | Yes | No | Yes | Yes
2023-12-04 08:11 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #513 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is in the kitchen in this unit | Yes | No | Yes | Yes
2023-12-04 08:12 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #512 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is in the kitchen in this unit | Yes | No | Yes | Yes
2023-12-04 08:13 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #511 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is in the kitchen in this unit | Yes | No | Yes | Yes
2023-12-04 08:14 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | Unit #510 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is in the kitchen in this unit | Yes | No | Yes | Yes
2023-12-04 13:27 | Sean | Donoghue | 34701 | 2500 state hwy |  | Eastham | MA | 2642 | 5082405900 | Electrical Inspector |  | CH220GFCI | Breaker | GFCI | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-01 | 2023-10-18 | [5 empty] | Stove turned on ¦the oven was started and tripped the GFCI in under 60 seconds | Amana AER 6303 MMSO | RC 1653881 |  | ADU | Kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/15593625357
2023-12-04 14:49 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 141A HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15594252160
2023-12-04 14:52 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 141B HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENTS | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15594277912
2023-12-04 15:22 | MICHAEL23465 | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | electrician |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 360A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15594514591
2023-12-04 15:26 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 360B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | ASSISTED HOUING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15594543486
2023-12-04 16:13 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-07 | 2022-09-20 | #220 466 River Street |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General electric | GT025317Q |  | Apartment | It is in the kitchen of this unit | Yes | No | Yes | Yes
2023-12-04 16:40 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 362A BLUE LEDGE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLEHOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15595225571
2023-12-05 08:32 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 362B BLUE LEDGE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15598065955
2023-12-05 08:36 | MICHAEL26465 | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 364 BLUE LEDGE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15598081780
2023-12-05 08:40 | MICHAEL26465 | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 368A BLUE LEDGE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15598099010
2023-12-05 08:58 | MICHAEL26465 | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 368B BLUE LEDGE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15598181484
2023-12-05 09:01 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | [5 empty] | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15598195086
2023-12-05 09:04 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 370A BLUE LEDGE DRVIE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15598212958
2023-12-05 09:07 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 370B BLUE LEDGE DRVIE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APAPRTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15598228083
2023-12-05 09:10 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 374 BLUE LEDGE DRVIE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15598242130
2023-12-05 09:13 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 384 BLUE LEDGE DRVIE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15598256894
2023-12-05 09:14 | Kevin | Washek | 29418 | 28 PINEWOOD DR | framingham | FRAMINGHAM | MA | 1701 | 5082552606 | president |  | eaton | Breaker | no other | 30 |  | 2 Pole | Eaton | Residence |  | 2023-10-10 | 2023-08-03 | 60 webster road |  | weston | MA | 2493 | breaker consistanly trips - equipmment is brand new | wolf | cs030pm/s/ph |  | 1 family | kitchen oven | No | No | No | No |  | https://www.formstack.com/admin/download/file/15598266054
2023-12-05 09:16 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085352947 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 386 BLUE LEDGE DRVIE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15598272943
2023-12-05 11:30 | GUSTAVO | SILVA | 14788 | 302 Desimone Dr |  | Marlborough | MA | 1752 | 5087402698 | President |  | Mp230 gf 2 pole | Breaker | SKU mp 230 gf | 30 |  | 2 Pole | Siemens | Residence |  | 2023-11-15 | 2023-11-15 | 24 magnolia |  | Concord | MA | 1742 | Won't hold the GFCI breaker tripping out the time | Bluestar | Bsd48 | Regular 50 amps | Single family | Kitchen oven | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15599102119
2023-12-05 15:20 | Joseph | A Silverio | 17118 | 32 Franklin St | 17 Park Rd | Lowell, MA | MA | 1854 | 19788514900 | eLECTRICIAN |  | Eaton- GFTCB250CS | Breaker | 50 | 50 |  | 2 Pole | Eaton | Commercial |  | 2023-12-01 | 2023-11-27 | 72 D Parker |  | Acton | MA | 1720 | tripping repeatedly with burners and oven on | GE SUMMIT | RAS 200DM 2WW | n/a | kitchen | kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/15600716161
2023-12-05 15:54 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2022-09-07 | 2023-09-20 | #414 466 River STreet |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-12-05 15:55 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2022-09-07 | 2023-09-20 | #413 466 River STreet |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-12-05 15:56 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2022-09-07 | 2023-09-20 | #412 466 River STreet |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-12-05 15:57 | Paul | Gray | 17521 | 39 Johnston Rd. |  | Dorchester | MA | 2124 | 6178220244 | president |  | SQUARE-D / HOM250GFI | Breaker | BREAKER | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2022-09-07 | 2023-09-20 | #409 466 River STreet |  | Mattapan | MA | 2126 | When GE range turns on, the equipment trips the GFCI Breaker installed | General Electric | GT025317Q |  | Apartment | It is the kitchen in this unit | Yes | No | Yes | Yes
2023-12-05 21:49 | Juan | Deras | 55899 | 110 Arlington St |  | Fitchburg | MA | 1420 | 617 206 7663 | Electrician |  | Eaton/GFTCB250 | Breaker | 2pole Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-05 | 2023-12-04 | 17 Lakeview Ave. |  | Waltham | MA | 2451 | GFCI breaker trips ay few minutes in use , when cooking , using the oven. | GE cafe appliances | CHS950P2MS1 | none | residence single family | Kitchen. Dedicated circuit for Electric range | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15602674941
2023-12-06 11:02 | John | Vespa | 17144 | 250 Milton st |  | Dedham | MA | 2026 | 617 325 1151 | Owner |  | QBGFT2050 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2023-08-05 | 2021-04-07 | 86 glencliff rd |  | Boston | MA | 2131 | Breaker kept tripping and tripping more frequently as time went on. | Jennair | JIS1450DS |  | single family | kitchen, stove | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15604859273
2023-12-07 08:30 | Olli | Tervo | 14228 | 870 Fitchburg State Rd |  | Ashby | MA | 1431 | 978-840-0105 | President |  | Eaton/GFTCB250 | Breaker | 2 pole | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-11-20 | 63 Patriots Rd. |  | Templeton | MA | 1468 | The breaker trips after a few minutes of use of the cook top. | Electrolux | ECC13668AS | none | Single family residence | Its a dedicated circuit for the cook top in the kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/15609875440 | https://www.formstack.com/admin/download/file/15609875441
2023-12-07 08:36 | Olli | Tervo | 14228 | 870 Fitchburg State Rd |  | Ashby | MA | 1431 | 978-840-0105 | President |  | Eaton/GFTCB250 | Breaker | 2pole | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-20 | 2023-11-20 | 63 Patriots Rd. |  | Templeton | MA | 1468 | The breaker is tripping after a few minutes of use of the double wall oven. | Electrolux | GCWD3067AFB | none | Single family residence | It is a dedicated circuit for the wall oven in the kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/15609899066 | https://www.formstack.com/admin/download/file/15609899067
2023-12-07 10:39 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 103 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610549283
2023-12-07 10:42 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 111 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610565661
2023-12-07 10:44 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 123 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB 655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15610583337
2023-12-07 10:48 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-13 | 80 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610604717
2023-12-07 10:52 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-13 | 85 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610632873
2023-12-07 10:54 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 87 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSIING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610648292
2023-12-07 10:58 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 91 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610670774
2023-12-07 11:00 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 93 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610684378
2023-12-07 11:15 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 97 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610787579
2023-12-07 11:18 | [11 empty] | Line Gard PGFS-86108 | Relay/Contactor | permanent ground fault splice | 60 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/15610808161 | 2023-10-20 | 2023-10-20 | [5 empty] | Power is good when the griddle is not ON, when griddle is turned ON the gfci automatically trips. | Garland | ECG-48R |  | Cafeteria | Electric griddle in center of cafeteria | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/15610808185 | https://www.formstack.com/admin/download/file/15610808186
2023-12-07 11:23 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 1 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 99 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610835746
2023-12-07 11:25 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-10-06 | 101 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610850758
2023-12-07 11:28 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BRAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 141 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610874146
2023-12-07 11:31 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREKAER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 150 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610891050
2023-12-07 11:35 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 151 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APAPRTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610920091
2023-12-07 11:38 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 152 BLUE LEDGE DRIVE |  | ROSLINDALE |  | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610943544
2023-12-07 11:41 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-07 | 154 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610961127
2023-12-07 11:44 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-13 | 160 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15610983813
2023-12-07 11:47 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-13 | 162 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15611004218
2023-12-07 11:51 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-16 | 2023-11-15 | 166 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15611031759
2023-12-07 11:58 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-17 | 2023-11-16 | 3 BLUE LEDGE TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15611079938
2023-12-07 12:00 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2022-11-10 | 2023-11-09 | 4 BLUE LEDGE TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | VB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15611097066
2023-12-07 12:02 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-10 | 2023-11-09 | 17 BLUE LEDGE TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15611110399
2023-12-07 12:05 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-10 | 2023-11-09 | 19 BLUE LEDGE TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15611125339
2023-12-07 12:07 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-11 | 2023-11-10 | 24 BLUE LEDGE TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15611141517
2023-12-07 13:53 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | electrician |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-10 | 2023-11-09 | 93 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15611856680
2023-12-07 13:56 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-10 | 2023-11-09 | 113 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15611877947
2023-12-07 14:00 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-10 | 2023-11-09 | 95 HIGHCREST RD |  | ROSLINDALE |  | 2131 | RANGE TRIPS OUT BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15611901101
2023-12-08 11:40 | RAYMOND | OSTROSKI | 16764 | 7 CARDINAL WAY |  | METHUEN | MA | 1844 | 7818380703 | OWNER |  | chn240gf | Breaker | CUTLER HAMMER | 40 |  | 2 Pole | Eaton | Residence |  | 2023-12-08 | 2023-12-08 | [5 empty] | Breaker doesn't hold when the stove is turned on. have had previous issues with this. | kitchenaid | kose500ess |  | single family | kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15616443867
2023-12-08 11:46 | RAYMOND | Ostroski | 16764 | 5 cardinal way |  | Methuen | MA | 1844 | 7818380703 | owner |  | chn240gf | Breaker | CUTLER HAMMER | 40 |  | 2 Pole | Eaton | Residence |  | 2023-12-08 | 2023-12-08 | [5 empty] | Breaker doesn't hold when the stove is turned on. have had previous issues with this. | kitchenaid | kose500ess |  | single family | kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15616478666
2023-12-08 11:48 | Raymond | Ostroski | 16764 | 3 cardinal way |  | methuen | MA | 1844 | 7818380703 | owner |  | chn240gf | Breaker | CUTLER HAMMER | 40 |  | 2 Pole | Eaton | Residence |  | 2023-12-08 | 2023-12-08 | [5 empty] | Breaker doesn't hold when the stove is turned on. have had previous issues with this. | kitchenaid | kose500ess |  | single family | kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15616486802
2023-12-08 11:51 | Raymond | Ostroski | 16764 | 1 cardinal way |  | methuen | MA | 1844 | 7818380703 | owner |  | chn240gf | Breaker | CUTLER HAMMER | 40 |  | 2 Pole | Eaton | Residence |  | 2023-12-08 | 2023-12-08 | [5 empty] | Breaker doesn't hold when the stove is turned on. have had previous issues with this. | kitchenaid | kose500ess |  | single family | kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15616509140
2023-12-08 13:45 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 103 |  | Beverly | MA | 1915 | Breaker tripped multiple times on several occasions when oven was preheating | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-12-08 13:52 | Nick | Taormina | 14918 | Roy Spittle associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 104 |  | Beverly | MA | 1915 | Breaker tripped several times on multiple occasions during oven preheating | GE | JB645RKSS | Na | Apartment | Kitchen | Yes | No | Yes | No
2023-12-08 13:59 | Nick | Taormina | 14918 | 5 Heritage Way | Roy Spittle Associates | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 109 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-12-08 14:03 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage WAY | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 201 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-12-08 14:11 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1915 | 978-282-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 206 |  | Beverly | MA | 1915 | Kitchen | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-12-08 14:27 | Nick | Taormina | 14918 | Rot Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 207 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-12-08 14:34 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1915 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 210 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment2 | Kitchen | Yes | No | Yes | No
2023-12-08 14:42 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | Na | 50 | Na | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 211 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | Apartment | Kitchen | Yes | No | Yes | No
2023-12-08 15:34 | Jarret | Brissette | 21641 | 368 State Road |  | West Tisbury | MA | 2575 | 5086930764 | owner |  | HOM250GFI | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-12-07 | 2023-12-07 | 6 Noras Lane |  | Edgartown | MA | 2539 | GFI breaker trips immediately when turned to the on position | Wolf | CI365c/b | none | Single family dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15618015153
2023-12-11 08:38 | Jeff | McLaughlin | 12014 | 9 concord sq. Unit 4 |  | Boston | MA | 2118 | 7742977436 | Owner |  | Leviton LB120-DS | Breaker | Breaker dual function | 20 |  | 1 Pole | Leviton | Residence |  | 2023-11-16 | 2023-11-16 | [5 empty] | Breaker trips during normal operating cycle | Samsung | RF27T5501SR/AA |  | Apartment/condo/kitchen | Kitchen fridge | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15625471100
2023-12-11 09:09 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 978-283-2299 | President |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 213 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | apartment | kitchen | Yes | No | Yes | No
2023-12-11 09:13 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | President |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-06-01 | 140 Rantoul Street Unit 215 |  | Beverly | MA | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | apartment | kitchen | Yes | No | Yes | No
2023-12-11 09:16 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | President |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 216 |  | Beverly | MA | 1915 | breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | apartment | kitchen | Yes | No | Yes | No
2023-12-11 09:19 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | President |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-06-01 | 140 Rantoul Street Unit 220 |  | Beverly | MA | 1915 | breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RKSS |  | apartment | kitchen | Yes | No | Yes | No
2023-12-11 09:22 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | President |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 302 |  | Beverly | MA | 1915 | breaker tripped multiple times on multiple occasions during oven preheat | GE | KB645RKSS |  | apartment | kitchen | Yes | No | Yes | No
2023-12-11 09:25 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | President |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 304 |  | Beverly | MI | 1915 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | KB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 09:31 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 306 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 09:35 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 60 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 310 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 09:37 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 311 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | ge | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 13:57 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 315 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 14:00 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 317 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 14:02 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 320 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES DURING MULTIPLE OCCASIONS | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 14:06 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-06 | 2023-07-02 | 140 Rantoul Street Unit 322 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 14:09 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 401 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 14:12 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 402 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 14:16 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 406 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 14:18 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 407 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 14:22 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 410 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 14:56 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 411 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 15:00 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 415 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 15:02 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 416 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 15:04 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Industrial | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 417 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 15:07 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 418 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 15:09 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 419 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-11 15:11 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 420 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-12 08:18 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 421 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-12 08:31 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 501 |  | Beverly | MI | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-12 08:33 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2022-07-01 | 140 Rantoul Street Unit 502 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | KB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-12 08:37 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 508 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-12 08:39 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 510 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | KB645RKSS |  | APARTMENT | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | Yes | No | Yes | No
2023-12-12 08:42 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 514 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-12 08:45 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 515 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-12 09:23 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB350 | Breaker | NA | 60 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 601 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KIRCEHN | Yes | No | Yes | No
2023-12-12 09:25 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 602 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-12 09:27 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 603 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-12 09:29 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-05 | 2023-07-01 | 140 Rantoul Street Unit 611 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | kitchen | Yes | No | Yes | No
2023-12-12 09:31 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-06 | 2023-07-01 | 140 Rantoul Street Unit 612 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JB645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-12 09:34 | Nick | Taormina | 14918 | Roy Spittle Associates | 5 Heritage Way | Gloucester | MA | 1930 | 9782832299 | PRESIDENT |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-13 | 2023-07-01 | 140 Rantoul Street Unit 404 |  | Beverly | MA | 1915 | BREAKER TRIPPED MULTIPLE TIMES ON MULTIPLE OCCASIONS DURING OVEN PREHEAT | GE | JC645RKSS |  | APARTMENT | KITCHEN | Yes | No | Yes | No
2023-12-12 11:32 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 202 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15632521724
2023-12-12 11:56 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 203 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15632700815
2023-12-12 12:01 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 204 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15632737886
2023-12-12 12:06 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 205 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15632776441
2023-12-12 12:10 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 302 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15632809402
2023-12-12 12:14 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 303 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15632838955
2023-12-12 12:17 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 304 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15632863784
2023-12-12 12:22 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 402 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15632899334
2023-12-12 12:26 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 403 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15632926568
2023-12-12 12:30 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 404 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15632954978
2023-12-12 12:34 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 407 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15632982976
2023-12-12 12:38 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 408 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15633015042
2023-12-12 12:45 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-12-18 | 3-7 and 13/31 Elm Street Unit 409 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15633067661
2023-12-12 12:48 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 502 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15633089867
2023-12-12 12:51 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 503 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15633115076
2023-12-12 12:55 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 504 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15633144171
2023-12-12 12:59 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 601 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15633179857
2023-12-12 13:03 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 602 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15633206582
2023-12-12 13:10 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 603 |  | Springfield | MA | 1103 | Breaker tripped multiple times on muliple occasions during oven preheat | GE | JB645Rk955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15633266009
2023-12-12 13:14 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 604 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15633291803
2023-12-12 13:56 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 605 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15633612694
2023-12-12 13:59 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 609 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15633637361
2023-12-12 14:34 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | OWNER |  | SQ-D HOMELINE AD-910 | Breaker | DOUBLE POLE 50 AMP GFCI HOMELINE | 15 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-27 | 2023-09-01 | 4 BISHOP ESTATE |  | LENOX | MA | 1240 | Breaker would not hold, kept tripping. | GE | PHS93OYP3FS |  | Single Family | Kitchen | No | No | No | No
2023-12-13 16:23 | Ryan | LaBrache | 22042 | 1 Summer Street |  | Watertown | MA | 2472 | 617-924-8866 | owner |  | Hom203GFI | Breaker | stabin | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2023-12-12 | 2023-12-11 | 19 Sudbury Rd |  | Concord | MA | 1742 | CB will not hold when Dryer runs | Sears | 417000000000 |  | Residential | Laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/15640628976
2023-12-14 08:09 | Peter | Keller | 13379 | 114 Boston Post Rd |  | Wayland | MA | 1778 | 5088898049 | President/Electrician |  | QF240A | Breaker | none | 40 |  | 1 Pole | Siemens | Residence |  | 2023-11-14 | 2023-11-13 | 128 Revolutionary Rd. |  | Concord | MA | 1741 | New oven for kitchen remodel. new 40 amp circuit run to oven. oven trips GFCI breaker repeatedly. I tried two different GFCI breakers | Cafe | CTC912P2NS1 |  | single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15643300049
2023-12-14 08:34 | Nathan | Hewes | 39206 | 17 | Woodworth Street | Dorchester | MA | 2122 | 6175422000 | Electrician |  | Ge Two pole 50 gfci breaker | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-08 | 2023-12-08 | 165 chestnut hill ave |  | Brighton | MA | 2135 | Induction stove does not hold | Electrolux | Ecfi3668as |  | Condo | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15643391563
2023-12-14 19:04 | Peter | Keller | 13379 | 114 Boston Post Rd |  | Wayland | MA | 1778 | 5088898049 | Owner/President/Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2023-11-16 | 2023-11-15 | 66 Cutler Farm Rd. |  | Sudbury | MA | 1776 | range repeatedly tripped 2 different GFCI Breakers almost immediately after installation/wiring. | Wolfe | DF48650G/S/P | none | Kitchen | Kitchen Range | No | No | No | No |  | https://www.formstack.com/admin/download/file/15647178294
2023-12-15 10:21 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-08 | 2023-11-07 | 83 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT OF GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING APARTMENTS | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15649497175
2023-12-16 12:10 | RANDY | O'GRADY | 12493 | 245 Forge Village |  | Groton | MA | 1450 | 9784486377 | owner electrician |  | GE 2 pole 50 GFCI plug in breaker THQL2150GFT | Breaker | none | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-16 | 2023-12-15 | 282B Great Rd |  | Acton, | MA | 1742 | Range Oven preheat bake for three minutes appliance causes breaker tripping | GE | JB2560M2WW | none | single Family | kitchen range | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15654127483
2023-12-17 11:26 | Gideon | Vesset | 36133 | 14 Donlon St. |  | Framingham | MA | 1701 | 6179660233 | sole propriator |  | Schneider Electric/ QO250GFI | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-12-12 | 2023-12-12 | 1731 Beacon St. unit 524 |  | Brookline | MA | 2445 | Breaker is Tripping as soon as it is switched on | Haier | QAS740 |  | apartment | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15656135942
2023-12-18 07:41 | Ryan | LaBrache | 22042 | 1 Summer Street |  | Watertown | MA | 2472 | 617-924-8866 | onwer |  | LB250-GS | Breaker | na | 50 |  | 2 Pole | Leviton | Residence |  | 2023-12-14 | 2023-09-20 | 4 Shepard St |  | Cambridge | MA | 2138 | Induction Range will not run on the GFI CB | Samsung | NE63B8611SG/AA |  | residential | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15658691726
2023-12-18 08:56 | Christopher | Trites | 40129 | 7 Kosciusko St |  | Woburn | MA | 01801-3863 | 7815898967 | Electrician |  | Square D Homeline Model- HOM250GFI | Breaker | 2 pole 50 GFCI circuit Breaker. New installation | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-12 | 2023-08-25 | 134 Bedford Rd |  | Woburn | MA | 1801 | Random tripping. Sometimes even when not in use. For example, breaker trips overnight and stove is off while trying to make breakfast. | Beko | PRIR34452SS |  | Single family home | Kitchen Range | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15658952538
2023-12-18 10:51 | George | Hassard | 13263 | 944 Salem Street |  | GROVELAND | MA | 1834 | 9783731393 | Electrician |  | Simens 2p50 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-10-06 | 2023-10-06 | 29-16 Victor St |  | Haverhill | MA | 1832 | Tripping after heating | GE | JB2560M3BB |  | Apartment | k | No | No | No | No |  | https://www.formstack.com/admin/download/file/15659581091
2023-12-18 11:01 | George | Hassard | 13263 | 944 Salem Street |  | GROVELAND | MA | 1834 | 9783731393 | Electrician |  | Simens | Breaker | QPF 2P50A | 50 |  | 2 Pole | Siemens | Residence |  | 2023-08-23 | 2023-08-28 | 37 Woodcock Ave 11 |  | Haverhill | MA | 1832 | Tripping when heating | GE Appliance | JB256DM3BB |  | Residential | Kitchen/Stove | No | No | No | No
2023-12-18 11:08 | George | Hassard | 13263 | 944 Salem Street |  | GROVELAND | MA | 1834 | 9783731393 | Electrician |  | HOM250GFICP | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-11-20 | 2023-11-20 | 2 School House Rd Unit 1106 |  | Gloucester | MA | 1930 | Tripping while heating | GE | JB645RR6SS |  | Apartment | Kitchen ¦ | No | No | No | No
2023-12-18 11:11 | George | Hassard | 13263 | 944 Salem Street |  | GROVELAND | MA | 1834 | 9783731393 | Electrician |  | HOM250GFICP | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-11-20 | 2023-11-20 | 2 School Rd Unit 2220 |  | Gloucester | MA | 1930 | Tripping under self clean | GE | JB645RR6SS |  | Apartment | Kitchen | No | No | No | No
2023-12-18 11:52 | William | Kotowski | 16525 | 101A Commercial St |  | Malden | MA | 2148 | 7813223173 | Owner |  | Siemens QF250A breaker | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2023-12-18 | 2023-12-18 | 77 Avon Hill Street |  | Cambridge | MA | 2139 | 240V cooktop uses equipment ground as neutral conductor. This is causing GFCI breaker to trip immediately. ¦Cooktop is wired this way from the manufacturer. | Miele | KM6375 |  | Single Family | Kitchen Cooktop | No | No | No | No | https://www.formstack.com/admin/download/file/15659973638 | https://www.formstack.com/admin/download/file/15659973639
2023-12-18 15:38 | Thomas | Gallagher | -31100 | 16 West street |  | Northborough | MA | 1532 | 508-330-0872 | electrical contractor |  | GFTCB250 | Breaker | HAGF | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-12 | 2023-12-12 | 3 Pheasant run |  | Wayland | MA | 1778 | Range immediately trips breaker | Wolf | IR36550/s/t | no | residential | Kitchen range | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15661447544
2023-12-18 20:00 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-03-06 | 99 Riverside Ave Unit 1108 |  | Medford | MA | 2155 | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | APartment | Kitchen¦Serial-FV104925Q | No | No | Yes | Yes
2023-12-18 20:03 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-03-07 | 99 Riverside Ave Unit 1109 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | apartment | kitchen¦Serial-DV126370Q | No | No | Yes | Yes
2023-12-18 20:04 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-03-08 | 99 Riverside Ave Unit 1110 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126365Q | No | No | Yes | Yes
2023-12-18 20:06 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-29 | 2023-03-07 | 99 Riverside Ave Unit 1111 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126367Q | No | No | Yes | Yes
2023-12-18 20:08 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-03-07 | 99 Riverside Ave Unit 1112 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126366Q | No | No | Yes | Yes
2023-12-18 20:11 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-03-07 | 99 Riverside Ave Unit 1113 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV093977Q | No | No | Yes | Yes
2023-12-18 20:13 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-04-27 | 99 Riverside Ave Unit 1115 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9ss |  | Apartment | Kitchen¦Serial-AV046066Q | No | No | Yes | Yes
2023-12-18 20:16 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-03-01 | 99 Riverside Ave Unit 1201 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126356Q | No | No | Yes | Yes
2023-12-18 20:17 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-03-02 | 99 Riverside Ave Unit 1202 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV092385Q | No | No | Yes | Yes
2023-12-18 20:19 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-03-02 | 99 Riverside Ave Unit 1203 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV130187Q | No | No | Yes | Yes
2023-12-18 20:21 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-03-03 | 99 Riverside Ave Unit 1204 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126288Q | No | No | Yes | Yes
2023-12-18 20:22 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-03-06 | 99 Riverside Ave Unit 1205 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126357Q | No | No | Yes | Yes
2023-12-18 20:24 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-03-03 | 99 Riverside Ave Unit 1206 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV092382Q | No | No | Yes | Yes
2023-12-18 20:26 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-03-02 | 99 Riverside Ave Unit 1207 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126355Q | No | No | Yes | Yes
2023-12-18 20:28 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-03-02 | 99 Riverside Ave Unit 1208 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126310Q | No | No | Yes | Yes
2023-12-18 20:29 | Philippe | Thibeault | 22128 | 124 river rd |  | Lowell | MA | 1852 | 978-815-6009 | Owner |  | Siemens afci gfci dual function breaker | Breaker | Single pole breaker | 15 |  | 1 Pole | Siemens | Residence |  | 2023-12-18 | 2023-12-17 | 8 fletcher ct |  | Acton | MA | 1720 | Light comes on the hood as soon as you turn the motor on it trips | Coppersmith | Artisan custom range hood at3 | None | Single family home | Hood above stove in kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15662826672
2023-12-18 20:30 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-03-03 | 99 Riverside Ave Unit 1209 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV092381Q | No | No | Yes | Yes
2023-12-18 20:32 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-02-24 | 99 Riverside Ave Unit 1210 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JB655SKBS5 |  | Apartment | Kitchen¦Serial-AV12007526Q | No | No | Yes | Yes
2023-12-18 20:33 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-03-03 | 99 Riverside Ave Unit 1211 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV074571Q | No | No | Yes | Yes
2023-12-18 20:36 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | Gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-02-17 | 99 Riverside Ave Unit 1301 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JB655SKBSS |  | Apartment | Kitchen¦Serial-AV071552Q | No | No | Yes | Yes
2023-12-18 20:38 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-02-22 | 99 Riverside Ave Unit 1302 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS655SKBSS |  | Apartment | Kitchen¦Serial-AV071551Q | No | No | Yes | Yes
2023-12-18 20:39 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-02-21 | 99 Riverside Ave Unit 1303 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JB655SKBSS |  | Apartment | Kitchen¦Serial-AV071529Q | No | No | Yes | Yes
2023-12-18 20:41 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-03-10 | 99 Riverside Ave Unit 1304 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV104926Q | No | No | Yes | Yes
2023-12-18 20:43 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-02-24 | 99 Riverside Ave Unit 1306 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV094073Q | No | No | Yes | Yes
2023-12-18 20:44 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-03-03 | 99 Riverside Ave Unit 1307 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126352Q | No | No | Yes | Yes
2023-12-18 20:46 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-02-24 | 99 Riverside Ave Unit 1308 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126296Q | No | No | Yes | Yes
2023-12-18 20:47 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-02-24 | 99 Riverside Ave Unit 1310 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK966 |  | Apartment | Kitchen¦Serial-DV092380Q | No | No | Yes | Yes
2023-12-18 20:49 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-02-16 | 99 Riverside Ave Unit 1406 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JB655SKSS |  | Apartment | Kitchen¦Serial-AV127525Q | No | No | Yes | Yes
2023-12-18 20:51 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-01-18 | 99 Riverside Ave Unit 1407 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9ss |  | Apartment | Kitchen¦Serial-ZTO28328Q | No | No | Yes | Yes
2023-12-18 20:52 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-25 | 2023-02-16 | 99 Riverside Ave Unit 1410 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JB655SKBSS |  | Apartment | Kitchen¦Serial-AV127524Q | No | No | Yes | Yes
2023-12-19 19:24 | Scott | Haynes | 20116 | 18 Maddie Way |  | Bellingham | MA | 2019 | 508-922-6557 | owner |  | GFTCB250 | Breaker | Plug-in | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-10-30 | 165 Shepard Road |  | Sturbridge | MA | 1518 | Breaker trips when the oven tries to get to temperature. | Frigidaire | GCFE3060BFA |  | Residential Kitchen | Oven in a kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15668130203
2023-12-19 19:50 | Scott | Haynes | 20116 | 18 Maddie Way |  | Bellingham | MA | 2019 | 508-922-6557 | Owner |  | GFTCB250 | Breaker | Plug-in | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-10-30 | 165 Shepard Road |  | Sturbridge | MA | 1518 | GFI trips when oven tries to reach temperature. | Samsung | 5142923 |  | Kitchen | oven in the kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15668225902
2023-12-19 21:13 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-04 | 2023-05-17 | 99 Riverside Ave Unit 212 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV110843Q | No | No | Yes | Yes
2023-12-19 21:15 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-05-17 | 99 Riverside Ave Unit 215 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV126673Q | No | No | Yes | Yes
2023-12-19 21:16 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-26 | 2023-05-17 | 99 Riverside Ave Unit 216 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV107321Q | No | No | Yes | Yes
2023-12-19 21:19 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-05-09 | 99 Riverside Ave Unit 410 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV130185Q | No | No | Yes | Yes
2023-12-19 21:21 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-04-28 | 99 Riverside Ave Unit 506 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV058699Q | No | No | Yes | Yes
2023-12-19 21:23 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-02 | 2023-04-28 | 99 Riverside Ave Unit 507 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV092259Q | No | No | Yes | Yes
2023-12-19 21:24 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-12 | 2023-04-28 | 99 Riverside Ave Unit 508 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-VT060066Q | No | No | Yes | Yes
2023-12-19 21:26 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-27 | 2023-05-04 | 99 Riverside Ave Unit 516 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-AV10636Q | No | No | Yes | Yes
2023-12-19 21:28 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-04 | 2023-04-21 | 99 Riverside Ave Unit 610 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV096248Q | No | No | Yes | Yes
2023-12-19 21:31 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-04 | 2023-04-24 | 99 Riverside Ave Unit 611 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV096251Q | No | No | Yes | Yes
2023-12-19 21:34 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-05-24 | 99 Riverside Ave Unit 805 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV114553Q | No | No | Yes | Yes
2023-12-19 21:35 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-05-24 | 99 Riverside Ave Unit 807 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-GV114555Q | No | No | Yes | Yes
2023-12-19 21:37 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-04 | 2023-02-01 | 99 Riverside Ave Unit 810 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen | No | No | Yes | Yes
2023-12-19 21:38 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-04 | 2023-03-24 | 99 Riverside Ave Unit 812 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-FV104618Q | No | No | Yes | Yes
2023-12-19 21:40 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2072 | 7814929520 | Foreman |  | HOM250GFIC | Breaker | gfci | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-09-28 | 2023-03-14 | 99 Riverside Ave Unit 1011 |  | Medford | MA |  | One of many apartments at Riverside Towers located at 99 Riverside Ave., Medford, MA that received a new General Electric stove during a remodel. Stoves were experiencing issues with the GFCI breaker. This caused residents to be unable to use their stove. Many of the stoves were burned off due to these tripping issues pursuant to the bulletin issued by General Electric for this issue. Burning off did not solve the problem and residents were continuing to have tripping issues with the GFCI breaker. A representative from General Electric came out to the site and stated that this was a known issue with the stove, that the engineers are attempting to fix and that we would not be able to fix the issue with burning off the stove or any other fix in the field. This is contrary to what GE claimed at the time of purchase. They claimed this was no longer an issue with their stove. The electrical inspector with the City of Medford was contacted and approved the use of rule 11 on these stoves. Per the rule the electrical connections in the apartment circuit as well as the connection of the appliance whip into the range were checked. The jumper from the neutral to the ground had been removed originally. Breaker has been changed from a GFCI to a standard trip Homeline 2 pole 50 amp breaker | GE | JBS60RK9SS |  | Apartment | Kitchen¦Serial-DV135929Q | No | No | Yes | Yes
2023-12-20 18:37 | Tiago | Felisbino | 23429 | 8 Riverbank terrace |  | Billerica | MA | 1821 | 617-529-9170 | Mater ELectrician |  | QF250A | Breaker | Oven | 50 |  | 2 Pole | Siemens | Residence |  | 2023-12-20 | 2023-12-20 | 345 North st |  | Medfield | MA | 2052 | The 2 pole 50A breakers trips when is plugged in to the stove . both the stove and 240v circuit was verified to check for continuity and and issues were detected . Also tried to replace the breaker for a new one , no success . | Bertazzoni | PRO365ICFEPNET |  | Residential | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15673065790
2023-12-21 18:51 | David | Hamner | 40074 | 187 Longfellow Rd |  | Waltham | MA | 2453 | 617-293-7185 | Owner |  | GFTCB250 | Breaker | GFI | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-16 | 2023-07-12 | 9 Marion Ave |  | Bedford | MA | 1730 | Stove heats half way up and then trips | LG | LREL6323S |  | House | Kitchen Stove | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15678121169
2023-12-22 14:58 | Craig | Amelisko | 53566 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 413-316-0260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-22 | 2023-10-18 | 3-7 &13-31 Elm Street Unit 212 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | jb645rk955 |  | Apartment | Kitchen | Yes | No | Yes | No
2023-12-23 10:03 | Bobby | Beaulieu | 38953 | 7 Pine Grove Road |  | Westford | MA | 1886 | 6172011874 | Owner |  | Cutler Hammer | Breaker | no | 40 |  | 2 Pole | Eaton | Residence |  | 2023-10-17 | 2023-10-15 | 21 Mark Vincent Dr |  | Westford | MA | 1886 | New GE double oven would trip after a few minutes. Customer had GE repair man out 4-5 times to troubleshoot the oven for any defects. They replaced boards and still oven would trip the GFI breaker. I replaced it with a regular 2 pole 40-amp circuit breaker and problem went away. | GE profile cafe | PTD7000SNSS |  | Kitchen | Only (1) item is affected and that is the oven | Yes | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15683027864
2023-12-26 11:08 | Daron | St Jean | 0 | 22 Henry Ave |  | Methuen | MA | 1844 | 5084511436 | Licensed Electrician - Owner |  | Siemens AG9AB00R | Breaker | na | 40 |  | 2 Pole | Siemens | Residence |  | 2023-11-03 | 2023-11-03 | 16 Pleasant |  | Andover | MA | 1810 | New Kitchen Aid wall oven micro combo trip Siemens GFCI 2 pole 4 amp breaker when oven is heating. Replaced with another GFCI and same thing. Regular breaker does not trip. Kitchen Aid rep confirmed some wall oven models may have this problem. | KichenAid | KOCE500ES |  | Single family | Kitchen - wall oven in cabinet | Yes | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15688870489
2023-12-26 13:50 | Christopher | Veliotis | 14765 | 13 Crabapple Dr. |  | Berkley | MA | 2779 | 508-326-6413 | Owner |  | GFTCB250 | Breaker | na | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-22 | 2023-12-07 | 57 Livoli Ave. |  | Braintree | MA | 2184 | 2 pole 50amp. GFCI breaker serving a plug-in range receptacle. Multiple nuisance tripping usually after appliance was in operation for a few minuets. A replacement GFCI circuit breaker of the same amperage and manufacturer was installed only to have the same issue. All elements of the branch circuit, receptacle and cord to the appliance have been inspected and found to be in compliance. | Whirlpool | KSEG700ESS6 | none | Single family dwelling | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15689639267
2023-12-26 17:19 | Albert | Quern | 28531 | 13 Prospect ST |  | West Newton | MA | 2465 | 6175715434 | Owner/ licensed electrician |  | Siemens L2307290492 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15690574818 | 2023-12-22 | 2023-12-21 | 22 FONTAINE ST |  | Marlborough | MA | 1752 | Breaker tripping as soon as it's turn on. | Frigidaire | Fcws302lafb |  | Kitchen | Kitchen | No | Yes | No | Yes | https://www.formstack.com/admin/download/file/15690574831 | https://www.formstack.com/admin/download/file/15690574832
2023-12-26 17:30 | Albert | Quern | 285531 | 13 Prospect ST |  | West Newton | MA | 2465 | 6175715434 | Owner/ licensed Electrician |  | Siemens L2303270277 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15690618845 | 2023-12-22 | 2023-12-21 | 22 FONTAINE ST |  | Marlborough | MA | 1752 | Breaker tripping as soon as it's turn on. | Frigidaire | FCFE3083ASB |  | Kitchen | Kitchen | No | Yes | No | Yes | https://www.formstack.com/admin/download/file/15690618858 | https://www.formstack.com/admin/download/file/15690618859
2023-12-27 11:17 | John | Puccio | 18249 | 96 Cedar Road North |  | Medford | MA | 2155 | 7813916057 | President |  | EATON | Breaker | 2 POLE GFCI CIRCUIT BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-27 | 2023-12-27 | 45 Saddle hill road |  | Weston | MA | 2493 | instant trip | Frigidaire | FPIC3677RFB | NONE | RESIDENTIAL | KITHEN COOKTOP | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/15692986016 | https://www.formstack.com/admin/download/file/15692986017
2023-12-27 11:21 | John | Puccio | 18249 | 96 Cedar Road North |  | Medford | MA | 2155 | 7813916057 | PRESIDENT |  | EATON | Breaker | 2 POLE GFCI CIRCUIT BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/15693008406 | 2023-12-27 | 2023-12-27 | 45 Saddle hill road |  | Weston | MA | 2493 | instant trip | Frigidaire | FPIC3677RFB | NONE | RESIDENTIAL | KITHEN COOKTOP | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/15693008421 | https://www.formstack.com/admin/download/file/15693008422
2023-12-27 17:08 | Richard | Chase | 21093 | P.O. Box 8112 |  | Haverhill | MA | 1835 | (781) 589-0262 | Electrician/Proprietor |  | QF250A | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-12-17 | 2023-12-17 | 13 Argyle St. |  | Andover | MA | 1810 | Circuit breaker tripped when range was turned on. Could not get circuit breaker to reset afterwards while range was plugged in. No fault current found. | AGA | AEL361DF | None | Single family | Dedicated range circuit in kitchen. | No | No | No | No |  | https://www.formstack.com/admin/download/file/15694756285
2023-12-27 19:20 | Leo | Brennan | 20151 | 56 Charlotte Road |  | East Walpole | MA | 2032 | 5089621651 | Owner |  | siemens - s-a qf250A gfci breaker | Breaker | breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2023-11-28 | 2023-10-19 | [5 empty] | When WOLF dual fuel range is turned on the breaker trips. Manufacturer recommends no GFCI/AFCI protection be used | Wolf Range | DF48650G/S/P |  | kitchen | kitchen range | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15695200652
2023-12-27 19:33 | Leo | Brennan | 20151 | 56 Charlotte Road |  | East Walpole | MA | 2032 | 5089621651 | Owner |  | Siemens - s-a-q120dfn plug on neutral dual function breaker | Breaker | gfci/afci | 20 |  | 1 Pole | Siemens | Residence |  | 2023-11-28 | 2023-10-19 | [5 empty] | refrigerator trips breaker when door opens | Sub - zero | DEC3050FI/L and DEC3050RID/R |  | kitchen | kitchen refrigerator/freezer | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15695241034
2024-01-01 22:29 | Dan | Virtan | 55215 | 24 KEACH ST |  | WALTHAM | MA | 02453-1621 | 6179130817 | President |  | Square D Homeline HOM250GFIC | Breaker | 2 pole | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-12-21 | 2023-12-21 | 32 Aquavia Road |  | Medford | MA |  | GFCI breaker is working fine with the cooktop. It is tripping the oven as soon as it's turned ON. | Frigidaire | GCFE3060BDA | no | Single family dwelling unit | Kitchen | No | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/15709560637 | https://www.formstack.com/admin/download/file/15709560638
2024-01-02 08:49 | Steven | Landry | 17503 | 170 E Richardson Rd | Dracut | DRACUT, MA | MA | 1826 | 9783751314 | electrical contractor |  | Siemens | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Commercial |  | 2023-12-28 | 2023-12-28 | 99 Pleasant St |  | Marlborough | MA | 1752 | installed GFCI breaker stove began to heat and then GFCI tripped. Let the oven cool tried again with the same result | GE | JS760DPBB | none | Nursing hiome | Kitchen 2nd floor | No | No | No | No |  | https://www.formstack.com/admin/download/file/15710553126
2024-01-02 08:57 | Steven | Landry | 17503 | 170 E Richardson Rd | Dracut | DRACUT | MA | 1826 | 9783751314 | electrical contractor |  | Seimens BF250 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Commercial |  | 2023-12-28 | 2023-12-28 | 99 Pleasant St |  | Marlborough | MA | 1752 | installed GCCI Breaker as stove heated GFCI tripped allowed stove to cool tried again same result | GE | JS760BPBB | none | Nursing Home | Kitchen 3rd floor | No | No | No | No |  | https://www.formstack.com/admin/download/file/15710585602
2024-01-02 11:35 | Kevin | Moran | 36382 | 872 Morton St apt. 102 |  | Boston | MA | 2126 | 339-987-9658 | Superintendent |  | HOM250GFICP | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-22 | 2023-11-20 | [5 empty] | The breaker trips on the stove within 2 minutes of preheating for baking or broiling. | GE | JB645DK9WW | none | Apartment | The kitchen stove only. | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15711468212
2024-01-02 14:40 | MICHAEL | ONEIL | 23464 | 14 NORFOLK AVE |  | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-06 | 2023-10-05 | 49 JUNE ST |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING APARTMENTS | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15712686693
2024-01-02 15:08 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-11 | 2023-11-10 | 64 JUNE ST |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING APARTMENTS | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15712868652
2024-01-02 15:21 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-12 | 60 JUNE ST |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE APARTMENT HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15712954483
2024-01-02 15:25 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-07 | 2023-11-06 | 50 JUNE ST |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15712983660
2024-01-02 15:28 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MD | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-13 | 52 JUNE ST |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15713003944
2024-01-02 15:32 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 1 Pole | Eaton | Residence |  | 2023-11-16 | 2023-11-15 | 56 JUNE ST |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15713025482
2024-01-02 15:35 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-11 | 2023-11-11 | 56 JUNE ST |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15713045482
2024-01-02 15:42 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTRCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-21 | 2023-11-22 | 102 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15713094180
2024-01-04 08:14 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-12 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 212 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15720975891
2024-01-04 08:20 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 309 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RK955 |  | Apartment | kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15720991087
2024-01-04 08:24 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 311 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15721002097
2024-01-04 08:28 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 410 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat. | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15721013490
2024-01-04 16:01 | Jesse | Kuhlman | 21804 | 313 Eastern Ave |  | Lynn | MA | 1902 | 7815127272 | President |  | HOM250GFICP | Breaker | NA | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-21 | 2023-10-13 | 10 Lanark Rd Unit 6 |  | Brookline | MA | 2445 | Breaker started tripping when oven was not being used and then it escalated into multiple times a day still not being used. | SMEG | SPR30UIMX | No | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15723740492
2024-01-05 12:06 | William | Campbell | 55431 | 27 jolly farm rd |  | Bradford | NH | 3221 | 603 351 1191 | Journeyman electrician |  | 4884006004 | Breaker | N/a | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2022-03-15 | 2022-03-15 | [5 empty] | Turned breaker on, it held with no problem. When the wall oven calls for heat it trips the breaker. | Bosch | HBL5451UC/07 |  | Dwelling | Kitchen, wall oven only. | No | No | No | No |  | https://www.formstack.com/admin/download/file/15727406666
2024-01-05 12:10 | William | Campbell | 55431 | 27 jolly farm rd |  | Bradford | NH | 3221 | 603 351 1191 | Journeyman electrician |  | 4884006004 | Breaker | N/A | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2022-03-15 | 2022-03-15 | [5 empty] | Installed breaker, turned on. No problems. Cook top worked for a month before it started tripping breaker when calling for heat. | Bosch | NIT8069SUC |  | Single family Dwelling | Kitchen, cook top only. | No | No | No | No |  | https://www.formstack.com/admin/download/file/15727433772
2024-01-08 09:45 | Tony | Marroquin | 14426 | 48 Chamberlain |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB240 | Breaker | GFCI Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2023-12-24 | 2023-11-01 | 27 Whalen Road |  | Hopkinton | MA | 1748 | Breaker trips when Jenn Air JJW3430LL oven is preheating. Similarly, LG DLEX5500V Dryer trips at the end of each cycle even with | Jenn Air | JJW3430LL | None | Single Home | Kitchen and Laundry Room | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15736291580
2024-01-08 10:07 | Matthew | Tulley | 17365 | 31 Country Rd |  | East Hampstead | NH | 3826 | 978-360-3882 | Electrician |  | Eaton BR 30A single pole GFCI | Breaker | NA | 30 |  | 1 Pole | Eaton | Commercial |  | 2023-12-12 | 2023-12-12 | 436 Broadway |  | Methuen | MA | 1844 | Machine trips when it starts, sometimes immediately and sometimes after a few minutes. | ECOLAB | ES4000 |  | n/a | n/a¦This was a commercial application in a restaurant kitchen. | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15736412690
2024-01-08 10:14 | Matthew | Tulley | 17365 | 31 Country Rd |  | East Hampstead | NH | 3826 | 978-360-3882 | Electrician |  | Easton BR 20 amp 2 pole breaker | Breaker | N/A | 20 |  | 2 Pole | Eaton | Commercial |  | 2023-12-12 | 2023-12-12 | 436 Broadway |  | Methuen | MA | 1844 | Machine would trip when in use, sometimes immediately and sometimes it would take a few minutes. | ECOLAB | DF ROTARY |  | N/A | Commercial kitchen in restaurant | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15736455952
2024-01-09 13:59 | Kevin | Moran | 36382 | 872 Morton St |  | Boston | MA | 2126 | 339-987-9658 | Superintendent |  | HOM250GFICP | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-22 | 2023-11-20 | [5 empty] | Breaker trips on range within 2 minutes of preheating to bake/broil. | GE | JB645RK9SS |  | Condominium | Kitchens of units 401-409, 301, 302, 312. | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15744209358
2024-01-09 13:59 | Kevin | Moran | 36382 | 872 Morton St. |  | Mattapan | MA | 2126 | 339-987-9658 | Superintendent |  | HOM250GFICP | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-22 | 2023-11-20 | [5 empty] | Breaker trips on wall oven within 2 minutes of preheating to bake/broil. | GE | PTS700SN3SS |  | Condominium | Kitchen of unit 406 | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15744210800
2024-01-09 13:59 | Kevin | Moran | 36382 | 872 Morton St. |  | Boston | MA | 2126 | 339-987-9658 | Superintendent |  | HOM250GFICP | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-22 | 2023-11-20 | [5 empty] | Breaker trips on wall oven within 2 minutes of preheating to bake/broil. | GE | PTS700SN3SS |  | Condominium | Kitchen of unit 308, 203, 207, 208, community room kitchen. | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15744213549
2024-01-10 20:00 | Corey | Hood | 23032 | 55 Anne Road |  | Norwood | MA | 2062 | 7819157358 | Manager |  | GFTCB240 | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2024-01-05 | 2024-01-04 | 103 Aletha Road |  | Needham | MA | 2492 | Wall mounted oven was tripping the GFCI after warming the oven for 2 minutes. Multiple attempts. All connections and terminations torqued and inspected. | Thermador | PO302W/02 |  | Single Family | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15752406591
2024-01-11 11:05 | Timothy | Consolini | 54293 | 1 Cody Lane |  | Southwick | MA | 1077 | (413) 237-5537 | Electrician |  | HOM250GFI | Breaker | none | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-01-11 | 2024-01-09 | 41 Prospect St Apt 41-6 |  | Webster | MA | 1570 | The circuit breaker trips when the oven is on bake. | General ELectric | JKS300SNSS | NO | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 11:06 | Timothy | Consolini | 54293 | 1 Cody Lane |  | Southwick | MA | 1077 | (413) 237-5537 | Electrician |  | HOM250GFI | Breaker | none | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-01-11 | 2024-01-09 | 41 Prospect St Apt 41-7 |  | Webster | MA | 1570 | The circuit breaker trips when the oven is on bake. | General ELectric | JKS300SNSS | NO | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:23 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 101 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:23 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 201 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:24 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 301 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:25 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 401 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:25 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 106 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:26 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 107 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:26 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 108 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:27 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 109 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:28 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 206 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:29 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 207 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:29 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 208 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:30 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 209 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:31 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 306 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:31 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 307 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:32 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 308 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:32 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 309 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:33 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 406 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:33 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 407 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:34 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 408 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 12:35 | Brian | Hess | 53648 | 1441 Plumtree Rd |  | Springfield | MA | 1119 | (413) 505-9983 | Electrician |  | THQL2150GFI | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2023-12-04 | 2023-12-04 | 53 Wilbraham Rd - Apt 409 |  | Springfield | MA | 1105 | Circuit breaker trips sometimes when oven range is not on. | General Electric | JB258RTSS | NONE | APARTMENT | KITCHEN | Yes | No | Yes | No
2024-01-11 14:30 | Joseph | A Silverio | 17118 | 32 Franklin St | 17 Park Rd | Lowell, MA | MA | 1854 | 19788514900 | Electrician |  | Eaton- GFTCB250CS | Breaker | 2pole | 50 |  | 2 Pole | Eaton | Residence |  | 2024-01-11 | 2023-12-22 | 273 Barker Ave Unit #2 Lowell MA 01854 |  | Lowell | MA | 1854 | Tripped repeatedly when range burners and oven is on. | GE SUMMIT | R BS360DM2BB |  | Kitchen | kitchen/ | No | No | No | No |  | https://www.formstack.com/admin/download/file/15756345657
2024-01-12 07:56 | Alexander | Stelmah | 22142 | 9 Sunset Ave |  | North Reading | MA | 1864 | 617 416 8054 | Master electrician |  | Square D- QO240GFI | Breaker | 2pole | 40 |  | 2 Pole | ABB | Residence |  | 2023-12-15 | 2023-12-15 | 56 Lake Shore Ave |  | Beverly | MA | 1915 | Tripped repeatedly when range burners and oven is on . | Bosch 800Series | HIS8055U |  | Kitchen | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15759554718
2024-01-12 08:27 | Gene | Sokolovskiy | 22317 | 50 Kearney Rd |  | Needham | MA | 2494 | 6175007060 | Master electrician |  | Siemens QF250A | Breaker | QF250A | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15759645645 | 2023-12-30 | 2023-12-29 | 4 Kensington St |  | Andover | MA | 1810 | Breaker tripped after approximately 40 minutes of range work | Electrolux | FGEF3035RFA |  | single family house | kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/15759645658 | https://www.formstack.com/admin/download/file/15759645659
2024-01-12 13:34 | Tony | Marroquin | 14426 | 48 Chamberlain st |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB240 | Breaker | none | 40 |  | 2 Pole | Eaton | Residence |  | 2024-01-11 | 2023-08-15 | 29 Whalen Road |  | Hopkinton | MA | 1748 | GFCI trips when wall oven is used. Making the function of the oven useless. | Jenn Air | JJW3430LL |  | Single Family | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/15761275931
2024-01-12 16:12 | Thomas | Pendleton | 23526 | 49 Oak street |  | Billerica | MA | 1862 | 978-479-7857 | Electrician |  | QO250GFICP | Breaker | NA | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-01-12 | 2024-01-02 | 36 Warwick ave |  | Waltham | MA | 2452 | Breaker trips instantly when plugging in the range. | Bosch | HIS8655U |  | Kitchen | Kitchen | No | No | No | No
2024-01-15 11:15 | Gregory | Comeau | 16659 | 2 Avery Street |  | Wilmington | MA | 1887 | 6178390191 | owner |  | GE THQL 1120DF | Breaker | breaker | 20 |  | 1 Pole | ABB | Residence |  | 2024-01-05 | 2024-01-02 | 1160 Beacon St |  | Brookline | MA |  | Fridge trips breaker 3 or 4 times a day | Thermador | PO302W/03 |  | condo | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15771516365
2024-01-15 11:20 | Gregory | Comeau | 16659 | 2 Avery Street |  | Wilmington | MA | 1887 | 6178390191 | owner |  | GE THQL 1120DF | Breaker | breaker | 20 |  | 1 Pole | ABB | Residence |  | 2024-01-05 | 2024-01-02 | 1160 Beacon St |  | Brookline | MA |  | Freezer trips breaker 3 or 4 times a day | BSH Home Appliance Corp | T241F905SP/23 |  | condo | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15771544626
2024-01-15 11:22 | Gregory | Comeau | 16659 | 2 Avery St |  | Wilmington | MA | 1887 | 6178390191 | owner |  | GE THQL 1120DF | Breaker | breaker | 20 |  | 1 Pole | ABB | Residence |  | 2024-01-05 | 2024-01-02 | 1160 Beacon St |  | Brookline | MA |  | fridgetrips breaker 3 or 4 times a day | BSH Home Appliance Corp | T301R905SP |  | condo | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15771558574
2024-01-15 11:23 | Jake | Carlan | 19711 | 944 Salem Street |  | GROVELAND | MA | 1834 | 9783731393 | electrician |  | L2104100859 | Breaker | L2104100859 | 15 |  | 2 Pole | Siemens | Residence |  | 2024-01-12 | 2024-01-12 |  |  | Haverhill | MA | 1830 | Tripping when pre heating | G.E | JB258DM4BB |  | Residential | Stove in kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15771563431
2024-01-15 11:25 | Gregory | Comeau | 16659 | 2 Avery Street |  | Wilmington | MA | 1887 | 6178390191 | Owner |  | GE THQL 1120DF | Breaker | breaker | 40 |  | 2 Pole | ABB | Residence |  | 2024-01-05 | 2024-01-02 | 1160 Beacon St |  | Brookline | MA |  | Wall oven trips breaker within 20 seconds of turni | Thermador | PO302W/03 |  | condo | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15771577273
2024-01-15 11:28 | Jake | Carlan | 19711 | 895 Salem St |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | L2207061343 | Breaker | breaker | 15 | 40 | 2 Pole | Siemens | Residence |  | 2024-01-12 | 2024-01-12 |  |  | Haverhill | MA | 1830 | Tripping when pre heating | GE | JB258DM3BB |  | Residential | Stove in kitchen | No | No | No | No
2024-01-15 16:00 | BRIAN | VEDDER | 100374 | 10 locust St | Middleton | Middleton, MA | MA | 01949-1206 | 9787666064 | foreman/electrician |  | Siemens/L2211042002 | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-01-03 | 2023-12-12 | 29 Summer St. |  | Medford | MA | 2153 | 2 pole 50 amp breakers for kitchen Ranges trip instantly when turned on. Field chord connections are correct and are clear upon testing. | Whirlpool | W11508753D | none | Condos/4 family | Just the kitchen range. | No | No | No | No |  | https://www.formstack.com/admin/download/file/15773125417
2024-01-16 14:14 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | OWNER |  | SQ-D Homelink | Breaker | n/a | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2022-05-31 | 2022-05-31 | 167 HARTSVILLE MILL RIVER ROAD |  | NEW MARLBORO | MA | 1244 | Breaker does not hold, kept tripping. | Fisher & Paykel | OR30SDI6X1 |  | Single Family | Kitchen | No | No | No | No
2024-01-16 16:09 | greg | comeau | 16659 | 2 Avery st |  | Wilmington | MA | 1887 | 6178390191 | owner |  | GE THQL 2130GF | Breaker | breaker | 30 |  | 2 Pole | ABB | Residence |  | 2024-01-13 | 2024-01-02 | 1160 Beacon St |  | Brookline | MA |  | cook top breaker within multiple times a day | Thermador | CIT36YWBB |  | condo | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15778681985
2024-01-16 16:14 | greg | comeau | 16659 | 2 Avery st |  | Wilmington | MA | 1887 | 6178390191 | owner |  | QF-250 Siemens | Breaker | breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2024-01-02 | 2024-01-02 | 23 south cedar park |  | melrose | MA | 2176 | Stove trips gfi breker instantly | La Cornue | cornufe 44 induction |  | dwelling | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/15778716406
2024-01-18 07:15 | Steve | Daniels | 16467 | 2 School House Road |  | Gloucester | MA | 1930 | 9783731393 | Electrician |  | Square D | Breaker | GFCI | 50 |  | 1 Pole | Siemens | Residence |  | 2024-01-09 | 2024-01-11 | [5 empty] | Stove continually tripping breaker | GE | JB645RK6SS |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15787447580
2024-01-19 14:17 | Christopher | Trites | 40129 | 7 Kosciusko St |  | Woburn | MA | 01801-3863 | 7815898967 | Manager/Electrician |  | sqaure D Homeline / HOM250GFI | Breaker | GFCI circuit breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-11-11 | 2023-10-10 | 33 Vernon St |  | Woburn | MA | 1801 | Random tripping while Range is in use, especially if using timer feature | Frigidaire Electric Range | FEF35BAWB | none | Single Family Dwelling/Kitchen | Kitchen Electric Range. Happens at random times while Range is in use or using timer feature | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15801538646
2024-01-19 14:39 | Christopher | Trites | 40129 | 7 Kosciusko St |  | Woburn | MA | 01801-3863 | 7815898967 | Electrician/Manager |  | Square D Homeline/ HOM250GFI | Breaker | GFCI Circuit Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-10-24 | 2023-07-26 | 26 Kendall Court |  | Bedford | MA | 1730 | Random tripping while Range is in use | Samsung | NE63B8211SS | no | single family dwelling/kitchen | Electric Range in Kitchen. New installation. Samsung tech checked range, but found nothing wrong | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15801669589
2024-01-21 13:50 | Steven | Doherty | 20370 | PO Box 215 |  | Sturbridge | MA | 1566 | 5083661119 | Installer |  | QF230A | Breaker | na | 30 |  | 2 Pole | Siemens | Residence |  | 2023-12-15 | 2023-12-15 | [5 empty] | GFI breaker trips immediately when the cooktop is turned on. | Cafe | CHS900 | none | single family | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15806873389
2024-01-22 11:23 | Matthew | Bates | 53268 | 14 Pandora Dr |  | Groveland | MA | 1834 | 9784205734 | Electrician |  | HOM250GFCI | Breaker | Square D home line | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-15 | 2023-01-05 | 466 Massachusetts Avenue unit 309 |  | Acton | MA | 1720 | Nuisance tripping multiple times. I replaced the breaker and still had the same issue. | GE Appliances | JTS3000SN2SS |  | Kitchen | The only thing affected was the kitchen oven circuit, which is dedicated | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/15810244072
2024-01-22 11:29 | Matthew | Bates | 53268 | 14 Pandora Dr |  | Groveland | MA | 1834 | 9794205734 | Electrician |  | HOM250GFCI | Breaker | GFI breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-15 | 2023-01-05 | 446 Massachusetts Avenue unit 304 |  | Acton | MA | 1720 | Nuisance, tripping multiple times even after the breaker was changed | GE appliances | JTS3000SN2SS |  | Kitchen | Wall oven on a dedicated circuit in the kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/15810314789
2024-01-22 11:34 | Matthew | Bates | 53268 | 14 Pandora Dr |  | Groveland | MA | 1834 | 9794205734 | Electrician |  | HOM250GFCI | Breaker | GFCI breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-08-15 | 2023-01-05 | 446 Massachusetts ave unit 115 |  | Acton | MA | 1720 | Nuisance tripping multiple times even after breaker was replaced | GE appliances | JTS3000SN2SS |  | Kitchen | Wall oven in kitchen on a dedicated circuit | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/15810350358
2024-01-23 13:00 | Mark | Narciso | 35879 | 86 Conscript Ave |  | Westport | MA | 2790 | 5088894407 | Manager |  | Hom250Gfi | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-03-15 | 2024-02-15 | 16 Parsons Walk |  | Marshfield | MA | 2050 | Breaker tripping instantaneous on new range. Was new circuit checked and looked for neutral to ground jumper in range Connections. Everything was clear. | LG | LREL6323S |  | Single Family | Just Range | No | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/15817095981
2024-01-23 21:24 | Kris | Leary | 50072 | 51 Hunthurst Circle |  | Worcester | MA | 1602 | (978)257-2151 | Homeowner |  | Eaton/GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-17 | 2023-12-17 | [5 empty] | The breaker would trip instantly when stove was turned on for test.¦¦¦This is filed by the electrician, Philip Arsenault. | Hotpoint Stove | R B757W B1WW |  | Single Family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/15819847507 | https://www.formstack.com/admin/download/file/15819847508
2024-01-23 21:40 | Amy | Elmore | 50072 | 10 Grove Heights Dr |  | Worcester | MA | 1605 | (617)306-2118 | Homeowner |  | Eaton/GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-01 | 2023-12-01 | [5 empty] | The breaker would trip instantly when stove was turned on for test.¦¦¦This is filed by the electrician, Philip Arsenault. | KitchenAid | KEBC247KBL02 |  | Single Family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/15819893250 | https://www.formstack.com/admin/download/file/15819893251
2024-01-25 07:33 | JACK | GRIFFIN | 418 | 26 JOANNA DR |  | South Yarmouth | MA | 2664 | 978-479-2521 | OWNER |  | SQUARE D QO | Breaker | 0 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-01-24 | 2024-01-23 | 30 TWISS RD |  | ORLEANS | MA |  | TRIPS AS SOON AS IT IS PLUGGED IN. I CHECKED GROUND TO NUETUAL AND TO THE TWO HOTS AND THERE IS NO READING. | BOCSH | HIS8655U /05 |  | HOUSE | KITCHEN RANGE | No | No | No | No
2024-01-25 13:16 | Iury | Silvestre | 58685 | 85 Linden St Apt 2 |  | Everett | MA | 2149 | 8572932758 | Electrician |  | Siemens QF240AP | Breaker | No other | 40 |  | 2 Pole | Siemens | Residence |  | 2024-01-15 | 2023-09-20 | 20 Sylvan St Apt 3 |  | Danvers | MA | 1923 | Breaker trips instantly when oven is turned on. | Electrolux Home Products | FCFE3083ASA | No other equipment | Apartment | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15828249425
2024-01-26 08:06 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-18 | 3-7 and 13/31 Elm Street Unit 230 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RK955 |  | Apartment | kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15831675600
2024-01-26 08:10 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-10 | 3-7 and 13/31 Elm Street Unit 231 |  |  |  |  | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RK955 |  | Apartment | kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15831685759
2024-01-26 08:13 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-10 | 3-7 and 13/31 Elm Street Unit 330 |  | Springfield | MA | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15831694992
2024-01-26 08:16 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 4133160260 | Project Manager |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2023-12-04 | 2023-10-10 | 3-7 and 13/31 Elm Street Unit 331 |  | Springfield |  | 1103 | Breaker tripped multiple times on multiple occasions during oven preheat | GE | JB645RK955 |  | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15831703789
2024-01-26 15:43 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-13 | 331A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT OF GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING APARTMENTS | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15834125968
2024-01-26 15:46 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB 250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-14 | 2023-10-15 | 331B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT OF GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15834147692
2024-01-26 15:50 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-12 | 2023-10-13 | 333A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT OF GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15834168119
2024-01-26 15:54 | MICHAEL | ONEIL | 26465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-10 | 2023-10-09 | 333B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT OF GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15834187379
2024-01-26 16:17 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-04 | 2023-10-03 | 337A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT OF GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15834319854
2024-01-28 12:51 | Declan | Hourihan | 10852 | 37 Hutchinson St. |  | Dorchester | MA | 2124 | 617-513-6894 | Electrician |  | GFTCB240 | Breaker | regular 40amp breaker | 15 | 40 amp | 2 Pole | Eaton | Residence |  | 2024-01-22 | 2024-01-22 | 55 Halcyon Rd |  | Newton | MA | 2459 | As soon as you turned on the stove. | F Bertazzoni | MAS304INMXV |  | Single family. home | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15838875066
2024-01-29 08:24 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ElectricianGFTCB250 |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-01-29 | 2024-01-26 | 339A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT OF GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCED | JB655SK355 |  | AFFORDABLE APARTMENT HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15841355647
2024-01-29 08:33 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-01-30 | 2024-01-29 | 339B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS out of GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE APARTMENT HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15841385228
2024-01-29 10:08 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-01-31 | 2024-01-30 | 341A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREKAER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENTS | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15841851039
2024-01-29 10:10 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-01-31 | 2024-01-30 | 341B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15841868015
2024-01-29 10:17 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | ELECTRICIAN |  | GFCIB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-01-31 | 2024-01-30 | 337B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREKAER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15841913424
2024-02-01 10:49 | Luis | Matute | 54935 | 6 Dana ave unit 7 |  | Hyde Park | MA | 2136 | 2039425569 | Electrician |  | L2301070334 | Breaker | Cord and plug | 50 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | [5 empty] | Breaker wouldn't stay on | Woulf | IR30450/S/T |  | Kitchen | Customers can not use Range or cook | No | No | No | No |  | https://www.formstack.com/admin/download/file/15860250332
2024-02-01 14:37 | MICHAEL | ONEIL | 263465 | 14 NORFOLK AVE |  | EASTON | MA | 2375 | 5082308001 | Master Electrician |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-13 | 335A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE APARTMENT HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15861912792
2024-02-01 14:40 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE |  | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2023-11-14 | 2023-11-13 | 335B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15861937052
2024-02-01 16:05 | Jason | Curran | 21794 | 2 CROSS ST |  | DOUGLAS | MA | 1516 | 774-239-0488 | OWNER |  | siemens QF250AP | Breaker | gfci 2pole 50 | 50 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-01-30 | [5 empty] | OVEN WILL TRIP WHILE TRYING TRYING TO PRE-HEAT. | MIELE | HR1956-2 |  | SINGLE FAMILY | KITCHEN RANGE. | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15862574252
2024-02-02 11:38 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE |  | EASTON | MA | 2375 | 5085358001 | master electrician |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-07 | 2024-02-06 | 327A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENTS | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15866523850
2024-02-02 11:41 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-07 | 2023-02-06 | 327B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15866545979
2024-02-02 11:59 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-08 | 2023-02-07 | 329A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15866661747
2024-02-04 20:48 | Nicholas | Dagoumas | 54009 | 7 3rd street |  | Dracut | MA | 1826 | 9786095057 | Owner/ electrical contractor |  | Q115DFN Seimens dual function | Breaker | Breaker | 15 |  | 1 Pole | Siemens | Residence |  | 2024-01-25 | 2024-01-25 | 337 north rd |  | Bedford | MA |  | Fridge keeps tripping dual function breaker. Changed breaker to a new dual function and problem continued. | Fisher & Paykel | Fisher & Paykel RS36A72J1 N |  | Kitchen | Kitchen fridge | No | No | No | No |  | https://www.formstack.com/admin/download/file/15875181040
2024-02-05 20:58 | Samuel | Sanchez | 57482 | 44 Newport Lane |  | Osterville | MA | 2655 | 8577708114 | foreman |  | Leviton/LB120-DFT/LB250-G | Breaker | BREAKER | 50 | 20 | 2 Pole | Leviton | Residence |  | 2024-01-11 | 2023-12-16 | [5 empty] | Appliances have a safety shut off feature, GFCI is duplicative and is tripping. This will need to be done for the refrigerator and stove. | Refrigerator Thermador | T36FT820NS | PRD366WHU | Kitchen | Rooms are not affected, just stove and refrigerator are affected. | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15881419943
2024-02-06 09:01 | Joseph | Camillo | 4414 | 29 Cook St |  | Billerica | MA | 1821 | 978-663-0292 | VP |  | Leviton LB-250-GF | Breaker | 5 ma | 50 |  | 2 Pole | Leviton | Residence |  | 2023-12-13 | 2023-11-15 | 25 Orlando St. ( Units 1-2-3-4-5-6-7-8-9-10-11-12 ) 12 unit apts . |  | Mattapan | MA | 2126 | Breaker Tripped In a few minutes of turning on . Happened on all 12 Units. | GE | JB256DM/RM |  | Dwelling | Kitchen Stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/15883176322
2024-02-06 09:17 | Joseph | Camillo | 4414 | 29 Cook St |  | Billerica | MA | 1821 | 9786630292 | VP |  | Leviton LB250-GF | Breaker | 5 ma | 50 |  | 2 Pole | Leviton | Residence |  | 2022-11-11 | 2022-09-15 | 31 Orlando St. (Units 1-2-3-4-5-6) 6 Units in Total) |  | Mattapan | MA | 2126 | Breaker Tripped a few minutes after turning on Stove. Happened in all 6 Units. | GE | JB256DM/RM | None | Dwelling | Stove in Kitchen. | No | No | No | No |  | https://www.formstack.com/admin/download/file/15883248585
2024-02-06 09:55 | Joseph | Camillo | 4414 | 29 Cook St |  | Billerica | MA | 1821 | 9786630292 | VP |  | Leviton LB250-GF | Breaker | 5 ma | 50 |  | 2 Pole | Leviton | Residence |  | 2022-11-11 | 2022-10-15 | 35 Orlando St. (Units 1-2-3-4-5-6) 6 Units in Total) |  | Mattapan | MA | 2126 | Breaker tripped a few minutes after turning on. | GE | JB256DM/RM | none | Dwelling | Stove in Kitchen. | No | No | No | No |  | https://www.formstack.com/admin/download/file/15883455563
2024-02-07 09:51 | Daniel | Bisdnack | 39157 | 926 East Ave |  | Oakland | RI | 2858 | 9784797001 | Electrician |  | GE THQL2150GFT2 2P 50A CB | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2024-02-02 | 2024-01-31 | 108 High Meadow Circle |  | Bourne | MA | 2532 | Breaker trips 5 minutes into heating cycle of oven. | GE | JB250DF7BB | None | Apartment | Kitchen | No | Yes | Yes | No | https://www.formstack.com/admin/download/file/15889543655 | https://www.formstack.com/admin/download/file/15889543656
2024-02-08 08:18 | [11 empty] | N/A | Cordset | Hardwired Installation | 30 | 50 | 2 Pole | Schneider Electric | Commercial |  | 2024-01-28 | 2023-12-15 | 4 & 6 Glen Brook Way |  | Medway | MA | 2053 | Equipment has been directly wired | GE | JEP5030DTBB, JKS5000DNBB, JVX3300DJBB |  | Apartments | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/15894917929 | https://www.formstack.com/admin/download/file/15894917930
2024-02-08 10:30 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-07 | 2024-02-06 | 329B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE APAPRTMENT HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15895555426
2024-02-08 10:42 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-07 | 2024-02-06 | 323 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCES | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15895631526
2024-02-08 10:54 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-07 | 2024-02-06 | 373 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15895712329
2024-02-08 10:57 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-07 | 2024-02-06 | 377 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SJ355 |  | SFFORADABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15895729221
2024-02-08 10:59 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-10 | 2024-02-09 | 379 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15895744487
2024-02-08 11:02 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-10 | 2024-02-09 | 381 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15895762512
2024-02-08 15:50 | matthew | poole | 12878 | 85 Townsend st |  | Pepperell | MA | 1463 | 978 549 5101 | master electrician |  | siemens QF230A | Breaker | QPF | 30 |  | 2 Pole | Siemens | Residence |  | 2024-02-05 | 2024-01-28 | 112 Dalton rd |  | Belmont | MA | 2478 | trips on oven activation | bosch | hbn5451uc/07 |  | kitchen | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15897667450
2024-02-09 10:26 | Daniel | Collette | 11260 | 9 Walter Dr |  | ware | MA | 1082 | 413-813-9357 | Master Electrician |  | GFTCB50 | Breaker | BR style | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-16 | 2022-02-15 | 6 Keith David Drive |  | Millbury | MA | 1527 | Initial powerup of range caused GFCI function of circuit breaker to trip. Per normal troubleshooting procedures, range was allowed to operate on a non-GFCI type circuit breaker to allow manufacturing oils to burn off of resistive elements. Upon re-installation of GFCI breaker, range top would function normally, but oven elements would trip GFCI breaker upon cycling. Element would power up and get hot, GFCI would trip when element was cycled ""off"". Re-installed non-GFCI type breaker. | General Electric | JB645DK9WW | none | Apartment | Kitchen range circuit. | No | Yes | No | No | https://www.formstack.com/admin/download/file/15900989159 | https://www.formstack.com/admin/download/file/15900989160
2024-02-09 13:03 | Brian | Bradley | 20351 | 266 Sudbury Street |  | Marlborough | MA | 1752 | 9782128014 | Master Electrician |  | Eaton - GFTCB230 | Breaker | BR GFCI | 30 |  | 2 Pole | Eaton | Residence |  | 2024-01-08 | 2024-01-08 | 667 Wellesley Street |  | Weston | MA | 2493 | When installing an Eaton 2 pole 30 Amp GFCI breaker for the installation of a new dedicated circuit for a infrared sauna, the breaker will nuisance trip when operating the sauna. The manufacturer clearly states that if you install a GFCI with the sauna in will nuisance trip on the first page of its manual. | Hallmark InfraSauna IS565 | 70-0151 | none (dedicated circuit) | Single Family | Only the dedicated sauna circuit is affected. | No | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/15901930343 | https://www.formstack.com/admin/download/file/15901930345
2024-02-09 17:47 | Samuel | Sanchez | 57482 | 31 Tufts St |  | Somerville | MA | 2145 | 8577708114 | Electrician |  | LB120-DFT | Breaker | na | 50 |  | 2 Pole | Leviton | Commercial |  | 2024-01-05 | 2023-10-25 | [5 empty] | The breakers in units that are tripping due to the Oven GE Appliance being incompatible with the ""GFCI protective devices"". | Electric Range oven 24"" | RAS300DMWW |  | Apartment Unit | Room¦101 2 1130A2 Electric Range oven 30"" JBS360DMWW¦102 1 1130A1 Electric Range oven 24"" RAS300DMWW¦103 1 1130A1 Electric Range oven 24"" RAS300DMWW¦104 4 1130A2 Oven Electric Range 30"" JBS360DMWW¦201 2 1130A2 Electric Range oven 30"" JBS360DMWW¦202 1 1130A1 Electric Range oven 24"" RAS300DMWW¦203 1 1130A1 Electric Range oven 24"" RAS300DMWW¦204 1 1130A2 Electric Range oven 24"" RAS300DMWW¦205 3 1130A2 Oven Electric Range 30"" JBS360DMWW¦206 3 1130A2 Oven Electric Range 30"" JBS360DMWW¦301 2 1130A2 Electric Range oven 30"" JBS360DMWW¦302 1 1130A1 Electric Range oven 24"" RAS300DMWW¦303 1 1130A1 Electric Range oven 24"" RAS300DMWW¦304 1 1130A1 Electric Range oven 24"" RAS300DMWW¦305 3 1130A2 Oven Electric Range 30"" JBS360DMWW¦306 3 1130A2 Oven Electric Range 30"" JBS360DMWW¦¦¦ | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15903950257
2024-02-10 17:11 | JAMES | FOSTER | 20014 | 209 Eliot Street | Eliot St | Milton MA 02186 | MA | 2186 | 16173220095 | OWNER |  | EATON BR50A | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2024-01-03 | 2023-08-11 | 99-101 WALDECK ST |  | BOSTON | MA | 2186 | 24 BREAKERS ARE TRIPPING WHICH ARE CONNECTED TO A GE STOVE. THE GE STOVE IS NOT COMPATABLE WITH THE BREAKERS | GE STOVE | GE ELECTRIC STOVE |  | KITCHEN | KITCHEN | Yes | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15906684037
2024-02-12 10:55 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MATER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-08 | 2024-02-07 | 285 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655KSK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15911483832
2024-02-12 10:58 | Brian | Bradley | 20351 | 266 Sudbury Street |  | Marlborough | MA | 1752 | 9782128014 | Master Electrician |  | BU-MP240GFA | Breaker | GFCI Breaker | 40 |  | 2 Pole | Siemens | Residence |  | 2024-01-11 | 2024-01-11 | 31 Sears Road |  | Weston | MA | 2493 | When installing an Siemens 2 pole 40 Amp GFCI breaker for the installation of¦a new dedicated circuit for a infrared sauna, the breaker will nuisance trip¦when operating the sauna. The manufacturer clearly states that if you¦install a GFCI with the sauna in will nuisance trip on the first page of its¦manual. | Finnleo - Sisu | Sisu-PS57 | dedicated circuit | Single Family | Only dedicated sauna circuit affected. | No | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/15911498349 | https://www.formstack.com/admin/download/file/15911498350
2024-02-12 11:06 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-09 | 2024-02-08 | 287 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15911553645
2024-02-12 11:11 | MICHAEL | ONEIL | 223465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-09 | 2024-02-08 | 321 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15911587605
2024-02-12 11:18 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-14 | 2024-02-13 | 56 HIGH CREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15911636829
2024-02-12 11:24 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-08 | 2024-02-07 | 55 HIGH CREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE APARTMENTS | kITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15911671384
2024-02-12 11:27 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-08 | 2024-02-06 | 61 HIGH CREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SJ355 |  | AFFORDABLE APPLIANCE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15911696896
2024-02-12 11:30 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | G FTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-09 | 2024-02-08 | 67 HIGH CREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15911716463
2024-02-12 11:35 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-08 | 2024-02-07 | 71A HIGH CREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15911747213
2024-02-12 11:37 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-09 | 2024-02-08 | 71B HIGH CREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15911762375
2024-02-12 11:40 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-10 | 2024-02-09 | 73A HIGH CREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15911778211
2024-02-12 11:42 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-10 | 2024-02-09 | 73B HIGH CREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15911793827
2024-02-12 18:45 | James | Duffy | 10505 | 239 boston st |  | TOPSFIELD | MA | 01983-2215 | 7819106589 | licensed electrician |  | siemens | Breaker | circuit breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2024-01-18 | 2024-01-01 | 120 Middlesex Rd |  | Chestnuthill | MA | 2467 | shortly after oven has been activated GFCI breaker trips off. | Thernador | prd366whu | nothing | kitchen | kitchen cooking | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15914456948
2024-02-12 21:02 | Steve | Laurencio | 18079 | 6 Powers Court |  | Lexington | MA | 2421 | 978 621-7221 | Electrician |  | Siemens QPF2 | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2024-02-12 | 2024-02-12 | [5 empty] | Circuit breaker trips on preheat. | Wolf double oven | DO3060TE/8/T | No | Single family | Kitchen wall oven | No | No | No | No |  | https://www.formstack.com/admin/download/file/15914977138
2024-02-13 11:41 | Preferred | Electrical Corp | 15019 | 1764 Main street | Tewsbury | Tewksbury Ma 01 | MA | 1876 | 16175902287 | President |  | Square D HOM250GFICP | Breaker | none | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2023-12-18 | 2023-12-18 | 8 Anthony Rd |  | Lexington | MA | 2420 | The oven trips instantly when turned on. Called manufacturer and was informed that the oven will not work on a GFCI breaker. | Wolf Induction Range and oven | #IR36550/S/T | NO | single family home | Kitchen oven | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15917369941
2024-02-14 11:06 | NALBO | CAMPOS | 14831 | 38 GARLAND ST |  | EVERETT | MA | 2149 | 6172598501 | LICENSED ELECTRICIAN/OWNER |  | HOM250GFIC | Breaker | HOM HACR TYPE CARR | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/15922713812 | 2024-02-09 | 2024-02-09 | Dual Fuel Range |  | 653 Main St | MA | 1742 | GFCI will trip immediately when range is turned on. Homeowner contacted manufacturer which told homeowner not to install the appliance on a GFCI protected circuit. This appliance is delivered with a manufactured installed 4 prong range plug in cord. | LA CORNUE | 44 SERIES | NONE | SINGLE FAMILY | KITCHEN | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/15922713826 | https://www.formstack.com/admin/download/file/15922713829
2024-02-14 13:34 | Theresa | Smith | 51290 | 52 Amherst Rd |  | Pelham | MA | 1002 | 617-682-5954 | Homeowner |  | Eaton GFTCB240 | Breaker | breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2024-02-01 | 2024-01-23 | [5 empty] | Circuit tripped when oven was preheating | Frigidaire | GCRE3060AFE | Nothing | Single family home | Kitchen | No | Yes | No | No
2024-02-14 13:49 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE |  | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-06 | 2024-02-05 | 327A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | THE RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD HAS REACHED AMPERAGE | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15923824144
2024-02-14 13:53 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-06 | 2024-02-05 | 327B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | THE RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD HAS REACHED AMPERAGE | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN¦ | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15923850470
2024-02-14 13:58 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-06 | 2024-02-05 | 329A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | THE RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD HAS REACHED AMPERAGE | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15923877670
2024-02-14 14:02 | MICHAEL | ONEIL | 23466 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-06 | 2024-02-05 | 311 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | THE RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD HAS REACHED AMPERAGE | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15923904212
2024-02-14 14:05 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 1 Pole | Eaton | Residence |  | 2024-02-06 | 2024-02-05 | 313 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | THE RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD HAS REACHED AMPERAGE | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15923922825
2024-02-14 14:09 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-14 | 2024-02-14 | 313 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | THE RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD HAS REACHED AMPERAGE | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15923947205
2024-02-14 14:11 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-06 | 2024-02-05 | 383 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | THE RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD HAS REACHED AMPERAGE | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15923965249
2024-02-14 14:14 | MICHAEL | ONEIL | 23463 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-06 | 2024-02-05 | 385 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | THE RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD HAS REACHED AMPERAGE | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15923979232
2024-02-14 14:16 | MICHAEL | ONEIL | 23463 | 14 NORFOLK AVE |  | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-06 | 2024-02-05 | 387 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | THE RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD HAS REACHED AMPERAGE | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/15923993091
2024-02-14 14:33 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE |  | EASTON | MA | 2375 | 5085358001 | master electrician |  | gftcb250 | Breaker | breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-06 | 2024-02-05 | 375 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | THE RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD HAS REACHED AMPERAGE | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15924104044
2024-02-15 11:35 | Timothy | Burgess | 8338 | 138 Lovejoy Rd |  | Andover | MA | 1810 | 978-604-5562 | Owner |  | THQL2140 | Breaker | THQL | 40 |  | 2 Pole | Eaton | Residence |  | 2023-02-15 | 2023-01-26 | 91 Bennington St |  | East Boston | MA | 2128 | Electric range continues to trip on a GFCI breaker. All actions have been taken to fix the problem with no success. | Beko Electric Range | PRIR34452SS |  | Kitchen | Stove is not usable with this tripping issue. | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15928729735
2024-02-15 12:46 | Ray | Ostroski | 16764 | 100 Trade Center | Suite G 700 | Woburn | MA | 1801 | 7818380703 | Owner |  | Chn240gf | Breaker | breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2024-02-15 | 2024-02-15 | 100 Trade Center, Suite G 700, Woburn MA 01801 |  | 7 dove lane | MA | 1844 | Stove trips when 2 pole GFI is put under load. | Jenn Air | JIC4536KS |  | Single Family | Kitchen Cooktop | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15929203831
2024-02-15 12:58 | Ray | Ostroski | 16764 | 100 Trade Center | Suite G 700 | woburn | MA | 1801 | 7818380703 | owner |  | Chn240gf | Breaker | gfci | 40 |  | 2 Pole | Eaton | Residence |  | 2024-02-15 | 2024-02-15 | 3 Cardinal Rd |  | Methuen | MA | 1844 | breaker trips under load from stove | Jenn Air | JDRP436HL |  | single family | Kitchen Stove | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15929279251
2024-02-15 13:18 | Ray | Ostroski | 16764 | 100 Trade Center | Suite G 700 | Woburn | MA | 1801 | 7818380703 | Owner |  | Chn240gf | Breaker | gfci | 40 |  | 2 Pole | Eaton | Residence |  | 2024-02-15 | 2024-02-15 | 9 dove lane |  | methuen | MA | 1844 | breaker trips when put under load by wall oven | kitchenaid | kose500ess |  | Single Family | Kitchen oven | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/15929408876
2024-02-15 13:30 | Ray | Ostroski | 16764 | 100 Trade Center | Suite G 700 | woburn | MA | 1801 | 7818380703 | owner |  | Cnh240gf | Breaker | gfci | 40 |  | 2 Pole | Eaton | Residence |  | 2024-02-15 | 2024-02-15 | 11 dove lane |  | methuen | MA | 1844 | breaker trips when put under load from oven | kitchenaid | KOSE500ESS |  | single family | kitchen oven | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15929486220
2024-02-19 09:05 | Brian | Ferreira | 53423 | 29 James st. |  | Taunton | MA | 2780 | 5087381950 | Electrician |  | square d homeline 2 pole 50a gfci breaker | Breaker | N/a | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-02-19 | 2024-02-19 | 6 September st. |  | Worcester | MA | 2780 | Every time the range got to temperature 450 it would trip the breaker in the basement | Amana | W10246520A | Nothing | Single family | It's the range in the kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15943327577
2024-02-20 08:55 | Aramis | Weimann | 59274 | 1 Rocky Brook Drive |  | Huntington | MA | 1050 | 4136855169 | Electrician |  | 4884006004 | Breaker | Breaker | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/15948284024 | 2024-02-20 | 2024-01-30 | 187 Brickyard Road |  | Southampton | MA | 1073 | stove has been tripping the breaker. Once when one burner and the oven was on. Twice when just the oven was on. | Frigidaire Gallery | GCRE3038AFD |  | Kitchen stove | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/15948284037 | https://www.formstack.com/admin/download/file/15948284038
2024-02-21 10:41 | Andrew | Woodford | 21637 | 74 Sand St |  | Gardner | MA | 1440 | 978-730-8870 | President |  | Eaton BR250GFI | Breaker | None | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-21 | 2023-06-06 | [5 empty] | After several calls from the home owner complaining the breaker keeps tripping. We changed the GFI breaker, and still the breaker trips in mid-charge. | Tesla charger | 1101789-00-J | none | single family | Garage EV charger only | No | No | No | No |  | https://www.formstack.com/admin/download/file/15954617982
2024-02-21 10:50 | Andrew | Woodford | 21637 | 74 Sand St |  | Gardner | MA | 1440 | 978-730-8870 | President |  | Eaton BR250GFI | Breaker | None | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-21 | 2023-06-06 | [5 empty] | After several calls from the home owner complaining the breaker keeps tripping. We changed the GFI breaker, and still the breaker trips in mid-charge. | Tesla charger | 1101789-00-J | none | single family | Garage EV charger only | No | No | No | No |  | https://www.formstack.com/admin/download/file/15954669040
2024-02-21 11:00 | Matthew | Betz | 53103 | 9 Stoughton St |  | Medford | MA | 2155 | 6175494108 | Home owner |  | QA120AFC | Breaker | NA | 20 | NA | 1 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15954742768 | 2023-08-01 | 2019-07-16 | 7 Stoughton St |  | Medford | MA | 2155 | Hello,¦¦I have been working with two electricians to resolve unwanted breaker arc fault trips since August 2023. I have spent over $10,000 to resolve the issues. As the homeowner, I have done everything to correct the issue and comply with our state electrical codes, but this is too much. Per my conversation with Joe Hurley (Electrical inspector in Medford) this form can also be used for unwanted Arc Fault breaker trips too. Joe stated this is the process to get a waiver from the state to go back to the old style breakers (non Arc fault).¦¦Attached to this form is a PDF that details all the work that was done and the investigation to resolve the issues. If for some reason there is an issue with the attachment, please email me at: mike.betzjr@gmail.com or call my cell at: 617-549-4108¦¦Thanks!¦¦Matthew Betz | Many - See attached investigation document | Many - See attached investigation document | Many - See attached investigation document | 2 Family | See attached document. Requesting a waiver to remove all Arc Fault breakers from the residence located at: 7 Stoughton St (Unit 2) Medford MA 02155 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/15954742782 | https://www.formstack.com/admin/download/file/15954742783
2024-02-21 12:15 | Chrstopher | Frawley | 34375 | 79 | WILSON AVE | WEYMOUTH | MA | 2188 | 16177506955 | president |  | eatongftcb240 | Breaker | breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2024-02-21 | 2024-02-21 | 79 plymouth ave |  | braintree | MA | 2184 | replaced breaker twice with new stove and cord | ge stove | 6099887 |  | resedential | stove in kitchen | No | No | Yes | No | https://www.formstack.com/admin/download/file/15955309630 | https://www.formstack.com/admin/download/file/15955309631
2024-02-22 08:03 | Timothy | Burgess | 8338 | 138 Lovejoy Rd |  | Andover | MA | 1810 | 978-604-5562 | Owner |  | THQL2140 | Breaker | THQL | 40 |  | 2 Pole | Eaton | Residence |  | 2023-02-15 | 2023-01-26 | 91 Bennington St |  | East Boston | MA | 2128 | Electric range continues to trip on a GFCI breaker. All actions have been taken to fix the problem with no success. | Beko Electric Range | PRIR34452SS |  | Kitchen | Stove is not usable with this tripping issue. | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15959775818
2024-02-22 13:33 | John | Vespa | 17144 | 250 Milton St |  | Dedham | MA | 2026 | 617 325 1151 | Owner |  | GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2024-01-25 | 2024-03-30 | [5 empty] | Range nuisance tripping | Cafe | CHS950P |  | kitchen | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15961652320
2024-02-22 14:57 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 347 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15962274602
2024-02-22 15:01 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB23465 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 353 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15962296701
2024-02-22 15:09 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 359A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15962345689
2024-02-22 15:18 | MICHAEL | ONEIL | 0 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 359D BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15962435566
2024-02-22 15:22 | MICHAEL | ONEIL | 0 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 359B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15962460926
2024-02-22 15:45 | MICHAEL | ONEIL | 0 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 359C BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15962642527
2024-02-22 15:57 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 361 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15962727488
2024-02-22 16:01 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 363 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15962750710
2024-02-22 16:13 | MICHAEL | ONEIL | 0 | 14 NORFOLK AVE |  | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 365 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15962830276
2024-02-22 16:15 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 367 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15962843197
2024-02-22 16:18 | MICHAEL | ONEIL | 0 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 369 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15962860566
2024-02-22 16:21 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 371 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15962875459
2024-02-22 16:23 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 68 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15962889986
2024-02-26 07:44 | Lorenzo | Arpini | 56262 | 74 Chapel St | #2 | Lowell | MA | 1852 | (781)866-0616 | Owner |  | ICB SH | Breaker | NA | 30 |  | 2 Pole | Schneider Electric | Commercial |  | 2024-02-24 | 2024-02-24 | 1144 Thorndike St |  | Plamer | MA | 1069 | Once machine is plugged in takes a few minutes to trip circuit breaker | Bunn | ICB SH, 120/208 SST W/WRLS 3500 WATT(DD) |  | COMERCIAL | SALES AREA | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15976205267
2024-02-26 07:58 | Lorenzo | Arpini | 0 | 74 Chapel St | 2 | Lowell | MA | 1852 | 7818660616 | owner |  | QO230GFI | Breaker | NA | 30 |  | 2 Pole | Schneider Electric | Commercial |  | 2024-02-24 | 2024-02-24 | 1144 Thorndike St |  | Plamer | MA | 1069 | Circuit breaker will trip a few minutes after appliance is plugged in | Hatco corporation | 2840242301 |  | Comercial | Sales area | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15976247294
2024-02-26 08:07 | Lorenzo | Arpini | 0 | 74 CHAPEL ST | 2 | Lowell | MA | 1852 | 7818660616 | Owner |  | QO230GFI | Breaker | NA | 30 |  | 2 Pole | Schneider Electric | Commercial |  | 2024-02-24 | 2024-02-24 | 1144 Thorndike St |  | Palmer | MA | 1069 | Breaker trips a few minutes after machine is plugged in | Schaerer | 7109 |  | NA | Sales Area | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15976281877
2024-02-26 08:12 | [11 empty] | QO230GFI | Receptacle | NA | 30 |  | 2 Pole | Schneider Electric | Commercial |  | 2024-02-24 | 2024-02-24 | 1144 Thorndike St |  | Palmer | MA | 1069 | Breaker Trips after a few minutes machine is plugged in | Schaerer | 7109 |  | NA | Sales Area | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/15976297154
2024-02-26 12:39 | Antoni | Pietrzykowski | 12958 | 4 open square way |  | Holyoke | MA | 1040 | 4134277624 | Electrician |  | Square D | Breaker | N/A | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-02-26 | 2024-02-26 | 785 Franklin Street |  | Belchertown | MA | 1007 | Breaker trips when oven is preheated. | Samsung | Dg68-00100b-01 | N/a | Single family home | Stove in kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/15978070809
2024-02-26 12:49 | Antoni | Pietrzykowski | 12958 | 4 Open Square |  | Holyoke | MA | 1040 | 4134277624 | Electrician Them |  | Square D | Breaker | N/A | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2024-02-26 | 2024-02-26 | 785 Franklin Street |  | Belchertown | MA | 1007 | Drying trips breaker after a few minutes | Samsung | GFD45essm1ww |  | House | Dryer basement | No | No | No | No |  | https://www.formstack.com/admin/download/file/15978136627
2024-02-28 08:55 | Curran | Jason | 21794 | 2 Cross Street |  | Douglas | MA | 1516 | 774-239-0488 | Master Electrician |  | Eaton CH250GFT | Breaker | GFCI breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-28 | 2024-02-28 | 67 Holman Street |  | Shrewsbury | MA | 1545 | Range trips breaker while being plugged in and not being used. | XOB | XOB30SC |  | Single Family Residence | Kitchen. | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15990920048
2024-02-28 09:06 | Jason | Curran | 21794 | 2 Cross Street |  | Douglas | MA | 1516 | 774-239-0488 | Master Electrician |  | Square D/HOM250GFICP | Breaker | GFCI breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-02-26 | 2024-02-26 | 59 Davis Hill Road |  | Paxton | MA | 1612 | Range tripping while plugged in and while not in use. | Thermador | PRD486WDHU |  | Single Family Residence | Kitchen. | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15990972133
2024-02-28 11:38 | Phillip | Aiello | 23342 | 399 Page St. |  | Lunenburg | MA | 1462 | 9788360515 | Master/Owner |  | Q120DF | Breaker | Dual function | 20 |  | 1 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/15991902461 | 2024-02-21 | 2024-02-21 | 152 Betty Ann Lane |  | Dracut | MA | 1826 | Ran new 20 amp circuit to fridge location in kitchen remodel. Tripped within an hour, reset and circuit kept tripping every ten minutes after. Swapped with new breaker and tried different spot in panel, circuit is still tripping. Brand new Frigidaire fridge and brand new wire and breaker. | Frigidaire | PRMC2285AF05 |  | Single family home | Kitchen refrigerator location, dedicated circuit | No | No | No | No | https://www.formstack.com/admin/download/file/15991902474 | https://www.formstack.com/admin/download/file/15991902475
2024-02-28 12:09 | Aaron | Conte | 21428 | Po Box 1525 |  | Newburyport | MA | 1950 | 9785025213 | VP |  | LB250-GS | Breaker | none | 50 |  | 2 Pole | Leviton | Residence |  | 2024-01-25 | 2024-02-05 | 122 Washington St |  | Topsfield | MA | 1983 | Breaker trips when is heating up. | Thermador | PRD486WDHU/06 |  | Home | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/15992116521
2024-02-28 12:21 | Aaron | Conte | 0 | Po box 1525 |  | newburyport | MA | 1950 | 9785025213 | VP |  | R03-LB230-GFR | Breaker | none | 30 |  | 2 Pole | Leviton | Residence | https://www.formstack.com/admin/download/file/15992196272 | 2024-01-26 | 2024-01-08 | 122 Washington St |  | Topsfield | MA | 1983 | Breaker trips occasionally while in cycle | Electrolux | ELFE7537AW1 |  | Home | Laundry room | No | Yes | No | No | https://www.formstack.com/admin/download/file/15992196285 | https://www.formstack.com/admin/download/file/15992196286
2024-02-28 12:35 | Aaron | Conte | 21428 | po box 1525 |  | newburyport | MA | 1950 | 9785025213 | VP |  | LB115-DFT | Breaker | none | 15 |  | 1 Pole | Leviton | Residence |  | 2024-01-19 | 2024-01-08 | 122 washington st |  | Topsfield | MA | 1983 | Breaker randomly trips | Thermador | T36FT820NS |  | Home | Kitchen | No | Yes | No | No | https://www.formstack.com/admin/download/file/15992401233 | https://www.formstack.com/admin/download/file/15992401234
2024-02-28 12:49 | Michael | Chesley | 11192 | 31 Hunt Rd |  | Kingston | NH | 3848 | 9782656865 | Owner |  | Qf250ap | Breaker | None | 50 |  | 2 Pole | Siemens | Residence |  | 2024-02-28 | 2024-02-28 | 17 larcom |  | Beverly | MA | 1915 | Breaker instantly trips when stove is plugged in. I talked to the manufacturer. They said to remove the gfci breaker | Electrolux | ECFI3668AS | None | Home | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15992494795
2024-02-28 12:52 | Michael | Chesley | 11192 | 31 Hunt Rd |  | Kingston | NH | 3848 | 9782656865 | Owner |  | Qf240 | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-28 | 2024-02-28 | 17 Larcom |  | Beverly | MA | 1915 | Breaker trips when oven is running randomly. I talked to the manufacturer. They said to remove the gfci breaker. | Electrolux | Ecwm3011asa | None | Home | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/15992517711
2024-02-28 20:31 | Phillip | Aiello | 23342 | 399 Page st |  | Lunenburg | MA | 1462 | 9788360515 | owner |  | Q120DF | Breaker | dual function | 20 |  | 1 Pole | Siemens | Residence |  | 2024-02-21 | 2024-02-21 | 152 Betty Ann Lane |  | Dracut | MA | 1826 | Ran new 20 amp circuit to fridge location in kitchen remodel. Tripped within an hour, reset and circuit kept tripping every 10 minutes after. Swapped with new breaker and tried a different spot in the panel. Circuit is still tripping. Brand new Frigidaire fridge and brand new homerun from panel and brand new breaker.¦ | Frigidaire | PRMC2285AF05 | homerun | single family home | Kitchen refrigerator location, dedicated circuit. | No | No | No | No | https://www.formstack.com/admin/download/file/15995165838 | https://www.formstack.com/admin/download/file/15995165839
2024-02-29 11:30 | Brett | Duca | 20266 | 10 n row rd |  | Sterling | MA | 1564 | 7746963707 | Owner |  | Gftcb240 | Breaker | Na | 40 |  | 2 Pole | Eaton | Residence |  | 2024-02-19 | 2024-02-16 | 21 monadnock st |  | Worcester | MA | 1609 | Double wall oven, new install. Oven turns on begins to preheat, after 30 seconds of heating breaker trips. Replaced breaker 3 times to rule out faulty breaker. | Ge | 191d2424g220 |  | Single fam | Kitchen wall oven | No | No | No | No | https://www.formstack.com/admin/download/file/15997777446 | https://www.formstack.com/admin/download/file/15997777447
2024-02-29 14:16 | Brooke | Heisler-Leary | 58767 | 72 wrentham rd |  | Springfield | MA | 1119 | 4132658094 | Electrician |  | 4884006004 | Breaker | N/A | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/15998918807 | 2024-02-29 | 2024-02-29 | [5 empty] | Range use trips breaker | Amana | AER6203MFS5 |  | Kitchen | Kitchen range | No | No | No | No |  | https://www.formstack.com/admin/download/file/15998918819
2024-02-29 18:17 | Anthony | Beaulieu | 20630 | 30 Lynn St |  | Lawrence | MA | 1843 | 6172016510 | Owner |  | us2:QF240AP | Breaker | Siemens | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-25 | 2024-02-25 | 30 Lynn St |  | Lawrence | MA | 1843 | Trips as soon as you turn the oven on | Bosh | us2:QF240AP |  | Kitchen | Kitchen oven | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16001040541
2024-03-01 15:40 | Brooke | Heisler-Leary | 58767 | 72 wrentham rd |  | Springfield | MA | 1119 | 4132658094 | Electrician |  | 4884006004 | Breaker | N/A | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16005993414 | 2024-02-29 | 2024-02-29 | [5 empty] | Range use trips breaker | Amana | AER6203MFS5 |  | Kitchen | Kitchen range | No | No | No | No |  | https://www.formstack.com/admin/download/file/16005993430
2024-03-01 15:45 | Brooke | Heisler-Leary | 58767 | 29 North County Rd |  | Florida | MA | 1247 | 4132658094 | Electrician |  | 488006004 | Breaker | Square D Homeline | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16006024201 | 2024-03-01 | 2024-03-01 | [5 empty] | Tripped during oven preheat | GE | JBP72T0K2WW |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16006024213
2024-03-04 15:26 | Kyle | Hammond | 21301 | 68 Eden Park Dr |  | North Attleboro | MA | 2760 | 5088384695 | Electrician |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-04 | 2024-03-04 | 37 Pleasant Lake Ave |  | Harwich | MA | 2645 | Installed multiple GFCI breakers for the range in this new home which tripped. Checked circuit and all connections everything is correct. Breaker does not trip until range is plugged in. | Bosch | HIS8655U | None | Single family | Kitchen range | No | No | No | No |  | https://www.formstack.com/admin/download/file/16016172886
2024-03-04 15:35 | Kyle | Hammond | 21301 | 68 Eden Park Dr |  | North Attleboro | MA | 2760 | 5088384695 | Electrician |  | LB250-G | Breaker | Breaker | 50 |  | 2 Pole | Leviton | Residence |  | 2024-02-08 | 2024-02-08 | 13 Emily Rd |  | Attleboro | MA | 2703 | Installed multiple GFCI circuit breakers for new electric range. All tripped when the range was turned on. Checked circuit and all connections, everything was correct. | Bosch | HIIP057U | None | Single family | Kitchen range | No | No | No | No |  | https://www.formstack.com/admin/download/file/16016239905
2024-03-05 14:04 | Michael | Conlon | 53904 | 18 SAWMILL RD |  | pelham | NH | 3076 | 9785513723 | Journeyman |  | ITE QF 250A | Breaker | NA | 50 |  | 2 Pole | Siemens | Residence |  | 2024-02-12 | 2024-02-12 | 13 Grist Mill RD |  | Acton | MA | 1720 | Brand new Induction range trips GFCI circuit breaker immediately when plugged in. | Electrolux | ECFI3668AS |  | Kitchen | Kitchen Range | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16021574707
2024-03-06 11:29 | Roy | Brooks | 14302 | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner |  | GFTCB250 | Breaker | Standard | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-27 | 2024-02-27 | 3 Montauk Avenue |  | Norfolk | MA | 2056 | Stove immediately tripped when breaker was on. Replaced with 50-amp regular breaker, ran for (1) hour to see if it would dry out any moisture within the stove wiring. Re-installed GFCI breaker and it still continued to trip, so installed 2-pole 50-amp Eaton breaker. Tripping issue resolved. | Frigidaire Stove | PCF13670AF |  | Kitchen | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16026456368
2024-03-06 11:53 | Devereau | Williams | 12118 | 22 Line street Unit D |  | Somerville | MA | 2143 | 617-529-1839 | Sole Proprietor/Owner |  | SIEQF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-02-29 | 2024-02-29 | 7 porter park |  | Cambridge | MA | 2140 | After Installing the GFCI breakers, the breakers would not hold. It only held when the new oven was not plugged in. (4 wires each two ovens) ¦After talking with other electricians, it appears that it's a common problem where the MFG needs to adopt the code requirements. I installed power for 2 ovens, and both had the same results. Two regular two pole breakers are installed.¦ | LG | LREL6321S | None | 2 family/kitchen oven | In each unit both dedicated ovens, that are from separate panels the GFCI will not hold. | No | No | No | No | https://www.formstack.com/admin/download/file/16026615984 | https://www.formstack.com/admin/download/file/16026615985
2024-03-06 12:22 | Tom | Juzba | 56789 | 25 Harrison ave |  | Greenfield | MA | 1301 | 4138871798 | Electrician |  | AD-910 | Breaker | Na | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16026815926 | 2024-03-06 | 2024-03-06 | [5 empty] | Turned oven on to bake at 350f. Breaker tripped. Tried again and breaker continued to trip. | Samsung | Ne59m4310ss | None | 1 family home | Kitchen oven | No | No | No | No | https://www.formstack.com/admin/download/file/16026815946 | https://www.formstack.com/admin/download/file/16026815947
2024-03-06 13:37 | Paul | Harris | 20510 | 95 Rounsevell Rd |  | Tewksbury | MA | 1876 | 617-212-7946 | Journeyman & Master Electrican |  | Leviton, Dual Function Circuit Breaker / LB120-DFT | Breaker | Breaker | 20 |  | 1 Pole | Leviton | Residence | https://www.formstack.com/admin/download/file/16027288417 | 2024-02-02 | 2024-02-02 | 49 Brentwood Rd |  | Tewksbury | MA | 1876 | GFCI Trip shortly after refrigerator is plugged in | Samsung Refrigerator Freezer combo, date of manufacture May 2013 | RFG297HDRS | None | Kitchen | One kitchen receptacle & one dining room receptacle. I installed a single receptacle for refrigerator/ freezer unit. Note the circuit is now connected to a Leviton 20 amp arc fault circuit breaker. | No | Yes | No | No | https://www.formstack.com/admin/download/file/16027288431 | https://www.formstack.com/admin/download/file/16027288432
2024-03-07 08:36 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-28 | 2024-02-27 | 357 HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING APARTMENT | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16031261858
2024-03-07 08:43 | Aramis | Weimann | 59274 | 1 Rocky Brook Dr |  | Huntington | MA | 1050 | 4135059515 | Electrician |  | 4884006004 | Breaker | None | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16031288607 | 2024-03-07 | 2024-02-22 | 11 Old Point St. |  | Springfield | MA | 1109 | Breaker was Nuisance tripping while using the stove and randomly throughout the day | Amana | AER6303MFS3 | None | Single Family House | Kitchen Stove | No | No | No | No | https://www.formstack.com/admin/download/file/16031288621 | https://www.formstack.com/admin/download/file/16031288622
2024-03-07 17:29 | Christopher | Trites | 40129 | 7 Kosciusko St |  | Woburn | MA | 01801-3863 | 7815898967 | Manager/Electrician |  | Eaton GFTCB250 | Breaker | 2 pole 50 GFCI breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2023-01-01 | 2023-06-28 | 46 Turning Mill Road |  | Lexington | MA | 2420 | Trip randomly at night | Samsung | NE63B8611SS | no | Kitchen | Kitchen Electric Range | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/16034952774
2024-03-07 21:50 | Evan | Carter | 0 | 157 Oakridge Ave |  | N. Attleboro | MA | 2760 | 5086431425 | Owner |  | Eaton GFCB250 | Breaker | 2 Pole 50 Amp GFCI | 50 |  | 2 Pole | Eaton | Residence |  | 2024-02-20 | 2024-02-20 | [5 empty] | Oven continuously trips breaker. Oven neutral and ground not common. Test greater than 80kohms when unplugged. | Whirlpool | WFE510S0AS0 |  | Single Family | Kitchen oven only. | No | No | No | No |  | https://www.formstack.com/admin/download/file/16035945308
2024-03-08 11:42 | Kirk | Backlund | 33462 | 8 Shire Dr | Suite 1 | Norfolk | MA | 2056 | 15083845382 | Owner |  | BRN240GF BRGFCI | Breaker | Panel mount | 40 |  | 2 Pole | Eaton | Residence |  | 2024-03-07 | 2024-03-01 | 340 main st |  | Norfolk | MA | 2056 | Random tripping when range is not in use. | GE | CCES700O4MW2 | NO | Home | Kitchen range | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16038338034
2024-03-08 12:30 | Alexander | Bielunis | 8653 | 29 Tyler Ct |  | Northampton | MA | 1046 | 4132043751 | Manager |  | Square D HOM240GFI | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-03-08 | 2024-03-08 | 29 Tyler Ct |  | Northampton | MA | 1060 | GFCI Trips when Cooktop is turned on | Fisher & Paykel | CID364DTB4 | NONE | 1 Family Home | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16038632922
2024-03-08 12:40 | Brian | Ferreira | 53423 | 29 james st. |  | Taunton | MA | 2780 | 5087381950 | Service electrician |  | 0136057 E82617 | Breaker | Gfci | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-01 | 2024-03-08 | 54 bridge st |  | Hatfield | MA | 1035 | Tripped when range got up to temperature swapped it out to a regular breaker and it stopped tripping. | Ge | 16D3871 P001 | Just the range | House | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16038697932
2024-03-08 13:27 | Nicholas | Blosz | 58100 | 44 Brandeis circle |  | Halifax | MA | 2338 | 7816080162 | Electrician |  | 4884006004 | Breaker | Gcfi 2 pole 50amp | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-03-05 | 2024-03-08 | 26 Falmouth ave unit 3 |  | Brockton | MA | 2301 | The gfci breaker would trip when the oven was turned on. | Frigidaire | GCRE3060AFH | None | Townhouse | Kitchen range | No | No | No | No | https://www.formstack.com/admin/download/file/16038995378 | https://www.formstack.com/admin/download/file/16038995379
2024-03-11 08:10 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #201 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047197599
2024-03-11 08:14 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #202 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047212310
2024-03-11 08:15 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #202 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047212801
2024-03-11 08:16 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #202 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047217445
2024-03-11 08:19 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #203 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047225966
2024-03-11 08:23 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #204 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047241624
2024-03-11 08:27 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #205 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047254205
2024-03-11 08:30 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #206 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047264255
2024-03-11 08:33 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #206 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047274940
2024-03-11 08:36 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #207 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047284045
2024-03-11 08:38 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 471 Page St. #2A |  | Stoughton | MA | 2072 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047292492
2024-03-11 08:41 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #208 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047301094
2024-03-11 08:43 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #211 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/16047309293
2024-03-11 08:45 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #213 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047315941
2024-03-11 08:47 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #214 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047323074
2024-03-11 08:49 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #215 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047330185
2024-03-11 08:51 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #216 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047340068
2024-03-11 08:54 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #217 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047352051
2024-03-11 08:57 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #218 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047360030
2024-03-11 08:58 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #219 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047366996
2024-03-11 09:04 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #301 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047395741
2024-03-11 09:07 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #302 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047408838
2024-03-11 09:12 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF2050A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #303 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047428743
2024-03-11 09:14 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF2050A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #304 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047437050
2024-03-11 09:15 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #305 |  | Allston | MA | 2431 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047444494
2024-03-11 09:17 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #306 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047451852
2024-03-11 09:18 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #307 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047457723
2024-03-11 09:20 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #309 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047464803
2024-03-11 09:22 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #311 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047472348
2024-03-11 09:24 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #313 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047479667
2024-03-11 09:26 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #314 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047490103
2024-03-11 09:27 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #315 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047498558
2024-03-11 09:29 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #316 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047506747
2024-03-11 09:31 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #317 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047514760
2024-03-11 09:32 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #318 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047523817
2024-03-11 09:34 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Commercial |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #319 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047533493
2024-03-11 09:40 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #401 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047560796
2024-03-11 09:41 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Commercial |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #402 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047568072
2024-03-11 09:42 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #404 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047575165
2024-03-11 09:44 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-02 | 45-55 Brighton Ave #404 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047581946
2024-03-11 09:45 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #405 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047590436
2024-03-11 09:47 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #406 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047598529
2024-03-11 09:48 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #407 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047606937
2024-03-11 09:50 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #408 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047614890
2024-03-11 09:51 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #409 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047623282
2024-03-11 09:53 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #411 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047632588
2024-03-11 09:54 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #413 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047638961
2024-03-11 09:55 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #414 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047647759
2024-03-11 09:58 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #415 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047661505
2024-03-11 09:59 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #416 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047670286
2024-03-11 10:01 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #417 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047680302
2024-03-11 10:02 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #418 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047689450
2024-03-11 10:04 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #419 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047696601
2024-03-11 10:05 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #501 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047705721
2024-03-11 10:07 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #502 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047713744
2024-03-11 10:08 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #503 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047722005
2024-03-11 10:09 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #504 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047730827
2024-03-11 10:12 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #505 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047744059
2024-03-11 10:14 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #506 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047755233
2024-03-11 10:16 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #507 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047771978
2024-03-11 10:17 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #507 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047777051
2024-03-11 10:19 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #508 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047788121
2024-03-11 10:20 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #509 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047799756
2024-03-11 10:22 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #511 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047809432
2024-03-11 10:23 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #513 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047818145
2024-03-11 10:25 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #515 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047827852
2024-03-11 10:26 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #516 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047835414
2024-03-11 10:28 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #517 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047848272
2024-03-11 10:30 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #518 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047857982
2024-03-11 10:32 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #515 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047868964
2024-03-11 10:33 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #519 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047879229
2024-03-11 10:36 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #601 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047893529
2024-03-11 10:37 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #602 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047900998
2024-03-11 10:38 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #603 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047910202
2024-03-11 10:40 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #604 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047918955
2024-03-11 10:41 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #605 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047927091
2024-03-11 10:42 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #606 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047935678
2024-03-11 10:43 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #607 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047943355
2024-03-11 10:45 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #608 |  | Allston | MA | 2134 | Breaker trips when oven is turned on | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047952488
2024-03-11 10:46 | Motti Electric | Co. | 8424 | 471 Page St. #2A |  | Stoughton | MA | 2072 | 7813448950 | Electrician |  | QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | 45-55 Brighton Ave #609 |  | Allston | MA | 2134 | Breaker trips when oven is turned on. | Whirlpool | WFE515S0JS1 |  | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16047961176
2024-03-11 15:18 | John | Manning | 52277 | 292 Douglas St |  | Uxbridge | MA | 1569 | 5087695792 | Sole proprietor |  | Siemens/qf250a | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16049826187 | 2024-03-06 | 2024-03-06 | 15 Avondale rd |  | Newton | MA | 2459 | Gfci trips on preheat and when broiler off is pressed. | GE | PHS930YPAFS |  | Single family | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16049826200 | https://www.formstack.com/admin/download/file/16049826201
2024-03-11 15:44 | John | Manning | 52277 | 292!Douglas St |  | Uxbridge | MA | 1569 | 5087695792 | Sole proprietor |  | Siemens Q120DFN 20 Amp | Breaker | Breaker | 20 |  | 1 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16050005970 | 2024-03-05 | 2024-03-05 | 15 Avondale rd |  | Newton | MA | 2459 | Randomly trips gfci breaker | Bosch | B36C80SN*, | None | Single family | Trips gfci randomly | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16050005984 | https://www.formstack.com/admin/download/file/16050005985
2024-03-12 22:53 | Douglas | Boyajian | 22925 | P.O. Box 1231 |  | Arlington | MA | 2474 | 7742442290 | Owner |  | Eaton | Breaker | Plug in | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-12 | 2024-02-22 | 51 Waldorf Rd |  | Newton | MA | 2464 | The GFCI breaker installed and required by current NEC codes trips immediately when connected to the cooktop. I have reached out to the the breaker manufacturer as well as the appliance manufacturer with no resolve. The breaker also tripped after the recommended burning cycle. | Wolf | C136560t/s | None | Single family dwelling | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16058061840
2024-03-13 14:15 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 226 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16061221003
2024-03-13 14:19 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 228 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16061245770
2024-03-13 14:22 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 236 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16061265195
2024-03-13 14:24 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 238 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16061279165
2024-03-13 14:36 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | master electrician |  | gftcb250 | Breaker | breaker |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 293 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16061360238
2024-03-13 14:45 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 301 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16061424894
2024-03-13 14:48 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 303 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16061444922
2024-03-13 15:04 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 263 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16061549957
2024-03-13 15:08 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 265 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | KITCHEN | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16061575505
2024-03-14 10:35 | MICHAEL | ONEIL | 0 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 267 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD APMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16065456846
2024-03-14 10:38 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 273 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD APMERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16065474468
2024-03-14 10:59 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 275 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16065604179
2024-03-14 11:02 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 279 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | ANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16065619279
2024-03-14 11:07 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 281 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | ANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16065648256
2024-03-14 11:10 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 283 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | ANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB+66SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16065672387
2024-03-14 11:12 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 305A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16065687692
2024-03-14 11:14 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 305B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16065701073
2024-03-14 11:16 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 307A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16065713382
2024-03-14 11:19 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 307B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16065729116
2024-03-14 11:21 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 309 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16065742085
2024-03-14 11:45 | Joseph | Camilo | 4414 | 29 Cook Street |  | Billerica | MA | 1821 | 978-663-0292 | Vice President |  | Q120DFN | Breaker | NONE | 20 |  | 1 Pole | Siemens | Commercial |  | 2024-03-01 | 2023-11-01 | 22 Mulberry UNIT 525 |  | Worcester | MA | 1604 | Refrigerator trips either a few minutes or hours after turning on. | Samsung | RT18M6215SR | NO | Apartment | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16065895939 | https://www.formstack.com/admin/download/file/16065895940
2024-03-14 12:00 | Joseph | Camilo | 4414 | 29 Cook Street |  | Billerica | MA | 1821 | 978-663-0292 | Vice President |  | Q120DFN | Breaker | None | 20 |  | 1 Pole | Siemens | Commercial |  | 2024-03-01 | 2023-11-01 | 22 Mulberry UNIT 519 |  | Worcester | MA | 1604 | Refrigerator trips either a few minutes or hours after turning on. | Samsung | RT18M6215SR |  | Apartment | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16065987812 | https://www.formstack.com/admin/download/file/16065987813
2024-03-14 12:08 | Joseph | Camilo | 4414 | 29 Cook Street |  | Billerica | MA | 1821 | 9786630292 | Vice President |  | Q120DFN | Breaker | None | 20 |  | 1 Pole | Siemens | Commercial |  | 2024-03-01 | 2023-11-01 | 22 Mulberry UNIT 412 |  | Worcester | MA | 1604 | Refrigerator trips either a few minutes or hours after turning on. | Samsung | RT18M6215SR | NO | Apartment | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16066039161 | https://www.formstack.com/admin/download/file/16066039162
2024-03-14 12:15 | Steven | Cohen | 14796 | 18 F Street |  | Hull | MA | 2045 | 3394400733 | owner |  | eaton/gftcb240 | Breaker | na | 40 |  | 2 Pole | Eaton | Residence |  | 2024-02-14 | 2024-01-28 | 18 F Street |  |  |  |  | when the homeowner turns on the oven, which is all electric, trips the breaker. Gas burner work | ge | cgs750p4mw2 |  | kitchen | nothing else was affected but the stove | No | No | No | No
2024-03-14 12:15 | Joseph | Camilo | 4414 | 29 Cook Street |  | Billerica | MA | 1821 | 9786630292 | Vice President |  | Q120DFN | Breaker | None | 20 |  | 1 Pole | Siemens | Commercial |  | 2024-03-01 | 2023-11-01 | 22 Mulberry UNIT 414 |  | Worcester | MA | 1604 | Refrigerator trips either a few minutes or hours after turning on. | Samsung | RT18M6215SR | NO | Apartment | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16066089017 | https://www.formstack.com/admin/download/file/16066089018
2024-03-14 12:21 | Joseph | Camilo | 0 | 29 Cook Street |  | Billerica | MA | 1821 | 9786630292 | Vice President |  | Q120DFN | Breaker | NONE | 20 |  | 1 Pole | Siemens | Commercial |  | 2024-03-01 | 2023-11-01 | 22 Mulberry UNIT 425 |  | Worcester | MA | 1604 | Refrigerator trips either a few minutes or hours after turning on. | Samsung | RT18M6215SR | NO | Apartment | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16066125270 | https://www.formstack.com/admin/download/file/16066125271
2024-03-14 12:45 | Joseph | Camilo | 4414 | 29 Cook Street |  | Billerica | MA | 1821 | 9786630292 | Vice President |  | Q120DFN | Breaker | None | 20 |  | 1 Pole | Siemens | Commercial |  | 2024-03-01 | 2023-11-01 | 22 Mulberry UNIT 427 |  | Worcester | MA | 1604 | Refrigerator trips either a few minutes or hours after turning on. | Samsung | RF25C5151SR | NO | Apartment | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16066274210 | https://www.formstack.com/admin/download/file/16066274211
2024-03-14 13:04 | Joseph | Camilo | 4414 | 29 Cook Street |  | Billerica | MA | 1821 | 9786630292 | Vice President |  | Q120DFN | Breaker | NONE | 20 |  | 1 Pole | Siemens | Commercial |  | 2024-03-01 | 2023-11-01 | 22 Mulberry UNIT 314 |  | Worcester | MA | 1604 | Refrigerator trips either a few minutes or hours after turning on. | Samsung | RT18M6215SR | NO | Apartment | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16066393046 | https://www.formstack.com/admin/download/file/16066393049
2024-03-14 14:13 | Nick | McElroy | 22642 | 381 Old Falmouth Rd. | Suite #32 | Marstons Mills | MA | 2648 | 5085664489 | President |  | Eaton / GFTCB240 | Breaker | Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2024-03-14 | 2024-02-28 | 35 Van Duzer Rd |  | Barnstable | MA | 2631 | Customer stated the GFCI would trip upon turning on the bottom oven. Tried changing the breaker and continued to trip. No ground fault in the wire path. | Thermador | PO302W/03 | None | Residential | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16066862799 | https://www.formstack.com/admin/download/file/16066862800
2024-03-14 15:01 | Joseph | Camilo | 4414 | 29 Cook Street |  | Billerica | MA | 1821 | 9786630292 | Vice President |  | Q120DFN | Breaker | None | 20 |  | 1 Pole | Siemens | Commercial | https://www.formstack.com/admin/download/file/16067174235 | 2024-03-01 | 2023-11-01 | 22 Mulberry UNIT 326 |  | Worcester | MA | 1604 | Refrigerator trips either a few minutes or hours after turning on. | Samsung | RT18M6215SR | NO | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16067174249
2024-03-14 15:11 | Joseph | Camilo | 4414 | 29 Cook Street |  | Billerica | MA | 1821 | 9786630292 | Vice President |  | Q120DFN | Breaker | None | 20 |  | 1 Pole | Siemens | Commercial |  | 2024-03-01 | 2023-11-01 | 22 Mulberry UNIT 327 |  | Worcester | MA | 1604 | Refrigerator trips either a few minutes or hours after turning on. | Samsung | RF25C5151SR | NO | Apartment | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16067250038 | https://www.formstack.com/admin/download/file/16067250039
2024-03-14 15:15 | Joseph | Camilo | 4414 | 29 Cook Street |  | Billerica | MA | 1821 | 9786630292 | Vice President |  | Q120DFN | Breaker | None | 20 |  | 1 Pole | Siemens | Commercial |  | 2024-03-01 | 2023-11-01 | 22 Mulberry UNIT 330 |  | Worcester | MA | 1604 | Refrigerator trips either a few minutes or hours after turning on. | Samsung | RT18M6215SR | NO | Apartment | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16067286431 | https://www.formstack.com/admin/download/file/16067286432
2024-03-14 15:25 | Joseph | Camilo | 4414 | 29 Cook Street |  | Billerica | MA | 1821 | 9786630292 | Vice President |  | Q120DFN | Breaker | None | 20 |  | 1 Pole | Siemens | Commercial |  | 2024-03-01 | 2023-11-01 | 22 Mulberry UNIT 227 |  | Worcester | MA | 1604 | Refrigerator trips either a few minutes or hours after turning on. | Samsung | RF25C5151SR | NO | Apartment | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16067349638 | https://www.formstack.com/admin/download/file/16067349639
2024-03-14 15:29 | Joseph | Camilo | 4414 | 29 Cook Street |  | Billerica | MA | 1821 | 9786630292 | Vice President |  | Q120DFN | Breaker | None | 20 |  | 1 Pole | Siemens | Commercial | https://www.formstack.com/admin/download/file/16067375785 | 2024-03-01 | 2023-11-01 | 22 Mulberry UNIT 112 |  | Worcester | MA | 1604 | Refrigerator trips either a few minutes or hours after turning on. | Samsung | RT18M6215SR | No | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16067375799
2024-03-14 15:30 | Joseph | Camilo | 4414 | 29 Cook Street |  | Billerica | MA | 1821 | 9786630292 | Vice President |  | Q120DFN | Breaker | None | 20 |  | 1 Pole | Siemens | Commercial |  | 2024-03-01 | 2023-11-01 | 22 Mulberry UNIT 114 |  | Worcester | MA | 1604 | Refrigerator trips either a few minutes or hours after turning on. | Samsung | RT18M6215SR | NO | Apartment | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16067381441 | https://www.formstack.com/admin/download/file/16067381442
2024-03-15 12:38 | Aramis | Weimann | 59274 | 1 Rocky Brook Dr |  | Huntington | MA | 1050 | 4135059515 | Electrician |  | 4884006004 | Breaker | Breaker | 30 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16071994575 | 2024-03-15 | 2024-03-15 | 17 Pinewood Circle |  | Montague | MA |  | Tripped immediately trying to turn breaker. Made sure everything was separated in dryer. Also breaker held when dryer is not plugged in | Kenmore | 110.6681 |  | Single family | Basement | No | No | No | No | https://www.formstack.com/admin/download/file/16071994588 | https://www.formstack.com/admin/download/file/16071994589
2024-03-16 08:22 | Marcelo | Deoliveira | 59249 | 3102 Homestead Blvd |  | Westboro | MA | 1581 | 7742456470 | electrician |  | eaton | Breaker | br | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-05 | 2024-03-01 | 3102 Homestead Blvd |  | Westboro | MA | 1581 | breaker won't stay on with with the range plugged on , even after ground and neutral were separate at the range | BOSCH INDUCTION RANGE | HIS8055U |  | TOWN HOUSE | KITCHEN | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/16075312222 | https://www.formstack.com/admin/download/file/16075312223
2024-03-17 08:25 | AJ | Tabrizi | 21477 | 10 Regis Rd |  | Andover | MA | 1810 | 9787193610 | president |  | Siemens QF250A | Breaker | 2 pole 50 AMP breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-11 | 2024-03-11 | 65 Plesant street unit 1, unit 2 and unit 3 |  | Brookline | MA |  | We install a 50 AMp GFCI breaker for an induction range. The outlet holds when nothing is plug into it. But as soon as we plug in the oven the GFI trips.¦when we change the GFI breaker to normal breaker, the breaker does not trip and oven will stay on.¦This is a three-unit condo and we have similar problem with all three units. | BOSCH | HIS8655U |  | 3 unit condo | kitchen range.¦this is a three unit condo and we have the same problem with all three kitchen range. | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16077539310
2024-03-18 14:28 | Joyce | Saret | 15503 | 31 Lafayette Lane |  | Norfolk | MA | 2056 | 508-740-8899 | Electrician |  | Eaton GFTCB250 | Breaker | HAGF | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-01 | 2023-12-22 | [5 empty] | Trips when the oven is on. Does not typically trip immediately; it takes a few minutes. | GE Spectra | J BP78W032WW | None | Home | Oven only | No | No | No | No | https://www.formstack.com/admin/download/file/16083080803 | https://www.formstack.com/admin/download/file/16083080804
2024-03-18 20:23 | AJ | Tabrizi | 21477 | 10 Regis Rd |  | Andover | MA | 1810 | 9787193610 | president |  | Siemens QF250A | Breaker | GFCI breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-11 | 2024-03-11 | 65 Plesant street unit 1, unit 2 and unit 3 |  | Brookline | MA |  | we installed a 2 pole 50 AMP siemens GFCI breaker for a Bosch Induction range. The GFCI breaker will hold if nothing is plug into it. as soon as we plug the range in it will trip the circuit..¦we change the breaker toa normal 50 AMP breaker and the range works fine.¦this is a 3-condo unit and all three have the same issue.¦ | BOSCH | HIS8655U |  | 3 unit condo | Kitchen range in all three units | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16085066841
2024-03-19 07:20 | joseph | silverio | 17118 | 32 franklin street |  | lowell | MA | 1854 | 9788514900 | electrician |  | eaton BR250 GFCI | Breaker | na | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-14 | 2024-03-11 | unit 78k parker street |  | 78 parker street | MA | 1720 | stove comes to temperature and trips repeatedly | general electric | RAS200DM2WW | na | apartment | kitchen stove | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/16086441272
2024-03-19 07:34 | joseph | silverio | 17118 | 32 franklin street |  | lowell | MA | 1854 | 9788514900 | electrician |  | eaton BR250 GFCI | Breaker | na | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-14 | 2024-03-11 | 70m parker street |  | acton | MA | 1720 | breaker tripping when oven comes to temp, heating up | general electric | RAS200DM2WW | na | kitchen stove | kitchen stove | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/16086475570
2024-03-19 07:41 | joseph | silverio | 17118 | 32 franklin street |  | lowell | MA | 1854 | 9788514900 | electrician |  | eaton BR250 GFCI | Breaker | na | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-15 | 2024-03-11 | [5 empty] | stove tripping when oven is heating to temperature, breaker trips repeatedly | general electric | RAS200DM2WW | na | apartment | kitchen stove | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/16086492927
2024-03-19 08:08 | Francis | Baudanza | 7755 | 5 Hilltop Dr |  | Bedford | MA | 1730 | 781-275-6662 | president/owner |  | Siemens QPF | Breaker | gfci | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-15 | 2024-03-14 | 4 Neillian Way |  | Bedford | MA | 1730 | Breaker was tripping after using a stove top burner for a while. After resetting it would hold for a while again. Long enough to finish cooking. Happened several times. | Kenmore | 79094339703 |  | duplex | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16086567230
2024-03-19 10:56 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 315A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JV655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087402009
2024-03-19 10:58 | MICHAEL | ONEIL | 0 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 315B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087417629
2024-03-19 11:01 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 317A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087432989
2024-03-19 11:08 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 317B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087484951
2024-03-19 11:11 | MICHAEL | ONEIL | 0 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 244 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087500722
2024-03-19 11:12 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 246 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087513417
2024-03-19 11:15 | MICHAEL | ONEIL | 0 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 252A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087528987
2024-03-19 11:17 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 252B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087544110
2024-03-19 11:20 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 254A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087562286
2024-03-19 11:22 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 254B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087577425
2024-03-19 11:23 | Chris | Polny | 11660 | 325 Hopping Brook |  | Holliston | MA | 1746 | 7742178986 | VP Electrical Operations |  | Eaton GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-19 | 2024-03-18 | 100 Maple St |  | Sherborn | MA | 1770 | Trips randomly when charging | Grizzly EV charger | GR1-14-24-AB |  | Single family | Car charger in garage | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/16087584917
2024-03-19 11:24 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 256A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087590838
2024-03-19 11:28 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 256B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087613833
2024-03-19 11:31 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 258A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087635578
2024-03-19 11:33 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 15082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-03-27 | 2024-03-26 | 258B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16087650251
2024-03-19 13:19 | Nick | McElroy | 670 | 381 Old Falmouth Rd. | Suite #32 | Marstons Mills | MA | 2648 | 5085664489 | President |  | CHN240GF | Breaker | Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2024-03-18 | 2024-03-18 | 5 Standish Rd |  | Orleans | MA | 2653 | Trips immediately when powered on, no short to ground on wiring. Changed breaker, same issue. | Wolf | CI30460TS | N/A | Kitchen | Kitchen cooktop | No | No | No | No |  | https://www.formstack.com/admin/download/file/16088350439
2024-03-19 14:00 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | Apartment kitchen Oven | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St Unit T1 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16088617913
2024-03-19 14:15 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | (857)636-2649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker. | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16088731705
2024-03-19 14:40 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit T2 |  | Quincy | MA | 2169 | Unit T2 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker. | GE Appliances | JS645SLSS | N/A | Apartment | Unit T2 Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16088897037
2024-03-19 14:46 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit T3 |  | Quincy | MA | 2169 | Unit T3 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit T3 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16088934427
2024-03-19 14:49 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit T4 |  | Quincy | MA | 2169 | Unit T4 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16088957622
2024-03-19 15:58 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit T5 |  | Quincy | MA | 2169 | Unit T5 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit T5 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16089416677
2024-03-19 16:02 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit T6 |  | Quincy | MA | 2169 | Unit T6 - Apartment kitchen's oven starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JTS3000SNSS | None | Apartment | Unit T6 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16089439949
2024-03-19 16:04 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit T7 |  | Quincy | MA | 2169 | Unit T7 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit T7 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16089453751
2024-03-19 16:20 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit T8 |  | Quincy | MA | 2169 | Unit T8 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit T8 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16089556692
2024-03-19 16:23 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit T9 |  | Quincy | MA | 2169 | Unit T9 - JS645SLSS | GE Appliances | JS645SLSS | None | Apartment | Unit T9 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16089579093
2024-03-19 16:27 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit T10 |  | Quincy | MA | 2169 | Unit T10 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | T10 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16089806765
2024-03-19 16:41 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit T11 |  | Quincy | MA | 2169 | Unit T11 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit T11 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16089892391
2024-03-20 12:59 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 101 |  | Quincy | MA | 2169 | Unit 101 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 101 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16094300551
2024-03-20 13:01 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 102 |  | Quincy | MA | 2169 | Unit 102 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 101 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16094315324
2024-03-20 13:04 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 103 |  | Quincy | MA | 2169 | Unit 103 - Apartment kitchen oven's heating element starts and after a short time, it trips the GFCI circuit breaker. | GE Appliances | JS645SLSS | None | Apartment | Unit 103 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16094333416
2024-03-20 13:09 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | Unit 105 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 105 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16094366601
2024-03-20 13:11 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 106 |  | Quincy | MA | 2169 | Unit 106 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 106 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16094377917
2024-03-20 14:26 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | One Adams Place, 859 Willard St. Unit 102 |  | Quincy | MA | 2169 | Unit 102 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 102 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16094869229
2024-03-20 14:28 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | One Adams Place, 859 Willard St. Unit 104 |  | Quincy | MA | 2169 | Unit 104 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 104 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16094885677
2024-03-20 14:34 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 107 |  | Quincy | MA | 2169 | Unit 107 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 107 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16094924828
2024-03-20 14:36 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 108 |  | Quincy | MA | 2169 | Unit 108 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 108 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16094937102
2024-03-20 14:42 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 109 |  | Quincy | MA | 2169 | Unit 109 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker. | GE Appliances | JS645SLSS | None | Apartment | Unit 109 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16094982653
2024-03-20 14:44 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 111 |  | Quincy | MA | 2169 | Unit 111 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 110 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16094994186
2024-03-20 14:46 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 113 |  | Quincy | MA | 2169 | Unit 113 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 113 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095005911
2024-03-20 14:49 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 123 |  | Quincy | MA | 2169 | Unit 123 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 123 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095027748
2024-03-20 14:51 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 125 |  | Quincy | MA | 2169 | Unit 125 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 125 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095041721
2024-03-20 14:55 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 127 |  | Quincy | MA | 2169 | Unit 127 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 127 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095062988
2024-03-20 14:56 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 129 |  | Quincy | MA | 2169 | Unit 129 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 129 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095074118
2024-03-20 15:00 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 131 |  | Quincy | MA | 2169 | Unit 131 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 131 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095098947
2024-03-20 15:02 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 133 |  | Quincy | MA | 2169 | Unit 133 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 133 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095110857
2024-03-20 15:03 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 134 |  | Quincy | MA | 2169 | Unit 134 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 134 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095121633
2024-03-20 15:06 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 135 |  | Quincy | MA | 2169 | Unit 135 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 135 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095141118
2024-03-20 15:08 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 136 |  | Quincy | MA | 2169 | Unit 136 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 136 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095152580
2024-03-20 15:10 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 137 |  | Quincy | MA | 2169 | Unit 137 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 137 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095166054
2024-03-20 15:13 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 138 |  | Quincy | MA | 2169 | Unit 138 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 138 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095188200
2024-03-20 15:15 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 139 |  | Quincy | MA | 2169 | Unit 139 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 139 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095200235
2024-03-20 15:17 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Managers |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 140 |  | Quincy | MA | 2169 | Unit 140 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 140 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095211413
2024-03-20 15:19 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Managers |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 141 |  | Quincy | MA | 2169 | Unit 141 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 141 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095223163
2024-03-20 15:33 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 201 |  | Quincy | MA | 2169 | Unit 201 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 201 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095320928
2024-03-20 15:35 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 202 |  | Quincy | MA | 2169 | Unit 202 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 202 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095332961
2024-03-20 15:36 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 203 |  | Quincy | MA | 2169 | Unit 203 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 203 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095344301
2024-03-20 15:38 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 204 |  | Quincy | MA | 2169 | Unit 204 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 204 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095355108
2024-03-20 15:41 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 205 |  | Quincy | MA | 2169 | Unit 205 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 205 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095376525
2024-03-20 15:43 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 206 |  | Quincy | MA | 2169 | Unit 206 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 206 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095388768
2024-03-20 15:45 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 207 |  | Quincy | MA | 2169 | Unit 207 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 207 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095400048
2024-03-20 15:47 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 212 |  | Quincy | MA | 2169 | Unit 212 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 212 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095412188
2024-03-20 15:50 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 209 |  | Quincy | MA | 2169 | Unit 209 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 209 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095432856
2024-03-20 15:52 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 211 |  | Quincy | MA | 2169 | Unit 211 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 211 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095443745
2024-03-20 15:54 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 213 |  | Quincy | MA | 2169 | Unit 213 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliance | JS645SLSS | None | Apartment | Unit 213 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095459586
2024-03-20 15:56 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 215 |  | Quincy | MA | 2169 | Unit 215 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 215 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16095471108
2024-03-21 16:48 | Christopher | Clapp | 15946 | PO BOX 213 |  | Hanover | MA | 2339 | 6175928508 | Master Electrician |  | Cutler Hammer C-H GFTCB250 | Breaker | Plug in Circuit Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-21 | 2024-03-21 | 102 Downer Ave |  | Hingham | MA | 2043 | Upon connecting the BR250 GFCI breaker to the branch circuit supplying a Viking MVIC636SBBG induction cooktop we found the GFCI breaker would not set. Removed cooktop from GFCI and the breaker would hold and test properly. Checked all connections from branch circuit conductors to cook top conductor and could not find any issue. | Viking | MVIC636SBBG | No other equipment | Residential single family home | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/16101740628
2024-03-22 09:45 | Chris | Polny | 11660 | 325 Hopping Brook |  | Holliston | MA | 1746 | 7742178986 | VP Electrical Operations |  | GFTCB250 | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-21 | 2024-03-21 | 104 Main St |  | Medfield | MA | 2052 | EV Charger trips breaker as soon as you pug it in. If you reset breaker with charger plugged in it will trip as well | Grizzl-e | GCD-6-24 | None | Single Family | EV charger in garage | No | No | No | No |  | https://www.formstack.com/admin/download/file/16104481648
2024-03-22 11:50 | Jarret | Brissette | 21641 | 368 State Road |  | West Tisbury | MA | 2575 | 5086930764 | owner |  | Square D QO250GFI | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-03-22 | 2024-03-22 | [5 empty] | GFI trips when oven is plugged in | Frigidaire | FFEH3051VS |  | (2) Multi family dwellings | (4) different Kitchens¦ | No | No | No | No |  | https://www.formstack.com/admin/download/file/16105194400
2024-03-22 12:45 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C101 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | None | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105519076
2024-03-22 12:46 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C101 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | None | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105526652
2024-03-22 12:54 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C102 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | None | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105569709
2024-03-22 13:01 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | One Adams Place, 859 Willard St |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | None | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105610226
2024-03-22 13:17 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit 103 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | None | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105699430
2024-03-22 13:20 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C104 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | None | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105716583
2024-03-22 13:25 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 105 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105745251
2024-03-22 13:29 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 106 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105768981
2024-03-22 13:32 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 30A 10KA | Breaker | N/A | 30 | 20 Amp To Cook top Replaced as well ADA Unit | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 107 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JTS3000SNSS |  | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105791978
2024-03-22 13:34 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 214 |  | Quincy | MA | 2169 | Unit 214 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 214 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105800129
2024-03-22 13:36 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 217 |  | Quincy | MA | 2169 | Unit 217 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 217 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105811739
2024-03-22 13:37 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 108 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105819885
2024-03-22 13:37 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 216 |  | Quincy | MA | 2169 | Unit 216 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 216 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105821662
2024-03-22 13:39 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 219 |  | Quincy | MA | 2169 | Unit 219 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 219 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105831352
2024-03-22 13:40 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 109 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105835458
2024-03-22 13:47 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C110 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105879410
2024-03-22 13:47 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 222 |  | Quincy | MA | 2169 | Unit 222 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 222 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105879749
2024-03-22 13:49 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 221 |  | Quincy | MA | 2169 | Unit 221 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 221 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105892092
2024-03-22 13:50 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Tower Manufacturing | Residence |  | 2024-03-01 | 2024-03-22 | 140 Whitwell St Unit C 111 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16105899640
2024-03-22 14:08 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 223 |  | Quincy | MA | 2169 | Unit 223 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 223 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106008893
2024-03-22 14:10 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 113 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106016199
2024-03-22 14:13 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St C 115 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106035742
2024-03-22 14:16 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St C 116 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106053057
2024-03-22 14:19 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 117 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106068349
2024-03-22 14:19 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 225 |  | Quincy | MA | 2169 | Unit 225 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 225 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106068489
2024-03-22 14:21 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 227 |  | Quincy | MA | 2169 | Unit 227 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 227 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106079618
2024-03-22 14:21 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 118 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106082613
2024-03-22 14:23 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 229 |  | Quincy | MA | 2169 | Unit 229 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 229 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106091784
2024-03-22 14:24 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 119 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106097323
2024-03-22 14:24 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 231 |  | Quincy | MA | 2169 | Unit 231 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 231 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106099477
2024-03-22 14:26 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 120 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106110576
2024-03-22 14:27 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 30 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 233 |  | Quincy | MA | 2169 | Unit 233 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JTS3000SNSS | None | Apartment | Unit 233 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106114276
2024-03-22 14:28 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 234 |  | Quincy | MA | 2169 | Unit 234 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 234 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106123658
2024-03-22 14:29 | Timothy | Whalley | 17500 | 859859 Willard St |  | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C121 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106126234
2024-03-22 14:30 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 235 |  | Quincy | MA | 2169 | Unit 235 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 235 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106136713
2024-03-22 14:32 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 122 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106144756
2024-03-22 14:32 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 236 |  | Quincy | MA | 2169 | Unit 236 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 236 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106149717
2024-03-22 14:34 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 123 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106157826
2024-03-22 14:34 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 237 |  | Quincy | MA | 2169 | Unit 237 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 237 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106160997
2024-03-22 14:36 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 238 |  | Quincy | MA | 2169 | Unit 238 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 238 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106172030
2024-03-22 14:36 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit 124 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106172809
2024-03-22 14:39 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 125 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106186607
2024-03-22 14:41 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 239 |  | Quincy | MA | 2169 | Unit 239 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 239 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106198612
2024-03-22 14:41 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 126 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106199757
2024-03-22 14:43 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 240 |  | Quincy | MA | 2169 | Unit 240 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 240 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106208342
2024-03-22 15:04 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 241 |  | Quincy | MA | 2169 | Unit 241 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 241 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106333475
2024-03-22 15:13 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 301 |  | Quincy | MA | 2169 | Unit 301 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 301 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106386766
2024-03-22 15:15 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 302 |  | Quincy | MA | 2169 | Unit 302 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 302 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106395775
2024-03-22 15:17 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 303 |  | Quincy | MA | 2169 | Unit 303 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 303 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106408907
2024-03-22 15:18 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 304 |  | Quincy | MA | 2169 | Unit 304 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 304 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106418282
2024-03-22 15:20 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 305 |  | Quincy | MA | 2169 | Unit 305 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 305 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16106428318
2024-03-25 06:37 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 201 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114074634
2024-03-25 06:41 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St C202 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114082905
2024-03-25 06:44 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St C 203 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114088875
2024-03-25 06:49 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 204 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114102444
2024-03-25 06:52 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St C 205 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114107459
2024-03-25 07:42 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 206 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114340249
2024-03-25 07:45 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 30A 10KA | Breaker | 20 amp Breaker for Cooktop as well. | 30 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C207 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114348160
2024-03-25 07:50 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 | N/A | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St C 208 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114362693
2024-03-25 07:52 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St C 209 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114369602
2024-03-25 07:55 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 210 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114377727
2024-03-25 07:57 | Timothy | Whalley | 0 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 211 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114384812
2024-03-25 07:59 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 212 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114391543
2024-03-25 08:02 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 213 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114401904
2024-03-25 08:04 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St C 214 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114409126
2024-03-25 08:06 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 215 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114415853
2024-03-25 08:09 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 30A 10KA | Breaker | 20 amp for cooktop as well ADA unit | 30 | 20 amp for cooktop as well ADA Unit | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 216 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114424256
2024-03-25 08:12 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 217 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114435544
2024-03-25 08:15 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 218 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114444474
2024-03-25 08:18 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 219 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114452808
2024-03-25 08:35 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 220 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114514158
2024-03-25 08:43 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell st Unit C 221 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114547208
2024-03-25 08:45 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 222 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114557572
2024-03-25 08:46 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 306 |  | Quincy | MA | 2169 | Unit 306 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 306 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114560571
2024-03-25 08:48 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 307 |  | Quincy | MA | 2169 | Unit 307 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 307 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114567203
2024-03-25 08:48 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 223 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114567798
2024-03-25 08:49 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 312 |  | Quincy | MA | 2169 | Unit 312 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 312 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114574025
2024-03-25 08:50 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 224 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114576662
2024-03-25 08:51 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 309 |  | Quincy | MA | 2169 | Unit 309 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 309 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114582537
2024-03-25 08:52 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 225 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114587395
2024-03-25 08:54 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 311 |  | Quincy | MA | 2169 | Unit 311 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 311 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114594158
2024-03-25 08:56 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 313 |  | Quincy | MA | 2169 | Unit 313 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 313 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114602083
2024-03-25 08:56 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 226 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114602987
2024-03-25 08:58 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 301 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114613711
2024-03-25 08:59 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 315 |  | Quincy | MA | 2169 | Unit 315 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 315 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114618008
2024-03-25 09:01 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 302 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114623739
2024-03-25 09:05 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 303 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114643953
2024-03-25 09:06 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 314 |  | Quincy | MA | 2169 | Unit 314 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 314 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114648243
2024-03-25 09:08 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 317 |  | Quincy | MA | 2169 | Unit 317 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 317 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114656427
2024-03-25 09:09 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 316 |  | Quincy | MA | 2169 | Unit 316 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 316 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16114663816
2024-03-25 10:10 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 304 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16115011627
2024-03-25 10:13 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 305 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16115025236
2024-03-25 10:15 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 306 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16115040517
2024-03-25 10:18 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 30A 10KA | Breaker | 20 Amp Breaker on Cooktop | 30 | 20 amp breaker on Cooktop | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 307 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JTS3000SNSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16115057280
2024-03-25 10:20 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 308 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16115073276
2024-03-25 10:23 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 309 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16115086243
2024-03-25 10:25 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 310 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16115100875
2024-03-25 10:27 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 311 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16115117529
2024-03-25 14:00 | Aramis | Weimann | 59274 | 1 Rocky Brook Dr |  | Huntington | MA | 1050 | 4135059515 | Electrician |  | THQL2130GFT | Breaker | 2pole 30amp | 30 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16116662466 | 2024-03-25 | 2024-03-25 | 13 Simon Ave |  | Adams | MA | 1220 | Breaker kept tripping. Everything is separated inside dryer and panel | Kenmore | 110.6485 |  | Single Family | Basement | No | No | No | No | https://www.formstack.com/admin/download/file/16116662479 | https://www.formstack.com/admin/download/file/16116662480
2024-03-25 16:06 | Aldo | Nolle | 21090 | 133 Baker Rd |  | Charlton | MA | 1507 | 5087699669 | Owner |  | Square D QO240GFI | Breaker | None | 40 | None | 2 Pole | ABB | Residence |  | 2024-03-22 | 2024-03-22 | 0 Sanctuary Rd. |  | Hopkinton | MA | 1748 | Breaker would constantly trip after 20-60 seconds. Replaced breaker with another of same type and it continued. Replaced breaker with a non GFCI type (Square D QO240) and now works fine.¦¦Also checked to be sure bonding jumper was removed at cord connection to stove. | Bosch 800 Series (Electric Range) | HIS8055U | None | Single Family Dwelling | Kitchen stove only. | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16117576822
2024-03-25 16:06 | Aldo | Nolle | 21090 | 133 Baker Rd |  | Charlton | MA | 1507 | 5087699669 | Owner |  | Square D QO240GFI | Breaker | None | 40 | None | 2 Pole | ABB | Residence |  | 2024-03-22 | 2024-03-22 | 0 Sanctuary Rd. |  | Hopkinton | MA | 1748 | Breaker would constantly trip after 20-60 seconds. Replaced breaker with another of same type and it continued. Replaced breaker with a non GFCI type (Square D QO240) and now works fine.¦¦Also checked to be sure bonding jumper was removed at cord connection to stove. | Bosch 800 Series (Electric Range) | HIS8055U | None | Single Family Dwelling | Kitchen stove only. | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16117578175
2024-03-25 19:20 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C312 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16118706522
2024-03-25 19:24 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 313 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16118724117
2024-03-25 19:28 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 314 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16118737892
2024-03-25 19:38 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 30A 10KA | Breaker | 20 amp breaker on cooktop as well | 30 | 20 amp breaker on cooktop as well | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 315 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JTS3000SNSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16118777793
2024-03-25 19:42 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C316 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16118793813
2024-03-25 19:46 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C317 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16118808155
2024-03-25 19:50 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 318 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16118827205
2024-03-25 19:53 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 319 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16118841617
2024-03-26 10:10 | Craig | Amelisko | 535668 | 37 Dressel Ave |  | Belchertown | MA | 1007 | 413-316-0260 | Project Manager |  | QOB120GFI | Breaker | N/A | 20 |  | 1 Pole | Schneider Electric | Commercial |  | 2024-03-22 | 2024-01-02 | 250 Springfield St |  | Wilbraham | MA | 1095 | Breaker trips at varying intervals after resetting. It is sometimes hours and is sometimes days between breaker trips. This has occurred over a dozen times. The breaker was changed and the new breaker acts as the original one did. | ECON-AIR | 6024 EX-2-PSP-F |  | N/A | N/A | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16121104258
2024-03-26 12:16 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C320 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16121924431
2024-03-26 12:20 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C321 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16121948316
2024-03-26 13:42 | Mark | Roussel | 21100 | 33 Old Forge Lane |  | Sudbury | MA | 1776 | 9784438888 | electrician |  | GE Model # THQL2150GFT2P | Breaker | GFCI circuit breaker | 50 |  | 2 Pole | ABB | Residence |  | 2024-03-24 | 2024-03-24 | 36 Center St |  | Sudbury | MA | 1776 | GFCI breaker pops immediately upon energizing-- If the Range is unplugged the GFCI breaker will hold up until the range is plugged in again | Bosch | HIS8655U | nothing else is connected | single family home / Kitchen | Kitchen | No | No | Yes | No | https://www.formstack.com/admin/download/file/16122907176 | https://www.formstack.com/admin/download/file/16122907177
2024-03-26 16:31 | Christopher | Clapp | 15946 | PO BOX 213 |  | Hanover | MA | 2339 | 617-592-8508 | Master Electrician |  | Eaton C-H GFTCB250 | Breaker | Plug in Circuit Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-20 | 2024-02-07 | 4 Pine Grove Rd. |  | Hingham | MA | 2043 | 50amp GFCI breaker trips breaker and will not allow a reset. Unplugging the Range from the receptacle and GFCI holds and tests properly | Wolfe | DF48650G/S/P | none | Single Family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16124081034
2024-03-26 19:31 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C322 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16124996283
2024-03-26 19:34 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St C 323 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16125009674
2024-03-26 19:38 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C324 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | GE | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16125023779
2024-03-27 08:01 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 325 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16126681819
2024-03-27 08:04 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 326 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16126693145
2024-03-27 08:07 | Timothy | Whalley | 0 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 401 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16126701573
2024-03-27 09:32 | Noah | King | 58682 | 63 Manthorne Rd | Unit 1 | West Roxbury | MA | 2132 | 774-217-4198 | Journeyman Electrician |  | Eaton CH CBGFT2030 2P 30A CB | Breaker | none | 30 |  | 2 Pole | Eaton | Residence |  | 2024-03-13 | 2024-03-13 | 20 Rowes Wharf, Unit 710 |  | Boston | MA | 2110 | Installed GFCI Breaker to feed hard wired induction oven, GFCI trips immediately when switched on. Installation company stated that oven is not compatible with GFCI breaker and breaker must be swapped out. | Wolf | SO3050TM/S/T | No other equipment | Residential Condo | Kitchen Oven is the only thing on the circuit. | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16127038263
2024-03-27 09:40 | Noah | King | 0 | 63 Manthorne Rd | Unit 1 | West Roxbury | MA | 2132 | 774-217-4198 | Journeyman Electrician |  | CH QBGFT2040 2P 40A CB | Breaker | None | 40 |  | 2 Pole | Eaton | Residence |  | 2024-03-13 | 2024-03-13 | 20 Rowes Wharf, Unit 710 |  | Boston | MA | 2110 | Installed GFCI Breaker to feed hard wired induction stove top, GFCI trips immediately when switched on. Installation company stated that stove is not compatible with GFCI breaker and breaker must be swapped out. | Wolf | CI304C/B | No other equipment | residential Condo | Kitchen Cook top is the only thing on this circuit. | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16127080600
2024-03-27 13:40 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 401 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16128609914
2024-03-27 15:06 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C402 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | No | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16129170720
2024-03-27 15:22 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C403 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16129275490
2024-03-27 15:54 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C404 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16129853256
2024-03-27 15:57 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C405 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16129869956
2024-03-27 16:10 | Timothy | Whalley | 0 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C406 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16129947229
2024-03-27 16:27 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C407 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130039530
2024-03-27 16:32 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C408 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130067259
2024-03-27 16:34 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 409 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130080047
2024-03-27 16:37 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 410 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130093890
2024-03-27 16:42 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 411 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130121970
2024-03-27 16:44 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 412 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130133883
2024-03-27 16:47 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 413 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130146151
2024-03-27 16:53 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 414 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130180354
2024-03-27 17:03 | Timothy | Whalley | 0 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 415 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130234763
2024-03-27 17:06 | Timothy | Whalley | 0 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 30A 10KA | Breaker | 20 amp on cooktop as well | 30 | 20 amp on cooktop as well | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 416 |  |  |  |  | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JTS3000SNSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130251118
2024-03-27 17:14 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C417 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130290752
2024-03-27 17:16 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 418 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130302215
2024-03-27 17:18 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 419 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130313549
2024-03-27 17:20 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 420 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130323939
2024-03-27 17:24 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C421 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130345627
2024-03-27 17:27 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 422 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130357627
2024-03-27 17:29 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 423 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16130368701
2024-03-28 08:55 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 424 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132505006
2024-03-28 08:58 | Timothy | Whalley | 0 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | !40 Whitwell St Unit C 425 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | GE | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132514106
2024-03-28 09:00 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 426 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132522342
2024-03-28 09:02 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 501 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132530385
2024-03-28 09:05 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C502 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132539175
2024-03-28 09:07 | Timothy | Whalley | 0 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 503 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132547778
2024-03-28 09:25 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 504 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132621661
2024-03-28 09:27 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 505 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132630878
2024-03-28 09:29 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C506 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132639221
2024-03-28 09:31 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C507 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132647611
2024-03-28 09:41 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 507 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132692017
2024-03-28 09:43 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 508 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132702635
2024-03-28 09:45 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 509 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132711761
2024-03-28 09:47 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C510 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132722028
2024-03-28 09:49 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C511 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132731040
2024-03-28 09:51 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C512 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132741148
2024-03-28 09:53 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C513 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132752954
2024-03-28 09:55 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 514 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132763861
2024-03-28 09:58 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C515 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132780354
2024-03-28 10:01 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 516 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132792054
2024-03-28 10:03 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 whitwell St Unit C517 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132804323
2024-03-28 10:08 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C518 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132834386
2024-03-28 10:10 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C519 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132846484
2024-03-28 10:13 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C 520 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132858462
2024-03-28 10:15 | Timothy | Whalley | 17500 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 140 Whitwell St Unit C521 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132869569
2024-03-28 10:24 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-03-22 | 2024-03-01 | 130 Whitwell St Unit C 102 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132914689
2024-03-28 10:27 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit 101 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132932049
2024-03-28 10:29 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 103 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132945416
2024-03-28 10:34 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 106 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16132972205
2024-03-28 10:42 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A105 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133011998
2024-03-28 10:44 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 140 Whitwell St Unit A107 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133026854
2024-03-28 10:48 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A110 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133046445
2024-03-28 10:50 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A111 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133061212
2024-03-28 10:53 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A112 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133075106
2024-03-28 10:55 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A113 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133088903
2024-03-28 10:58 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A114 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133102578
2024-03-28 11:00 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A115 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133114910
2024-03-28 11:02 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 202 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133127695
2024-03-28 11:04 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A201 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133142026
2024-03-28 11:07 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A204 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133156426
2024-03-28 11:09 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A203 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133174143
2024-03-28 11:20 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 206 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133246174
2024-03-28 11:33 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A207 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133328385
2024-03-28 12:06 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A209 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133541665
2024-03-28 12:11 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A210 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133571893
2024-03-28 12:13 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A211 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133587380
2024-03-28 12:17 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A212 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS | none | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133617459
2024-03-28 12:20 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A213 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133633124
2024-03-28 12:22 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 214 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133647608
2024-03-28 12:25 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A215 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133661699
2024-03-28 12:27 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A302 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133676487
2024-03-28 12:29 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A301 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133692251
2024-03-28 12:32 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 304 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133707860
2024-03-28 12:34 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A303 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133723436
2024-03-28 12:36 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A306 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133737837
2024-03-28 12:38 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 305 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133752869
2024-03-28 12:41 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A307 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | Ge | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133766763
2024-03-28 12:43 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A309 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133781174
2024-03-28 12:45 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A310 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133795494
2024-03-28 12:47 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 311 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133809164
2024-03-28 12:50 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A312 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133823824
2024-03-28 12:53 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A312 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133846108
2024-03-28 12:56 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 313 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133865062
2024-03-28 12:59 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 314 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133883651
2024-03-28 13:01 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A315 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS |  | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16133897002
2024-03-28 15:11 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 402 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16134704009
2024-03-28 15:14 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A401 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16134722868
2024-03-28 15:17 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A404 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16134742956
2024-03-28 15:20 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A403 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16134760585
2024-03-28 15:22 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell st Unit A406 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16134777039
2024-03-28 15:25 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A407 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135017213
2024-03-28 15:27 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 409 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135100234
2024-03-28 15:30 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A410 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135116850
2024-03-28 15:32 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A411 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135131945
2024-03-28 15:36 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A412 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135153930
2024-03-28 15:38 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 413 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135168869
2024-03-28 15:40 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 414 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135181828
2024-03-28 15:43 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 415 |  | Quincy | MA | 2169 | ¦Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135197602
2024-03-28 15:46 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 502 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135220219
2024-03-28 15:49 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A501 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135236079
2024-03-28 15:51 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A 504 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135251954
2024-03-28 15:54 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A503 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135266935
2024-03-28 15:57 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A506 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135288160
2024-03-28 16:00 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A507 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135304017
2024-03-28 16:02 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A509 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135319671
2024-03-28 16:04 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A510 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135334538
2024-03-28 16:07 | Timothy | Whalley | 53195 | One Adams Place | 859 Willard St | Quincy | MA | 2169 | 7742184288 | Construction Manager |  | GFCI Circuit Breaker - QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2023-08-01 | 2023-05-01 | 130 Whitwell St Unit A511 |  | Quincy | MA | 2169 | Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE | JS645SLSS | None | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16135350500
2024-03-28 19:37 | Corey | Hood | 8228 | 55 Anne Road |  | Norwood | MA | 2062 | 7819157358 | Owner/Manager |  | GFTCB250 | Breaker | Stab on Eaton Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-03-22 | 2024-03-26 | 39 Mason Road |  | Newton | MA | 2459 | Double Wall oven tripped the breaker multiple times after starting to heat. Changed Breaker, still tripped, checked all connections and made sure both appliance and circuit was properly grounded | Thermador | PODMC301W/04 | Thermador MC30WP/01 (Microwave wires into oven and oven connects to feeder) | Single Family | Single Family Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16136322779
2024-03-29 09:11 | Brian | Ferreira | 53423 | 29 james st. |  | Taunton | MA | 2780 | 5087381950 | Electrician |  | Square d | Breaker | Qo | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-03-28 | 2024-03-11 | 41 west brookfield road. |  | North brookfield | MA | 1535 | As soon as the stove was brought up to temperature the oven kept tripping. | General Electric | 229c6112p001 | Just the range | Home | Inside of the kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16137791081
2024-03-30 17:27 | Nick | Bouvier | 55405 | 250 Harvey Mountain Road, Tolland, MA |  | Granville | MA | 1085 | 4133190444 | Electrician |  | AD-910 | Breaker | Square D | 50 |  | 2 Pole | ABB | Residence |  | 2024-03-30 | 2024-03-25 | [5 empty] | Oven tripping before it comes to preheated temperature | Samsung | 0GG67DCN302158E |  | House | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16142602222 | https://www.formstack.com/admin/download/file/16142602223
2024-04-01 14:08 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 319 |  | Quincy | MA | 2169 | Unit 319 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 319 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16148846869
2024-04-01 14:09 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 322 |  | Quincy | MA | 2169 | Unit 322 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 322 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16148858629
2024-04-01 14:11 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 321 |  | Quincy | MA | 2169 | Unit 321 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 321 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16148872756
2024-04-01 14:13 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 323 |  | Quincy | MA | 2169 | Unit 323 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 323 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16148886632
2024-04-01 14:15 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 325 |  | Quincy | MA | 2169 | Unit 325 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 325 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16148900860
2024-04-01 14:17 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 327 |  | Quincy | MA | 2169 | Unit 327 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 327 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16148914130
2024-04-01 14:21 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 329 |  | Quincy | MA | 2169 | Unit 329 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | 329 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16148937266
2024-04-01 14:23 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 331 |  | Quincy | MA | 2169 | Unit 331 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 331 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16148951131
2024-04-01 14:25 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 333 |  | Quincy | MA | 2169 | Unit 333 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 333 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16148964712
2024-04-01 14:27 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 334 |  | Quincy | MA | 2169 | Unit 334 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 334 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16148977490
2024-04-01 14:30 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 335 |  | Quincy | MA | 2169 | Unit 335 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 335 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149003606
2024-04-01 14:34 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 30 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 336 |  | Quincy | MA | 2169 | Unit 336 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JTS3000SNSS | None | Apartment | Unit 336 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149030269
2024-04-01 14:36 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 337 |  | Quincy | MA | 2169 | Unit 337 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS |  | Apartment | Unit 337 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149045089
2024-04-01 14:38 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 338 |  | Quincy | MA | 2169 | Unit 338 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 338 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149055456
2024-04-01 14:39 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 339 |  | Quincy | MA | 2169 | Unit 339 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 339 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149065667
2024-04-01 14:41 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 340 |  | Quincy | MA | 2169 | Unit 340 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 340 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149075607
2024-04-01 14:43 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 341 |  | Quincy | MA | 2169 | Unit 341 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 341 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149093412
2024-04-01 14:51 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 401 |  | Quincy | MA | 2169 | Unit 401 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 401 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149146443
2024-04-01 14:55 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 402 |  | Quincy | MA | 2169 | Unit 402 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 402 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149175185
2024-04-01 15:01 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 403 |  | Quincy | MA | 2169 | Unit 403 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 403 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149214927
2024-04-01 15:03 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 404 |  | Quincy | MA | 2169 | Unit 404 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 404 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149227662
2024-04-01 15:05 | Brooke | Heisler-Leary | 58767 | 29 North County Rd |  | Florida | MA | 1247 | 4132658094 | Electrician |  | 488006004 | Breaker | Square D Homeline | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16149239560 | 2024-03-01 | 2024-03-01 | [5 empty] | Tripped during oven preheat | GE | JBP72T0K2WW |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16149239572
2024-04-01 15:05 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 405 |  | Quincy | MA | 2169 | Unit 405 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 405 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149240467
2024-04-01 15:05 | Brooke | Heisler-Leary | 58767 | 29 North County Rd |  | Florida | MA | 1247 | 4132658094 | Electrician |  | 488006004 | Breaker | Square D Homeline | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16149245340 | 2024-03-01 | 2024-03-01 | [5 empty] | Tripped during oven preheat | GE | JBP72T0K2WW |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16149245352
2024-04-01 15:07 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 406 |  | Quincy | MA | 2169 | Unit 406 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 406 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149253955
2024-04-01 15:08 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 407 |  | Quincy | MA | 2169 | Unit 407 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 407 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149266328
2024-04-01 15:12 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 412 |  | Quincy | MA | 2169 | Unit 412 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 412 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149289105
2024-04-01 15:14 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 409 |  | Quincy | MA | 2169 | Unit 409 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 409 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149304164
2024-04-01 15:17 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 409 |  | Quincy | MA | 2169 | Unit 409 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 409 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149321205
2024-04-01 15:18 | Brooke | Heisler-Leary | 58767 | 9 Cullen hill rd |  | Huntington | MA | 1050 | 4132658094 | Electrician |  | 4884006004 | Breaker | Square D | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-01 | 2024-04-01 | [5 empty] | Breaker tripped during preheat cycle | Whirlpool | WFE975H0HZ1 |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16149331438
2024-04-01 15:20 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 411 |  | Quincy | MA | 2169 | Unit 411 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 411 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149340747
2024-04-01 15:24 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 413 |  | Quincy | MA | 2169 | Unit 413 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 413 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149372096
2024-04-01 15:26 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 415 |  | Quincy | MA | 2169 | Unit 415 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 415 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149382791
2024-04-01 15:28 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 414 |  | Quincy | MA | 2169 | Unit 414 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 414 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149393702
2024-04-01 15:29 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 417 |  | Quincy | MA | 2169 | Unit 417 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 417 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149403758
2024-04-01 15:31 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 416 |  | Quincy | MA | 2169 | Unit 416 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 416 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149415645
2024-04-01 15:48 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 419 |  | Quincy | MA | 2169 | Unit 419 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 419 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149534304
2024-04-01 15:50 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 422 |  | Quincy | MA | 2169 | Unit 422 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 422 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149545165
2024-04-01 15:52 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 421 |  | Quincy | MA | 2169 | Unit 421 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 421 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149555858
2024-04-01 15:53 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 423 |  | Quincy | MA | 2169 | Unit 423 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 423 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149566757
2024-04-01 16:01 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 425 |  | Quincy | MA | 2169 | Unit 425 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 425 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149620216
2024-04-01 16:06 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 427 |  | Quincy | MA | 2169 | Unit 427 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 427 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149655772
2024-04-01 16:10 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 429 |  | Quincy | MA | 2169 | Unit 429 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 429 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149675945
2024-04-01 16:17 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 431 |  | Quincy | MA | 2169 | Unit 431 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 431 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149720933
2024-04-01 16:21 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 30 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 433 |  | Quincy | MA | 2169 | Unit 433 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 433 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149749350
2024-04-01 16:23 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 434 |  | Quincy | MA | 2169 | Unit 434 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 434 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149761367
2024-04-01 16:25 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | None | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 435 |  | Quincy | MA | 2169 | Unit 435 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 435 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149777292
2024-04-01 16:27 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 436 |  | Quincy | MA | 2169 | Unit 436 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 436 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149787308
2024-04-01 16:30 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 437 |  | Quincy | MA | 2169 | Unit 437 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 437 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149807083
2024-04-01 16:32 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 438 |  | Quincy | MA | 2169 | Unit 438 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 438 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149817904
2024-04-01 16:37 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 439 |  | Quincy | MA | 2169 | Unit 439 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 439 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149853853
2024-04-01 16:41 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 440 |  | Quincy | MA | 2169 | Unit 440 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 440 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149878002
2024-04-01 16:43 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 441 |  | Quincy | MA | 2169 | Unit 441 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 441 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149894044
2024-04-01 16:46 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 523 |  | Quincy | MA | 2169 | Unit 523 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 523 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149912969
2024-04-01 16:50 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 525 |  | Quincy | MA | 2169 | Unit 525 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 525 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149934860
2024-04-01 16:52 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 527 |  | Quincy | MA | 2169 | Unit 527 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 527 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149951685
2024-04-01 16:54 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 30 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 529 |  | Quincy | MA | 2169 | Unit 529 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 529 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149962082
2024-04-01 16:56 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 531 |  | Quincy | MA | 2169 | Unit 531 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 531 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149973043
2024-04-01 16:58 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 533 |  | Quincy | MA | 2169 | Unit 533 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 533 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149987411
2024-04-01 17:00 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 534 |  | Quincy | MA | 2169 | Unit 534 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 534 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16149996672
2024-04-01 17:02 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 535 |  | Quincy | MA | 2169 | Unit 535 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 535 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16150008582
2024-04-01 17:22 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 536 |  | Quincy | MA | 2169 | Unit 536 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker. | GE Appliances | JS645SLSS | None | Apartment | Unit 536 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16150131507
2024-04-01 17:25 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 537 |  | Quincy | MA | 2169 | Unit 537 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 537 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16150145180
2024-04-01 17:27 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 538 |  | Quincy | MA | 2169 | Unit 538 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 538 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16150156090
2024-04-01 17:28 | Joseph | Giannino | 17500 | One Adams Place, 859 Willard St. |  | Quincy | MA | 2169 | 8576362649 | Construction Manager |  | QPF GFCI 5mA 2P 240V 40A 10KA | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-02-01 | 2024-02-01 | 120 Whitwell St. Unit 539 |  | Quincy | MA | 2169 | Unit 539 - Apartment kitchen oven's heating element starts and¦after a short time, it trips the GFCI circuit breaker.¦ | GE Appliances | JS645SLSS | None | Apartment | Unit 539 - Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16150164061
2024-04-01 18:53 | Brooke | Heisler-Leary | 58767 | 9 Cullen hill rd |  | Huntington | MA | 1050 | 4132658094 | Electrician |  | 4884006004 | Breaker | Square D | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-01 | 2024-04-01 | [5 empty] | Breaker tripped during preheat cycle | Whirlpool | WFE975H0HZ1 |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16150587226
2024-04-02 09:11 | Ray | Ostroski | 16764 | 100 Trade Center | Suite G 700 | Woburn | MA | 1801 | 7818380703 | owner |  | Chn240gf | Breaker | Cutler Hammer | 40 |  | 2 Pole | Eaton | Residence |  | 2024-03-28 | 2024-03-28 | 8 Wren Way |  | Methuen | MA | 1844 | Kitchen oven trips breaker when under load | KitchenAid | KOSE500ESS |  | Single Family | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16152810468
2024-04-02 09:16 | Ray | Ostroski | 16764 | 100 Trade Center | Suite G 700 | Woburn | MA | 1801 | 7818380703 | owner |  | CHN240gf | Breaker | Cutler Hammer | 40 |  | 2 Pole | Eaton | Residence |  | 2024-03-28 | 2024-03-28 | 10 Wren Way |  | Methuen | MA | 1844 | Oven Trips Breaker under load | KitchenAid | KOSE500ESS |  | Single Family | kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16152830950
2024-04-02 09:20 | Ray | Ostroski | 16764 | 100 Trade Center | Suite G700 | Woburn | MA | 1801 | 7818380703 | Owner |  | CHN240GF | Breaker | Cutler Hammer | 40 |  | 2 Pole | Eaton | Residence |  | 2024-03-28 | 2024-03-28 | 12 Wren Way |  | Methuen | MA | 1844 | Oven Trips Breaker Under Load | KitchenAid | KOSE500ESS |  | Single Family | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16152851858
2024-04-02 11:07 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | VP-Owner |  | Eaton | Breaker | n/a | 40 |  | 2 Pole | Eaton | Residence |  | 2024-03-22 | 2024-03-15 | 18 POINT ROAD |  | MONTEREY | MA | 1245 | Breaker does not hold, kept tripping. | GE | PHS930YPFS |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16153520040
2024-04-02 11:15 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | VP-Owner |  | Square D Homeline | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-03-22 | 2024-03-15 | 55 STRATFORD ROAD |  | NEW MARLBORO | MA | 1230 | Breaker does not hold, kept tripping. | Fisher Paykel | WOSV2-30 |  | Single Family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16153585959
2024-04-03 12:12 | Michael | Colonna Jr | 16036 | 441 COOPER RD |  | NORTHBRIDGE | MA | 1534 | 5089222693 | electrician |  | Q115DF | Breaker | Dual function circuit breaker | 15 |  | 1 Pole | Siemens | Residence |  | 2024-04-02 | 2024-04-02 | 224 Central Turnpike |  | Sutton | MA | 1590 | fridg kept tripping dual function breaker, replaced with arc fault only breaker and tripping stopped, appliance manual stated avoid plugging into GFCI protected outlet, receptacle, wiring, cord all in good condition, they even swapped out the fridg with a new identical model still tripped, the appliance will not work on a GFCI circuit | Frigidaire | GRMS2773AF01 | 0 | New single family home | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16159937850
2024-04-03 12:59 | Nick | McElroy | 670 | 381 Old Falmouth Rd. | Suite #32 | Marstons Mills | MA | 2648 | 5085664489 | president |  | HOM230GFIC | Breaker | Breaker | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-03 | 2024-01-30 | 42 Stone Bridge Lane |  | Barnstable | MA | 2648 | Trip when oven is on, incompatible with GFCI, tried swapping breaker with same result. | Bosch | HDIP056U/04 | N/A | Kitchen | Kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/16160282780
2024-04-04 14:17 | John | Vespa | 17144 | 250 Milton St |  | Dedham | MA | 2026 | 617 325 1151 | Owner |  | QF250A | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2024-04-01 | 2024-04-01 | 29 Aberdeen St |  | Newton | MA | 2461 | Stove cooktop tripping, Installation manual recommends to not install GFCI breaker | Bosch | HIS8055U |  | 1 family | kitchen stove cooktop tripping | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/16166561632
2024-04-05 08:36 | Kennith | Sparrow | 20580 | 151 Mystic Ave #2 |  | Medford | MA | 2148 | 7816487771 | Owner |  | GE Load Center | Breaker | NA | 50 |  | 2 Pole | Industrial | Residence |  | 2024-04-04 | 2024-01-17 | 10 Corporal McTernan St #404 |  | Cambridge | MA |  | Installed 1/17/24 on 3/27/24 call from homeowner Breaker tripping when using oven went by check all connections and burnt off using a regular 2 pole 50 breaker reinstalled GFCI breaker and did not trip. 4/4/24 got a call from homeowner tripping again. Removed 2 pole 50 GFCI breaker install regular 2 pole 50 breaker. | GE Appliances | PHS930YPBFS |  | Kitchen oven circuit | Oven outlet | No | No | No | No |  | https://www.formstack.com/admin/download/file/16170577572
2024-04-05 10:04 | Jonathan | Fielding | 31091 | 85 Dunstable Rd |  | North Chelmsford | MA | 1863 | 9788665498 | Electrician |  | Eaton GFTCB230 | Breaker | Breaker | 30 |  | 2 Pole | Eaton | Residence |  | 2024-03-25 | 2024-03-22 | 22 Butternut |  | Dracut | MA | 1826 | Dryer trips GFI breaker upon plugging into receptacle | Electrolux | ELFE7637BW0 | None | Single Family | Dryer | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/16170974638
2024-04-05 12:33 | Chris | Polny | 11660 | 325 Hopping Brook |  | Holliston | MA | 1746 | 7742178986 | VP Electrical Operations |  | Siemens AFGA2 | Breaker | n/a | 20 |  | 1 Pole | Siemens | Residence |  | 2024-03-29 | 2024-03-29 | 116 Hanlon Rd |  | Holliston | MA | 1746 | Manual for fridge says no gfci. Fridge tripped gfci | Freigedaire | GRMC2273CF02 |  | Singl familye | Only fridge in kitchen is affected | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/16171870262
2024-04-05 14:49 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | master electrician |  | GFTCB250 | Breaker | BREAKER |  | 50 | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 260A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16172671214
2024-04-05 14:53 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 260B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB65535355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16172700145
2024-04-05 14:56 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 262A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16172717910
2024-04-05 15:07 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 262B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16172782693
2024-04-05 15:10 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 272A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16172798250
2024-04-05 15:13 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 272B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16172822628
2024-04-05 15:16 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 274A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB65SK355 |  | AFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16172837923
2024-04-05 15:33 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTR ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 274B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16172938796
2024-04-05 15:37 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 266A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16172963820
2024-04-05 15:42 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 266B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16172996129
2024-04-05 15:46 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 264A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16173015428
2024-04-05 15:48 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 264B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16173029442
2024-04-05 16:01 | Brian | Ferreira | 53423 | 29 james st. |  | Taunton | MA | 2780 | 4133349561 | Electrician |  | Square d | Breaker | Homeline | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-04 | 2024-03-12 | 5 stoddard st. |  | Upton | MA | 1568 | As soon as oven got up to temperature the breaker would trip. | Samsung | Dg68-00101b | None | House | Just the kitchen range circuit | No | No | No | No |  | https://www.formstack.com/admin/download/file/16173102247
2024-04-05 16:33 | Brian | Ferreira | 53423 | 29 james st. |  | Taunton | MA | 2780 | 4133349561 | Electrician |  | Square d | Breaker | Homeline | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-04 | 2024-03-12 | 5 stoddard st. |  | Upton | MA | 1568 | As soon as oven got up to temperature the breaker would trip. | Samsung | Dg68-00101b | None | House | Just the kitchen range circuit | No | No | No | No |  | https://www.formstack.com/admin/download/file/16173284819
2024-04-09 08:13 | Thomas | Juzba | 56789 | 14 Kelleher Drive |  | Deerfield | MA | 1373 | 4138871798 | Electrician |  | QO230GFIC | Breaker | 4prong plug and cord | 30 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16185722680 | 2024-04-06 | 2024-04-05 | [5 empty] | Breaker continues to trip whenever homeowner tries to operate their dryer | Whirlpool | LE4440XWW0 | None | Single family home | Laundry room | No | No | No | No | https://www.formstack.com/admin/download/file/16185722693 | https://www.formstack.com/admin/download/file/16185722694
2024-04-09 08:58 | Thomas | Juzba | 56789 | 14 Kelleher Drive |  | Deerfield | MA | 1373 | 4138871798 | Electrician |  | QO240GFICP | Breaker | 4prong plug and cord | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16185889927 | 2024-04-06 | 2024-04-05 | [5 empty] | Breaker continued to trip as customer was trying to use their oven | Whirlpool | RF386PXE2 | None | Single family home | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16185889940 | https://www.formstack.com/admin/download/file/16185889941
2024-04-10 08:18 | Brooke | Heisler-Leary | 58767 | 9 Cullen hill rd |  | Huntington | MA | 1050 | 4132658094 | Electrician |  | 4884006004 | Breaker | Square D | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-01 | 2024-04-01 | [5 empty] | Breaker tripped during preheat cycle | Whirlpool | WFE975H0HZ1 |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16191335878
2024-04-10 08:18 | Brooke | Heisler-Leary | 58767 | 9 Cullen hill rd |  | Huntington | MA | 1050 | 4132658094 | Electrician |  | 4884006004 | Breaker | Square D | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-01 | 2024-04-01 | [5 empty] | Breaker tripped during preheat cycle | Whirlpool | WFE975H0HZ1 |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16191336248
2024-04-10 08:18 | Brooke | Heisler-Leary | 58767 | 9 Cullen hill rd |  | Huntington | MA | 1050 | 4132658094 | Electrician |  | 4884006004 | Breaker | Square D | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-01 | 2024-04-01 | [5 empty] | Breaker tripped during preheat cycle | Whirlpool | WFE975H0HZ1 |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16191336516
2024-04-10 08:24 | Brooke | Heisler-Leary | 58767 | 16 Dalton St |  | Wilbraham | MA | 1095 | 4132658094 | Electrician |  | QO240GFICP | Breaker | Square D | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-10 | 2024-03-01 | [5 empty] | Breaker trips with oven preheating | GE | JB735DP2WW |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16191356547
2024-04-10 08:24 | Brooke | Heisler-Leary | 58767 | 16 Dalton St |  | Wilbraham | MA | 1095 | 4132658094 | Electrician |  | QO240GFICP | Breaker | Square D | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-10 | 2024-03-01 | [5 empty] | Breaker trips with oven preheating | GE | JB735DP2WW |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16191357118
2024-04-10 09:51 | Tony | Marroquin | 14426 | 48 Chamberlain |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB250 | Breaker | Gfci | 50 |  | 2 Pole | Eaton | Residence |  | 2023-09-28 | 2023-07-28 | 59 Chamberlain st |  | Hopkinton | MA | 1748 | Tesla level 2 charger nuisance tripping at dedicated circuit. | Tesla | Level 2 |  | Single home | Garage | Yes | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/16191740804
2024-04-11 18:05 | Richard | Leger | 17034 | 140 Crescent Rc |  | Needham | MA | 2494 | 617-529-0166 | Owner |  | Eaton GFTCB250 | Breaker | None | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/16200640577 | 2024-02-21 | 2024-02-20 | 11 Olde Field Rd |  | Newton | MA | 2459 | Cooktop would randomly trip when heating. We replaced the breaker to rule out that as the cause. We traced the wire for faults and found none. The manufacturer rep/tech acknowledged that they have an issue. They tried troubleshooting the cooktop on site. They replaced various components and nothing solved the issue. | GE | PHP9036ST1SS | None | Kitchen | This is a cooktop installed in the kitchen of the property. | No | Yes | Yes | No | https://www.formstack.com/admin/download/file/16200640591 | https://www.formstack.com/admin/download/file/16200640592
2024-04-15 12:14 | Thomas | Juzba | 56789 | 26 Sunset Drive |  | Montague | MA | 1376 | 4138871798 | Electrician |  | Thql2140gft | Breaker | UPC 783164-48537 | 40 |  | 2 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/16213899708 | 2024-04-15 | 2024-04-15 | [5 empty] | Customer could not use over without breaker tripping | General electric | J bp35s m3ss | None | Single family home | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16213899728 | https://www.formstack.com/admin/download/file/16213899729
2024-04-16 10:04 | JOSEPH | REGO | 14348 | 30 OLD MEADOW ROAD |  | BREWSTER | MA | 2631 | 508-896-0011 | OWNER |  | QO250GFCI | Breaker | BREAKER | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-01 | 2024-04-16 | [5 empty] | New range intermittently has tripped multiple gfci breakers. | KITCHENAID | KSDG950ESS6 | NONE | KITCHEN | KITCHEN RANGE | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16219133919
2024-04-17 10:26 | Mark | Flores | 52255 | 97 Groveland Ave |  | South Weymouth | MA | 2190 | 7816643215 | Electrician |  | QF250A | Breaker | other | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16225217341 | 2023-12-25 | 2023-12-24 | 12 Hitching Post Lane |  | Hingham | MA | 2043 | The Range Continuously Trips Breaker. Have had appliance people out, have checked all connections in wiring, and appliance itself. Breaker will not hold when appliance is connected | WOLF | IR36550/S/T | None | Single Family Dwelling | Only Kitchen Range Appliance circuit tripping | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16225217364 | https://www.formstack.com/admin/download/file/16225217366
2024-04-17 10:39 | Mark | Flores | 52255 | 97 Groveland Ave |  | South Weymouth | ME | 2190 | 7816643215 | Electrician |  | QF250A | Breaker | Other | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16225311479 | 2023-12-25 | 2023-12-22 | 12 Hitching Post Lane |  | Hingham | MA | 2043 | Range would not Work , immediately trips breaker when plugged in. only holds on conventional Breaker. Wiring was checked at all points of the circuit , no continuity. Appliance manufacturer was contacted with no results. appliance man checked appliance. appliance wired according to listing and installation instructions. ¦ | WOLF | IR36550/S/T | None | Single Family Dwelling | Kitchen Appliance Range Circuit Only, within kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16225311493 | https://www.formstack.com/admin/download/file/16225311494
2024-04-18 07:34 | Jonathan | Moreira | 22519 | 6 Concord Rd. |  | Stoneham | MA | 2180 | 7815891970 | Owner |  | Qfga2n | Breaker | Na | 20 |  | 1 Pole | Siemens | Residence |  | 2024-01-10 | 2024-04-11 | 6 Concord Rd. |  | Stoneham | MA | 2180 | Nuisance tripping of GFCI circuit breaker every time built in microwave was used. Plugged microwave into different ground fault protected circuit and found the microwave would trip this circuit as well, after which I plugged it into an arc fault only protected circuit and found microwave to work as intended. Microwave is on a dedicated 20 amp circuit plugged into a single receptacle located within the space for the built in microwave. Installed an arc fault only circuit breaker on said circuit | Thermador | MD24WS/03 |  | 2 family | Unit 2 kitchen microwave | No | No | Yes | No | https://www.formstack.com/admin/download/file/16230480327 | https://www.formstack.com/admin/download/file/16230480328
2024-04-18 12:31 | Michael | Bell | 17374 | P. O. Box 1038 |  | Plymouth | MA | 02362-1038 | 5082948148 | Licensed electrician |  | BR 250 GFCI | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-15 | 2024-04-10 | 263 Sandwich stree |  | Plymouth | MA | 2360 | New electric stove trips breaker. Multiple GFCI breaker tried | Beko | PRIR34452SS | None | Single family dwellin | Kitchen stove | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/16232089019
2024-04-18 15:53 | Joseph | Fortin | 20860 | 14 Winthrop St |  | Rehoboth | MA | 2769 | 7745658142 | Vice President |  | LB240-G | Breaker | Breaker | 40 |  | 2 Pole | Leviton | Residence |  | 2024-01-09 | 2024-03-20 | 62 Station Drive - Pinehills 2 |  | Plymouth | MA | 2360 | Every time the oven starts to heat up the breaker trips. | Whirlpool | WEE515S0LS | none | 13 out of 176 residential apartments | The kitchen range. | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16233446669
2024-04-21 09:53 | Michael | Bell | 17374 | P. O. Box 1038 |  | Plymouth | MA | 02362-1038 | 5082948148 | Licensed electrician |  | BR 250 GFCI | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-15 | 2024-04-10 | 263 Sandwich stree |  | Plymouth | MA | 2360 | New electric stove trips breaker. Multiple GFCI breaker tried | Beko | PRIR34452SS | None | Single family dwellin | Kitchen stove | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/16242982519
2024-04-22 12:28 | Ryan | LaBrache | 22042 | 1 Summer Street |  | Watertown | MA | 2472 | 16175384851 | Onwer |  | BRN250GF | Breaker | stab in | 50 |  | 1 Pole | Eaton | Residence |  | 2024-04-17 | 2024-03-13 | 120 Codman Rd |  | Brookline | MA | 2445 | Wall oven won't hold on GFI CB | GE appliances | php9036dt1bb |  | Single Family | Kichen wall oven | No | No | No | No |  | https://www.formstack.com/admin/download/file/16247286419
2024-04-22 13:25 | Tony | Marroquin | 14426 | 48 Chamberlain St |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB240 | Breaker | none | 40 |  | 2 Pole | Eaton | Residence |  | 2024-03-25 | 2024-02-05 | 53 Chamberlain St |  | Hopkinton | MA | 1748 | Breaker trips when oven is in use. | KitchenAid | KOSE500ESS |  | Single Family Home | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/16247672567
2024-04-22 14:53 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | master electrician |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 260A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16248281362
2024-04-22 14:55 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 260B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16248298209
2024-04-22 14:58 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 262A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16248318158
2024-04-22 15:00 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 262B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16248334053
2024-04-22 15:03 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 272A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLAINCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16248354244
2024-04-22 15:05 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 272B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16248370373
2024-04-22 15:08 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 274A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16248388841
2024-04-22 15:15 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 274B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16248443221
2024-04-22 15:18 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 266A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16248462789
2024-04-22 15:20 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 266B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16248479991
2024-04-22 15:23 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 264A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16248496271
2024-04-22 15:26 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 264B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16248517142
2024-04-23 11:30 | Tony | Marroquin | 14426 | 48 Chamberlain St |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB230 | Breaker | None | 30 |  | 2 Pole | Eaton | Residence |  | 2024-04-23 | 2024-02-05 | 53 Chamberlain St |  | Hopkinton | MA | 1748 | Breaker trips when dryer is in use. | LG | DLEX6700B |  | Single Family Home | Laundry Room | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/16252794444
2024-04-24 10:46 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | master electrician |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 270 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258138109
2024-04-24 10:48 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 33 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258153729
2024-04-24 10:50 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 35 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHENN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258165319
2024-04-24 10:53 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 37 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258180378
2024-04-24 10:55 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 39 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258196802
2024-04-24 11:00 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 2 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258225641
2024-04-24 11:02 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 4 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258242568
2024-04-24 11:04 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELCTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 4 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258253771
2024-04-24 11:06 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 6 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258265571
2024-04-24 11:11 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 8 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLAICNE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258293501
2024-04-24 11:18 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 26A HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258342056
2024-04-24 11:20 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 26BRANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258355224
2024-04-24 11:23 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 28A HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDBALE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258375171
2024-04-24 11:25 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 28B HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258386665
2024-04-24 11:27 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 30A HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258400165
2024-04-24 11:29 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 30B HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258412063
2024-04-24 11:31 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 32A HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258426862
2024-04-24 11:33 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 32B HIGHCREST RD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16258438558
2024-04-24 14:23 | Seamus | O'Doherty | 16761 | 453 Clapboardtree Street |  | Westwood | MA | 2090 | 6177199603 | Owner (Kerry Electric ) |  | Siemens Cat No QF250A | Breaker | Circuit Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2024-04-18 | 2024-04-18 | 67 Crowningshield Rd |  | Brookline | MA | 2446 | New installation¦GfCI circuit breaker for stove turned on and stayed on with no stove plugged in to outlet¦Jumper between neutral and ground was removed¦as soon as new stove is plugged in the Gfci circuit breaker trips¦GFCI circuit breaker was replaced and that also trips ¦ | Cornufe 90 ""Albertine ""Induction C9-I | C9MF-1. Serial # 12293. 214011 | none | single Residence | Kitchen Stove only | No | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/16259524003 | https://www.formstack.com/admin/download/file/16259524004
2024-04-24 15:45 | Ron | Berube | 12171 | PO BOX 488 |  | DRACUT | MA | 1826 | 9782650105 | OWNER |  | SEIMENS | Breaker | BREAKER | 50 |  | 2 Pole | Siemens | Residence |  | 2024-04-24 | 2024-04-24 | 40 Green Meadow Dr |  | Tewksbury | MA |  | Trips when oven is on | Frigidaire | FPET3077RF |  | KITCHEN | OVEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/16260053886
2024-04-24 20:04 | jian quan | fang | 57608 | 419 Furnace brook pkwy |  | quincy | MA | 2170 | 6174800908 | n/a |  | eaton | Breaker | n/a | 60 |  | 2 Pole | Eaton | Commercial |  | 2024-04-20 | 2024-04-20 | 14 Harvard st |  | Brookline | MA | 2445 | appliance trips the breaker when heating up food, equipment manufacturer suggests replace it with regular breaker | rational | LM100BE.AXXXXX | no | n/a | appliance installed in commercial kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16261578360
2024-04-24 20:04 | jian quan | fang | 57608 | 419 Furnace brook pkwy |  | quincy | MA | 2170 | 6174800908 | n/a |  | eaton | Breaker | n/a | 60 |  | 2 Pole | Eaton | Commercial |  | 2024-04-20 | 2024-04-20 | 14 Harvard st |  | Brookline | MA | 2445 | appliance trips the breaker when heating up food, equipment manufacturer suggests replace it with regular breaker | rational | LM100BE.AXXXXX | no | n/a | appliance installed in commercial kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16261579332
2024-04-25 08:32 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 48 JUNE ST |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLAINCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16263171415
2024-04-25 08:35 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 50 JUNE ST |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16263181675
2024-04-25 08:39 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 52 JUNE ST |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16263197953
2024-04-25 08:41 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 56 JUNE ST |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDBABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16263204742
2024-04-25 08:44 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 87A HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16263213383
2024-04-25 08:46 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 87B HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16263221327
2024-04-25 08:48 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 88A HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16263228499
2024-04-25 08:50 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 88B HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16263236210
2024-04-25 08:52 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 88B HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16263242863
2024-04-25 08:53 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 16 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLAINCE | JB655SK355 |  | AFFORDBALE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16263250013
2024-04-25 10:54 | Roy | Brooks | 14302 | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner |  | Eaton | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-22 | [5 empty] | Each time the stove reached a certain temp. of 450 degrees or above it would trip the GFCI breaker. | Bosch | HBL5651UC/06 |  | Kitchen | Kitchen oven | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16263985943
2024-04-25 11:46 | Thomas | Juzba | 56789 | 9 Pomeroy St |  | West Stockbridge | MA | 1266 | 4138871798 | Electrician |  | HOM240GFI | Breaker | Gfi breaker | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16264331068 | 2024-04-25 | 2024-04-25 | [5 empty] | Breaker tripped when stove was turned on | LG | LREL6325F | None | Single family home | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16264331089 | https://www.formstack.com/admin/download/file/16264331091
2024-04-26 09:23 | Aramis | Weimann | 59274 | 1 Rocky Brook Dr |  | Huntington | MA | 1050 | 4135059515 | Electrician |  | 136935 | Breaker | Cutler Hammer | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/16269464807 | 2024-04-26 | 2024-04-26 | 38 bay path road |  | Spencer | MA | 1562 | Turned on stove. About 10 minutes went by and breaker trip. Reset breaker and tripped again not long after | Kenmore | 911.9114 |  | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16269464821 | https://www.formstack.com/admin/download/file/16269464822
2024-04-26 13:41 | Thomas | Juzba | 56789 | 26 Sunset Drive |  | Montague | MA | 1376 | 4138871798 | Electrician |  | Thql2140gft | Breaker | UPC 783164-48537 | 40 |  | 2 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/16270954383 | 2024-04-15 | 2024-04-15 | [5 empty] | Customer could not use over without breaker tripping | General electric | J bp35s m3ss | None | Single family home | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16270954396 | https://www.formstack.com/admin/download/file/16270954397
2024-04-26 13:41 | Thomas | Juzba | 56789 | 14 Kelleher Drive |  | Deerfield | MA | 1373 | 4138871798 | Electrician |  | QO230GFIC | Breaker | 4prong plug and cord | 30 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16270956198 | 2024-04-06 | 2024-04-05 | [5 empty] | Breaker continues to trip whenever homeowner tries to operate their dryer | Whirlpool | LE4440XWW0 | None | Single family home | Laundry room | No | No | No | No | https://www.formstack.com/admin/download/file/16270956211 | https://www.formstack.com/admin/download/file/16270956212
2024-04-26 13:54 | Alex | Lopez | 51952 | 203 Orchard Street |  | Belchertown | MA | 1007 | 4138871798 | Electrician |  | Hom240gfci | Breaker | Stove breaker | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16271032159 | 2024-04-24 | 2024-04-26 | [5 empty] | Breaker was tripping when customer used stove | General Electric Company | R B758D P1WW | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16271032172 | https://www.formstack.com/admin/download/file/16271032173
2024-04-29 08:58 | Thomas | Ribero | 12759 | 95 Jacoby Ave |  | Pittsfield | MA | 1201 | 413-446-9348 | owner |  | Square D type QO 250 GFCI circuit breaker | Breaker | none | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-24 | 2024-04-16 | [5 empty] | Range kept tripping the breaker. Service tech was sent out to examine the range but could not resolve the issue. He contacted the manufacturer. Manufacturer stated that the range would likely trip the GFCI breaker at any amperage lower than 8 milliamps | AGA | Mercury 36 Induction | none | home | It's the kitchen range. | No | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/16279070459
2024-04-29 10:57 | David | Ryan | 59323 | 84 Fowler Rd |  | Lowell | MA | 1854 | 3214567049 | Foreman |  | SIEMENS 50a 2pole | Breaker | N/a | 50 |  | 2 Pole | Siemens | Residence |  | 2024-04-29 | 2024-04-25 | 748 grayson drive |  | Springfield | MA | 1119 | Nuisance tripping under load | Frigidaire | 316065306 |  | Single family home | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16279742233
2024-04-29 13:42 | Shaemus | ODorherty | 16761 | 67 Crowninshield Road |  | Brookline | MA | 2446 | 617-719-9603 | Electrician |  | QF250A | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16280848382 | 2024-02-02 | 2024-02-02 | [5 empty] | As soon as it is plugged in it is tripping the circuit breaker. We spoke to Yale and they said that this occurs with these stoves and that we should apply to the state to be in the database. | LaCornue Stove | Albertine 36 Series - 12293214011 |  | Single Family Home | Kitchen Stove | Yes | Yes | Yes | No | https://www.formstack.com/admin/download/file/16280848394 | https://www.formstack.com/admin/download/file/16280848395
2024-04-30 11:47 | Brad | patrick | 16808 | 4 cutting ave |  | woburn | MA | 1801 | 9784883800 | master electrician |  | siemens QF250P | Breaker | Siemens 2 pole standard breaker 50 amp | 50 |  | 2 Pole | Siemens | Residence |  | 2024-04-30 | 2024-04-30 | [5 empty] | oven trips every time appliance is turned on. operates normally on standard breaker. this issue was found while upgrading to a 4 wire receptacle and feed. oven is roughly 25 years old. contacted appliance manufacturer and was told that appliance was too old to operate properly with a modern GFCI breaker | ge | zke55sdss | none | kitchen | kitchen oven only. nothing else on circuit | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16285942759
2024-04-30 15:15 | David | Johnson | 23919 | 11 Suncrest Ave |  | Wilmington | MA | 1887 | 6172576333 | electrician |  | siemens- type QPF | Breaker | 2 pole breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2024-04-08 | 2024-04-08 | 9 Applewood Dr |  | Ipswich | MA | 1938 | Freestanding induction range top burners worked okay, one minute after turning on oven GFCI tripped many times | Frigidaire Freestanding Induction Range | GCR13058AF | none | Single family Home | kitchen range | No | No | No | No |  | https://www.formstack.com/admin/download/file/16287470713
2024-04-30 19:49 | Peter | Keller | 13379 | 114 Boston Post Rd |  | Wayland | MA | 1778 | 5088898049 | Electrician/owner |  | QF250A | Breaker | NA | 50 |  | 2 Pole | Siemens | Residence |  | 2024-04-01 | 2024-04-01 | 83 Fox Run |  | Sudbury | MA | 1776 | Kitchen renovation. New Thermador wall oven. Trips the GFCI breaker within 10 seconds of turning unit on | Thermador | PODMC301W | none | Single family dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16289070611
2024-04-30 20:01 | Peter | Keller | 13379 | 114 Boston Post Rd |  | Wayland | MA | 1778 | 5088898049 | Electrician/owner |  | QF250A | Breaker | NA | 50 |  | 2 Pole | Siemens | Residence |  | 2024-04-01 | 2024-04-01 | 83 Fox Run |  | Sudbury | MA | 1776 | Kitchen renovation. New Thermador dual fuel range.¦Breaker trips within seconds of energizing | Thermador | PRD48WDSGU | none | single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16289115116
2024-05-01 08:54 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 20 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16290839096
2024-05-01 08:56 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 22A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16290848469
2024-05-01 08:58 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 22B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16290855989
2024-05-01 09:01 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 24A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | EASTON | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16290865011
2024-05-01 09:03 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 24B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16290874201
2024-05-02 06:59 | Ryan | LaBrache | 22024 | 1 Summer Street |  | Watertown | MA | 2472 | 6179248866 | Onwer |  | QF230A | Breaker | Stab in | 30 |  | 2 Pole | Siemens | Residence |  | 2024-05-01 | 2024-03-20 | 287 Commonweath Ave |  | Boston | MA | 2215 | GFI breaker would not hold when wall oven was running | Wolf Appliance, Inc. | S03050PE/S/P |  | multifamily | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16296147916
2024-05-02 09:44 | William | Booker | 22110 | 1399 East Street |  | Mansfield | MA | 2048 | 5089643532 | master electrician |  | QF230A | Breaker | qf | 30 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16296690761 | 2024-04-29 | 2024-04-29 | 7 beatrice rd |  | franklin | MA | 2038 | steam oven tripping instantly. Contacted manufactor and they stated unit is not recommended or intended to be on a gfci protected circuit. | wolf | sn13614303 | none | single family | wall oven in kitchen | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/16296690775 | https://www.formstack.com/admin/download/file/16296690776
2024-05-02 11:45 | Jonathan | Moreira | 22519 | 6 Concord Rd. |  | Stoneham | MA | 2180 | 7815891970 | Electrician |  | Qfga2n | Breaker | Breaker | 20 |  | 1 Pole | Siemens | Residence |  | 2024-01-23 | 2024-04-12 | 43 Ackers Ave |  | Brookline | MA | 2445 | Built in microwave would consistently trip circuit breaker when it was used. Tried plugging in to two other GFCI protected circuits with same result. | Thermador | MD24WS/03 |  | Two family | Kitchen | No | No | Yes | No | https://www.formstack.com/admin/download/file/16297810839 | https://www.formstack.com/admin/download/file/16297810840
2024-05-02 21:31 | Corey | Hood | 8228 | 55 Anne Road |  | Norwod | MA | 2062 | 7819157358 | Owner |  | GFTCB240 | Breaker | 2 pole | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-26 | 2024-04-25 | 94 Elder Road |  | Needham | MA | 2494 | Oven Trips when heating starts. Happens continuously. Used 2 different breakers (same type) | Thermador | PO302W/02 |  | Residential | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16301048289
2024-05-05 18:53 | Joshua | chabot | 12322 | 1 Eugenia Ln |  | Plaistow | NH | 3865 | 9789143276 | electrician/owner |  | QF250A | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-03 | 2024-05-03 | 44 Maple Ave |  | Andover | MA | 1810 | new Bosch Range will not function on a gfci breaker. tested cord and bonding jumper is removed. gfci instantly trips when plugging in appliance | Bosch | HIS8655U | no other equipment | single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16310273919
2024-05-05 19:11 | Steven | Durnig | 30005 | 220 Summer St. |  | South | MA | 2071 | 508-958-5558 | owner |  | Cutbrn250gf | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-19 | 2024-04-19 | Kitchen |  | Norfolk | MA | 2056 | New electric range top appliance tripping upon initial powering up circuit. | Kitchen Aid | W11362928A |  | Residential | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16310317495
2024-05-05 21:58 | Todd | Whitney | 51157 | 639 Townsend Harbor Road |  | Lunenburg | MA | 1462 | 978-582-4698 | President |  | GFTCB230 | Breaker | N/A | 30 |  | 2 Pole | Eaton | Residence |  | 2024-04-01 | 2024-03-22 | [5 empty] | Unit trips minutes after use of unit. | GE Cafe | C2S950P2M2S1 | Nothing | Kitchen | Kitchen | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/16310708735 | https://www.formstack.com/admin/download/file/16310708736
2024-05-06 09:02 | RANDY | O'GRADY | 12493 | 245 Forge Village |  | Groton | MA | 1450 | 9784486377 | owner |  | Square D Homeline | Breaker | none | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-03 | 2024-05-01 | 12 Farmstead Way |  |  |  |  | Breaker Intermitently Trips when stove is on | Bosch | HIS8655U/05 | none | Kitchen | Kitchen Stove | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/16311952313
2024-05-06 09:41 | Matt | Doremus | 21923 | 244 Cedar St. #3 #3 |  | Somerville | MA | 2145 | 7817386180 | President |  | Siemens QF250A | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2024-04-26 | 2024-04-26 | 244 Cedar St. #3 #3 |  | Newton | MA |  | Cooktop trips the gfci breaker after about 30 seconds of power on. | Wolf | CI36560T/S |  | Kitchen | Induction cooktop appliance in Kitchen | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/16312134657
2024-05-08 16:34 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Owner |  | Eaton BRN240GF | Breaker | no | 40 |  | 2 Pole | Eaton | Residence |  | 2024-04-30 | 2024-04-30 | 292 Westford St. |  | Carlisle | MA |  | Installed a 2 pole 40 amp gfci breaker on a new cook top. Tripped immediately. Replaced the breaker. Had the same result. | Wolf | C136580C/B |  | Single family | Kitchen | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/16326470096
2024-05-08 18:10 | Steve | Laurencio | 18079 | 21 Railroad Ave |  | Bedford | MA | 1730 | 978 621-7221 | Electrician |  | Siemens | Breaker | 0 | 30 |  | 2 Pole | Siemens | Residence |  | 2024-05-07 | 2024-05-07 | 21 Railroad Ave |  | Bedford | MA | 1730 | Wall oven trips on Preheat. | General Electric | PT7800SHASs | Microwave/ Wall Oven. | Kitchen | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16326977191 | https://www.formstack.com/admin/download/file/16326977192
2024-05-08 18:57 | Steve | Laurencio | 18079 | PO BOX 645 |  | Bedford | MA | 1730 | 978 621-7221 | Electrician |  | Siemens QF250A | Breaker | 0 | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-08 | 2024-05-08 | 4 Upland Rd. |  | Andover | MA | 1810 | GFCI circuit breaker tripped instantly when electric cooktop is turned ON. | Miele KM 6375 | O9775920 |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16327169383
2024-05-08 21:20 | Joseph | Penney | 11412 | 3 Daniel Drive |  | Stoneham | MA | 2180 | 6175900558 | electrician |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-23 | 2024-03-06 | 120 Clyde Street |  | Brookline | MA | 2467 | gfci breaker trips within a few minutes of oven being on. Does not trip with a non-gfci breaker. | Wolf Appliance, Inc. | DF48650C/S/P | nothing | single family home (kitchen) | kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16327644897 | https://www.formstack.com/admin/download/file/16327644898
2024-05-09 14:11 | Greg | Zolotas | 23420 | 2 Will Sawyer St. |  | Peabody | MA | 1960 | 978-804-8975 | Owner |  | Murray | Breaker | Arc Fault | 20 |  | 1 Pole | Siemens | Residence |  | 2024-05-09 | 2024-05-09 | Microwave kitchen |  | 8 junction rd | MA |  | Kitchen microwave constant tripping. 2015 renovation. | Murray | A92n51ac | None | Single family | Kitchen microwave | No | No | No | No |  | https://www.formstack.com/admin/download/file/16330974342
2024-05-09 14:51 | George | M Harrison | 10353 | 51 KING STREET | King St | Abington MA 02351 | MA | 2351 | 3397887229 | Onwer/operator |  | Homeline square D | Breaker | none | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-07 | 2024-05-07 | 70 Lovering Heights Unit number 5, 7,9, 10, 11 and 12 |  | Medway | MA | 2053 | Tripping under load | Summit | RE2114W | none | Kitchen | Tripped under load | No | No | No | No |  | https://www.formstack.com/admin/download/file/16331230861
2024-05-11 17:59 | David | Niemi | 20725 | 8 Dunton Rd. |  | Wilmington | MA | 1887 | 6174176112 | Electrician |  | HOM230GFIC | Breaker | NA | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2024-02-09 | 2024-02-09 | 312 Old Connecticut Path |  | Wayland | MA | 1778 | The dryer will not hold while installed on the GFCI breaker. | Samsung | dve45b6300c | None | single family | laundry closet | No | No | No | No |  | https://www.formstack.com/admin/download/file/16339784714
2024-05-13 09:11 | Joseph | mahoney | 54340 | 1 fahey way |  | Billerica | MA | 1821 | 617-293-4022 | Owner |  | Siemens | Breaker | 2 pole GFCI breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-07 | 2024-05-02 | 5 clyde |  | Lexington | MA | 2420 | When 50A 2 pole GFCI breaker is hooked up to electric cooktop it trips instantly. In manufacturers specs it says "" A GFCI is not recommend for this installation, and may cause operational interference."" | Wolf Appliance | CI36560C/B | None | Residential home | Kitchen electric cook top | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16343734767
2024-05-14 08:42 | James | Foster | 20014 | 207 Eliot Street |  | Milton | MA | 2186 | 8575051604 | Project Manager |  | Eaton GFTCB250 | Breaker | Circuit Breaker |  |  | 2 Pole | Eaton | Residence |  | 2024-04-08 | 2024-04-08 | 346 Somerville Ave |  | Somerville | MA | 2143 | GE stoves were provided and cannot integrate with the GFCI Breakers which are causing a constant nuisance tripping. The units listed below are the units where the work was performed.¦¦607, 516, 515, 513, 512, 509, 508, 507, 503, 501, 417, 416, 415, 412, 411, 407, 406, 405, 315, 402, 401, 313, 312, 309, 308, 306, 303, 302, 215, 212, ¦209, 206 | GE | JB256RTSS |  | Kitchen | Kitchen electric stove is not compatible with the GFCI circuit breakers. | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16349558066
2024-05-14 11:51 | MICHAEL | ONEIL | 236465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | master electrician |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 28 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16350655702
2024-05-14 12:00 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 30A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16350709828
2024-05-14 12:02 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 30B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE QAPPLINCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16350726713
2024-05-14 12:06 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 32A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16350748779
2024-05-14 14:26 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 32B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16351658814
2024-05-14 14:28 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 34 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16351676685
2024-05-14 14:30 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 34 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16351691327
2024-05-14 14:34 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 36 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16351715440
2024-05-14 14:38 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 40 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16351741614
2024-05-14 14:41 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 42 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16351763325
2024-05-14 14:50 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 46 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16351821720
2024-05-14 14:53 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 48 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16351845532
2024-05-15 15:54 | Robert | Burkett | 14236 | 193 L St |  | Boston | MA | 2127 | 6173892257 | Owner |  | QF250A | Breaker | 2 pole | 50 |  | 2 Pole | Siemens | Residence |  | 2024-04-17 | 2024-04-17 | 31A Belmont St |  | Charlestown | MA | 2127 | Breaker will not even turn on. The stove manufacturer uses the ground as a neutral. There is no way to separate them | Wolf | IR36550/S/T |  | Single family | Kitchen stove/oven | No | No | No | No | https://www.formstack.com/admin/download/file/16360271051 | https://www.formstack.com/admin/download/file/16360271052
2024-05-15 17:52 | MATTHEW | DOREMUS | 21923 | 244 Cedar St, #3 |  | Somerville | MA | 2145 | 7817386180 | President |  | Eaton BRN230GFCS | Breaker | Class A | 30 |  | 2 Pole | Eaton | Residence |  | 2024-04-24 | 2024-04-24 | 50 Garden St. #1 |  | Cambridge | MA | 2138 | Cooktop tripped immediately upon energizing. Replaced breaker with non-gfci breaker without problems. Left non-gfci breaker installed for 1 week. Returned and re-installed gfci breaker with same exact results | Wolf Induction Cooktop | CI243TF/S |  | Condo | Kitchen induction cooktop | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/16360996996
2024-05-15 20:30 | John | Christoforou | 22420 | 69 HOMESTEAD RD |  | HOLDEN | MA | 1520 | 7742321783 | Owner |  | 40A 2 pole Eaton GFCI breaker | Breaker | None | 40 |  | 2 Pole | Eaton | Residence |  | 2024-05-15 | 2024-03-15 | 58 Deanna Drive |  | HOLDEN | MA | 1520 | This breaker is for an electric stove/cook top. breaker holds when oven is not turned on. however, as soon as owners turn on burns/internal oven, the breaker will trip out. | GE | PB935YPFS | None | Home,Single family. New build | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/16361866275
2024-05-15 20:35 | Vincent | Zizzo | 0 | 21 Foam Ave |  | Revere | ME | 2151 | 7818449037 | Owner |  | Siemens | Breaker | n/a | 20 |  | 1 Pole | Siemens | Residence |  | 2024-01-07 | 2024-01-06 | 18 Woodland Road |  | Medford | MA | 2153 | Fridge would trip every 8 hrs after intial power up. Contacted appliance supplier and manufacturer both stated fridge should be removed from GFCI breaker. | GE | N/A | none | single family | Kitchen fridge | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16361885226
2024-05-16 10:00 | Eric | Caldon | 21306 | 100 DEANVILLE RD |  | ATTLEBORO | MA | 2703 | 7742296409 | owner |  | cutler hammer br | Breaker | none | 40 |  | 2 Pole | Eaton | Residence |  | 2024-05-09 | 2024-05-02 | 27 Berson rd |  | seekonk | MA | 2771 | oven will not turn on at all , instanly trips the breaker upon turning on breaker. equipment is hard wired | GE | JTD5000EN2ES | none | kitchen | kitchen wall oven | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16363810730 | https://www.formstack.com/admin/download/file/16363810731
2024-05-16 14:51 | joe | silverio | 17118 | 32 franklin street |  | lowell | MA | 1844 | 978-851-4900 | electrician |  | eaton | Breaker | n/a | 50 |  | 2 Pole | Eaton | Residence |  | 2024-05-14 | 2024-05-02 | unit 70k parker street |  | acton | MA | 1720 | burners working no issues, oven turned on multiple tripping occurances | general electric | RAS200DM2WW |  | apartment | kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/16365645914
2024-05-16 16:07 | Mathew | Wilson | 21852 | 123 Highland Ave |  | Somerville | MA | 2143 | 5084793865 | Master Electrician |  | Leviton / LB250-323-00G | Breaker | GFCI Breaker | 50 |  | 2 Pole | Leviton | Residence |  | 2023-11-01 | 2023-11-01 | 139 Franklin St |  | Allston | MA | 2134 | Breaker trips immediately after turning on cooktop | Miele | KM6370 |  | Single Family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16366140250
2024-05-17 11:32 | Nick | Bouvier | 55405 | 35 Amherst st |  | Springfield | MA | 1085 | 4133190444 | Electrician |  | AD-910 | Breaker | None | 30 |  | 2 Pole | Industrial | Residence | https://www.formstack.com/admin/download/file/16370257182 | 2024-05-17 | 2024-05-10 | [5 empty] | Tripping when running dryer | Kenmore | 110.652 | None | Home | Pantry | No | No | No | No | https://www.formstack.com/admin/download/file/16370257217 | https://www.formstack.com/admin/download/file/16370257220
2024-05-20 14:54 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 28 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16381804835
2024-05-20 14:56 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 30A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16381818660
2024-05-20 14:59 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 30B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16381837838
2024-05-20 15:02 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 32A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16381859791
2024-05-20 15:05 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 32B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16381877241
2024-05-20 15:08 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 34 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16381895190
2024-05-20 15:12 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 36 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16381924414
2024-05-20 15:14 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 38 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16381937790
2024-05-20 15:17 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 40 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16381957507
2024-05-20 15:27 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 42 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16382034156
2024-05-20 15:30 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 44 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB644SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16382053038
2024-05-20 15:33 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 46 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16382076511
2024-05-20 15:59 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | master electrician |  | gftcb250 | Breaker | breaker |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 48 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16382241614
2024-05-20 16:01 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 50 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16382258920
2024-05-20 16:42 | Jesse | Kuhlman | 21804 | 313 Eastern Avenue |  | Lynn | MA | 1902 | 6176762620 | OWNER |  | Square D, Homeline | Breaker | none | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-10 | 2024-04-23 | 6 Rockne Ave |  | Boston | MA | 2124 | Breaker would trip when oven not in use. | Samsung | NE63B8211SS |  | Single family home | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16382528795
2024-05-20 22:04 | James | McCormack | 22340 | 1 Cobblers Ln |  | Ipswich | MA | 1938 | 9784710544 | Owner |  | LB240-G | Breaker | Hydraulic Magentic | 40 |  | 2 Pole | Leviton | Residence |  | 2024-05-20 | 2024-05-16 | 51 Heath St |  | Somerville | MA | 2145 | When the cooktop runs it trips the GFCI circuit breaker | GE | PHP9030DTBB | None | Condominium | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16383870581
2024-05-21 08:40 | Alex | Lopez | 51952 | 203 Orchard Street |  | Belchertown | MA | 1007 | 4138871798 | Electrician |  | Hom240gfci | Breaker | Stove breaker | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16385206251 | 2024-04-24 | 2024-04-26 | [5 empty] | Breaker was tripping when customer used stove | General Electric Company | R B758D P1WW | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16385206264 | https://www.formstack.com/admin/download/file/16385206265
2024-05-21 09:12 | Nathan | Ashe | 21136 | 241 River st Ext |  | Billerica | MA | 1821 | 9785943519 | Master Electrician |  | GFTCB260 | Breaker | N/A | 60 |  | 2 Pole | Eaton | Residence |  | 2024-05-09 | 2024-02-02 | 89 N. High St |  | Foxborough | MA | 2035 | Whirlpool range causing 60A GFI to trip. Went through the entire circuit found no other issues with the wiring or equipment | Whirlpool | WFE320M0JS3 |  | Single family home | Kitchen Range is the only equipment affected by the GFI tripping | No | No | No | No | https://www.formstack.com/admin/download/file/16385342668 | https://www.formstack.com/admin/download/file/16385342669
2024-05-21 09:42 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-04-17 | 2024-04-16 | 52 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16385504046
2024-05-21 09:45 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 55 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16385517737
2024-05-21 09:47 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELCTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 56 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16385530556
2024-05-21 09:50 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 58 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16385550190
2024-05-21 09:53 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 54 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16385568975
2024-05-21 09:55 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 60 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16385580868
2024-05-21 09:57 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 62 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16385590718
2024-05-21 09:59 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 64 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16385605004
2024-05-21 10:02 | John | Vespa | 17144 | 250 Milton st, LL007 |  | Dedham | MA | 2026 | 617 325 1151 | Owner |  | GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2024-05-16 | 2024-05-14 | 27 May st |  | Boston | MA | 2130 | Breaker tripping on new stove installation, stove not compatible with GFCI breaker. | Frigidaire | GCFI3060BF |  | Single family | kitchen appliance. | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/16385618861
2024-05-21 10:22 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 66A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16385732548
2024-05-21 10:24 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 66B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16385745648
2024-05-21 10:26 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 68A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16385756946
2024-05-21 10:28 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 68B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16385768714
2024-05-21 13:34 | Brandon | Daniels | 1971 | 895 Salem Street |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Siemens | Breaker | 2 pole 50A GFCI | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-15 | 2024-03-15 | 27 Victor Street Unit 9 |  | Haverhill | MA | 1832 | Frequent tripping when electric range was in use | GE | JB2560M3BB |  | Apartment | Kitchen range | No | No | No | No
2024-05-21 13:39 | Trevor | Hebb | 1971 | 895 Salem Street |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Siemens QPF GFCI | Breaker | QPF GFCI | 50 |  | 2 Pole | Siemens | Residence |  | 2024-01-19 | 2024-01-19 | 37 woodcock st |  | Haverhill | MA | 1832 | Tripping while heating | GE | JB2560 M3BB |  | Apartment | Kitchen | No | No | No | No
2024-05-21 13:42 | Trevor | Hebb | 1971 | 895 Salem Street |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Siemens | Breaker | QPF | 50 |  | 2 Pole | Siemens | Residence |  | 2024-02-15 | 2024-02-15 | 28 Victor Street |  | Haverhill | MA | 1832 | Tripping while heating | whirlpool | WFC31550JB3 |  | Apartment | Kitchen | No | No | No | No
2024-05-21 13:45 | Jake | Carlan | 1971 | 895 Salem Street |  | Groveland | MA | 1834 | 9783731393 | electrician |  | L2207171384 | Breaker | Siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | [5 empty] | Breaker trips when oven is on | GE | JB256D M3BB |  | N/A | Kitchen | No | No | No | No
2024-05-21 13:48 | Jake | Carlan | 1971 | 895 Salem Street |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | L2305030312 | Breaker | Siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-04 | 2024-03-04 | [5 empty] | trips when oven is on | GE | JB258DM5BB |  | Apartment | kitchen | No | No | No | No
2024-05-21 14:13 | David | DeGrazia | 17119 | PO Box 299 |  | E. Freetown | MA | 2717 | 5085420179 | Master Electrician / Owner |  | Eaton | Breaker | NA | 30 | NA | 2 Pole | Eaton | Residence |  | 2024-04-22 | 2024-02-01 |  |  | 461 North Road Sudbury | MA | 1776 | when appliance is turned on circuits are tripped shortly there after This is an ongoing problem? issue | Whirlpool | WED5605MW0 | NA | residence group home | laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16387237217
2024-05-21 14:17 | David | DeGrazia | 17119 | PO Box 299 |  | E. Freetown | MA | 2717 | 5085420179 | Mater electrican/owner |  | Eaton | Breaker | NA | 40 | NA | 2 Pole | Eaton | Residence |  | 2024-04-22 | 2024-02-01 |  |  | 461 North Road Sudbury | MA | 1776 | When appliance is turned on the breaker trips shortly there after | Whirlpool | WOES3030LS00 | na | residence group hoe | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16387264074
2024-05-21 19:57 | Larry | LaFountain | 32397 | 40 Reservation rd |  | holyoke | MA | 1040 | 413-575-9491 | owner/operator |  | SIEMENS QF240A | Breaker | none | 40 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16389056358 | 2024-04-10 | 2024-04-09 | 19 pleasant view drive |  | hatfield | MA | 1038 | Circuit and appliance tested and all operating within manufacturer specs.¦¦New appliance does not work on a GFCI breaker as it trips upon running. ¦¦Ran appliance element multiple times on broil to burn off any manufactures oils/residues and still tripped as before.¦¦Appliance runs flawlessly on a non-GFCI breaker | Frigidaire | PCFI3668AF | none | single family residential kitchen | Circuit and appliance tested and all operating within manufacturer spec¦¦New appliance does not work on a GFCI breaker as it trips upon running. ¦¦Ran appliance element multiple times on broil to burn off any manufactures oils/residues and still tripped as before.¦¦Appliance runs flawlessly on a non-GFCI breaker | No | No | No | No | https://www.formstack.com/admin/download/file/16389056372 | https://www.formstack.com/admin/download/file/16389056373
2024-05-22 07:53 | jonathan | ferrera | 57718 | 57 shore dr |  | auburn | MA | 1501 | 9787607969 | electrician |  | General Electric | Breaker | n/a | 50 |  | 2 Pole | ABB | Residence |  | 2024-04-10 | 2024-03-15 | 202 berlin rd |  | marlborough | MA | 1752 | 50 amp ABB gfci breaker keeps tripping owner had the manufacture do a visit and replaced the top burner and bottom burner. the brand was whirlpool. then they had that unit replaced with a Maytag range . | Maytag | MER6600FW6 |  | single family home | the kitchen range on the first floor | No | Yes | No | Yes |  | https://www.formstack.com/admin/download/file/16390544593
2024-05-22 09:58 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 70 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391035727
2024-05-22 10:00 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 72A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391046382
2024-05-22 10:02 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 72B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSIG | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391055762
2024-05-22 10:04 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICAIN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 74A BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391068030
2024-05-22 10:10 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 74B BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391100315
2024-05-22 10:13 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 76 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391111617
2024-05-22 10:18 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 200 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391140535
2024-05-22 10:20 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 202 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORSBALE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391150349
2024-05-22 10:22 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 204 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391161251
2024-05-22 10:24 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 206 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB6555SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391171528
2024-05-22 10:26 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 208 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDBALE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391183405
2024-05-22 10:28 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 210 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391192586
2024-05-22 10:43 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 212 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391282863
2024-05-22 10:45 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 214 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391295188
2024-05-22 10:49 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 216 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391319445
2024-05-22 10:51 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 218 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391329122
2024-05-22 10:53 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 220 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391339524
2024-05-22 10:54 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 222 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16391349770
2024-05-22 17:41 | Michael | Bell | 17374 | P.O. Box 1038 |  | Plymouth | MA | 2362 | 5082948148 | Licensed Electrician |  | Eaton BR220 GFCI | Breaker | NA | 20 |  | 2 Pole | Eaton | Residence |  | 2024-05-01 | 2024-05-01 | 15 Haven Road |  | Plymouth | MA | 2360 | This is a wall oven on a new dedicated circuit. The oven will not get up to temperature without tripping the GFI breaker. We tried a second GFI breaker with the same results. The appliance distributer sent out a service person who tested and found that this oven is not compatible with a GFI breaker. | GE | ZTSX1FPSN2SS | none | Single family dwelling | Kitchen: single wall oven on dedicated circuit | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16393817623
2024-05-24 07:18 | jack | griffin | 25919 | 26 JOANNA DR |  | South Yarmouth | MA | 2664 | 9784792521 | owner |  | siemans | Breaker | 0 | 20 |  | 1 Pole | Siemens | Residence |  | 2024-05-13 | 2024-04-01 | 37 Clamshell |  | Chatham | MA |  | the breaker trips randomly | thermodor | t36ft820ns |  | 1 family | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16400893694
2024-05-24 07:35 | jack | griffin | 25919 | 26 JOANNA DR |  | South Yarmouth | MA | 2664 | 9784792521 | owner |  | sqd homeline 40 amp | Breaker | 0 | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-22 | 2024-05-21 | 219 |  | Chatham | MA |  | the range trips the breaker | bosch | his8655u /05 |  | kitchen | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16400931929
2024-05-24 08:32 | jack | griffin | 25919 | 26 JOANNA DR |  | South Yarmouth | MA | 2664 | 9784792521 | owner |  | seimens | Breaker | 0 | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-17 | 2024-05-17 | 15 Nickerson |  | Eastham | MA |  | oven breaker trips | bosch | hblp752uc/07 |  | 1 family | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16401087815
2024-05-28 05:43 | Matthew | Bachand | 23450 | 14 Turner Rd |  | Charlton | MA | 1507 | 7746331023 | President/Installer |  | THQL2150GFT2-GFT | Breaker | HACR | 50 |  | 2 Pole | ABB | Residence |  | 2024-05-14 | 2024-05-13 | 66 Ward St |  | Worcester | MA | 1610 | When stove burners were turned on GFCI breaker would trip. Tried replacing with new burners. Problem got worse. Tried to ""burn in"" burners with regular breaker then reinstall GFCI breaker to no avail. | General Electric | J BP35D M1WW | none | Multi family | Kitchen Stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/16412645988
2024-05-28 11:31 | Steven | Rooney | 0 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | service manager |  | Eaton BR | Breaker | 2p50 | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-05 | 2023-10-05 | 16G Ashland Street Worcester |  |  |  |  | old stove trip breaker right away | GE | JBP66BOB1wit | no | apartment style condo | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16414084019
2024-05-28 11:35 | Steven | Rooney | 50969 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service Manager |  | Eaton | Breaker | 2p50 | 50 |  | 2 Pole | Eaton | Residence |  | 2023-10-05 | 2023-10-05 | 401 South Street |  |  |  |  | breaker trip instantly | Whirlpool | MOD RF266LX50 | none | apartment style condo | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16414117227
2024-05-28 11:42 | Steven | Rooney | 50969 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service Manager |  | Eaton 2p50 GFI BR breaker | Breaker | 2p50 | 50 | none | 2 Pole | Eaton | Residence |  | 2023-08-30 | 2023-08-30 | 401 South Street |  |  |  |  | keep tripping breaker, new stove | Frigidaire | FCFE306AS | none | apartment style condo | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16414180020
2024-05-28 11:50 | Steven | Rooney | 50969 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service Manager |  | Eaton 2p50 BR GFI breaker | Breaker | none | 50 | none | 2 Pole | Eaton | Residence |  | 2023-12-15 | 2023-12-15 | 401 South Street |  |  |  |  | new stove, new wiring, breaker trips | GE | JB645rk9SS | none | apartment style condo | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16414227751
2024-05-28 11:55 | Steven | Rooney | 50969 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service manager |  | Eaton BR 2p50GFI | Breaker | none | 50 | none | 2 Pole | Eaton | Residence |  | 2023-12-15 | 2023-12-15 | 204 Franklin Crossing Rd |  | Franklin | MA |  | new stove and new wiring ,trips the breaker | GE | JB645RK9SS | none | apartment style condo | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16414266831
2024-05-28 12:00 | Steven | Rooney | 50969 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service manager |  | BR | Breaker | none | 50 | none | 2 Pole | Eaton | Residence |  | 2023-08-30 | 2023-08-30 | 11 Davis Road Unit C7 |  | Acton | MA |  | new wiring, new stove. breaker trip when stove is plug in | Frigidaire | FCFE3062AS | none | apartment style condo | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16414300573
2024-05-28 12:04 | Steven | Rooney | 50969 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | service manager |  | Eaton | Breaker | none | 50 | none | 2 Pole | Eaton | Residence |  | 2023-08-30 | 2023-08-30 | 16 Ashland St Unit 3L |  | Worcester | MA |  | breaker keep tripping instantly | Whirlpool | MOD RF266LX50 | none | apartment style condo | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16414324948
2024-05-28 12:05 | David | DeGrazia | 17119 | PO Box 299 |  | E Freetown | MA | 2717 | 5085420179 | Master Electrician/Owner |  | Eaton | Breaker | NA | 30 |  | 2 Pole | Eaton | Residence |  | 2024-04-18 | 2024-03-18 | 66 West Blvd |  | Onset | MA | 2558 | when appliance is turned on circuits are tripped shortly thereafter. This is an ongoing problem/issue | Whirlpool | WED 5605MW0 | NA | residence | Laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16414333745
2024-05-28 12:11 | David | DeGrazia | 17119 | PO Box 299 |  | E Freetown | MA | 2717 | 5085420179 | Master Electrician/Owner |  | Eaton | Breaker | na | 40 |  | 2 Pole | Eaton | Residence |  | 2024-04-18 | 2024-03-18 | 66 West Blvd |  | Onset | MA | 2558 | when appliance is truned on breaker trips shortly thereafter | Whirlpool | WOES3030LS00 | na | single family | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16414367112
2024-05-28 12:23 | David | DeGrazia | 17119 | PO Box 299 |  | E. Freetown | MA | 2717 | 5085420179 | Master Electrician/Owner |  | Eaton | Breaker | na | 30 |  | 2 Pole | Eaton | Residence |  | 2024-05-01 | 2024-04-01 | 5 Long Neck Rd |  | Wareham | MA | 2571 | when appliance is turned on circuits are tripped shortly thereafter This is an ongoing problem/issue | Whirlpool | WED 5605MWO | NA | residential group home | Laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16414442474
2024-05-28 12:27 | David | DeGrazia | 17119 | PO Box 299 |  | E. Freetown | MA | 2717 | 5085420179 | Master Electrician/Owner |  | Eaton | Breaker | na | 40 |  | 2 Pole | Eaton | Residence |  | 2024-05-01 | 2024-04-01 | 5 Long Neck Rd |  | Wareham | MA | 2571 | when applaince is turned on breaker trips shortly threafter | Whirlpool | WOES3030LS00 | na | residential group home | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16414473681
2024-05-28 13:48 | Brian | Doherty | 31892 | 162 willow Rd | #3 | Nahant | MA | 1908 | 781-953-7801 | Electrician |  | LB250-GST | Breaker | Smart | 50 |  | 2 Pole | Leviton | Residence |  | 2024-05-08 | 2024-05-01 | 16 Woodchester dr |  | Weston | MA |  | We tested cooktop when installed, seemed ok. Customer went to use it over this weekend and it tripped every time. | Wolf | Mod Ci365C/B |  | 1 fam | Kitchen cooktop only | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16415005269 | https://www.formstack.com/admin/download/file/16415005270
2024-05-28 14:16 | Brian | Doherty | 31892 | 162 willow Rd | #3 | Nahant | MA | 1908 | 781-953-7801 | Electrician |  | Leviton/LB250-GST | Breaker | Leviton | 50 |  | 2 Pole | Leviton | Residence | https://www.formstack.com/admin/download/file/16415196635 | 2024-05-02 | 2024-05-02 | 16 Woodchester dr |  | Weston | MA |  | Breaker nuisance tripping started immediately. Followed manufacturer's instructions and installed a regular breaker just to burn off oils. Re-installed GFI breaker and it seemed ok. Breaker tripped multiple times on its own with or without using oven. | Wolf | DO30PM/S/PH | 0 | 1 family | Oven only | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16415196649 | https://www.formstack.com/admin/download/file/16415196650
2024-05-28 18:43 | Brian | Doherty | 31892 | 162 willow Rd | #3 | Nahant | MA | 1908 | 781-953-7801 | Electrician |  | Leviton/LB250-GST | Breaker | Leviton | 50 |  | 2 Pole | Leviton | Residence | https://www.formstack.com/admin/download/file/16416762223 | 2024-05-02 | 2024-05-02 | 16 Woodchester dr |  | Weston | MA |  | Breaker nuisance tripping started immediately. Followed manufacturer's instructions and installed a regular breaker just to burn off oils. Re-installed GFI breaker and it seemed ok. Breaker tripped multiple times on its own with or without using oven. | Wolf | DO30PM/S/PH | 0 | 1 family | Oven only | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16416762237 | https://www.formstack.com/admin/download/file/16416762238
2024-05-29 10:22 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | master electrician |  | gftcb250 | Breaker | breaker |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 81 HighCrest Terrace |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419201043
2024-05-29 10:27 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 83A HighCrest Terrace |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419229825
2024-05-29 10:29 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 83B High Crest Terrace |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419241580
2024-05-29 10:32 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 85A High Crest Terrace |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419256384
2024-05-29 10:35 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 85B High Crest Terrace |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419275413
2024-05-29 10:38 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 73 High Crest Terrace |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419290672
2024-05-29 10:41 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 75 High Crest Terrace |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419310632
2024-05-29 10:43 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 77 High Crest Terrace |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419323356
2024-05-29 10:49 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 79 High Crest Terrace |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419357032
2024-05-29 11:31 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 201 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419618014
2024-05-29 11:33 | MICHAEL | ONEIL | 0 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 207 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419630665
2024-05-29 11:35 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 209 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419643659
2024-05-29 11:39 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 211 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419670174
2024-05-29 11:41 | MICHAEL | ONEIL | 0 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 215 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419683291
2024-05-29 11:43 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 217 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDBALE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419696568
2024-05-29 11:44 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 223 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419709423
2024-05-29 11:46 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 225 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419721604
2024-05-29 11:48 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GGFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 231 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419732983
2024-05-29 11:54 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 40 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE THE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16419773788
2024-05-30 12:00 | Travis | Prairie | 23595 | 115 King Street |  | Franklin | MA | 2038 | 7745711907 | Owner |  | GFTCB240 | Breaker | no | 40 |  | 2 Pole | Eaton | Residence |  | 2024-05-09 | 2024-05-08 | 92 South Street |  | Foxboro | MA | 2035 | During the service change, a new 4 wire range circuit was ran and after installing on a GFCI breaker it began to trip after 10 minutes of the oven being on. This happened constantly and tried to run the oven multiple times. | Maytag | MER6755AAS | no | Single family dewelling | The range in the kitchen was the only equipment affected. | No | Yes | No | No | https://www.formstack.com/admin/download/file/16425307330 | https://www.formstack.com/admin/download/file/16425307331
2024-05-31 09:28 | Brooke | Heisler-Leary | 58767 | 16 Dalton St |  | Wilbraham | MA | 1095 | 4132658094 | Electrician |  | QO240GFICP | Breaker | Square D | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-10 | 2024-03-01 | [5 empty] | Breaker trips with oven preheating | GE | JB735DP2WW |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16430754697
2024-06-03 08:49 | Thomas | Juzba | 56789 | 28 Jeffrey Circle |  | Southwick | MA | 1077 | 4138871798 | Electrician |  | QO240GFI | Breaker | 2pole | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16440632621 | 2024-06-03 | 2024-06-03 | [5 empty] | The breaker trips when turning on the stove | Kenmore | 79090313014 | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16440632634 | https://www.formstack.com/admin/download/file/16440632635
2024-06-03 20:18 | James | Murray | 55471 | 83 Warren Rd |  | Townsend | MA | 01469-1360 | 19785024927 | Electrician |  | Eaton GFTGCB250 | Breaker | None | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-26 | 2024-04-24 | 83 Warren Rd |  |  |  |  | Upon installation of new Electric Range GFCI Breaker trips immediately when equipment is plugged in. | Electrolux | ECFI3668AS | None | Single Family Dwelling | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16444595346
2024-06-03 20:45 | James | Murray | 55471 | 83 Warren Rd |  | Townsend | MA | 1469 | 9785024927 | Electrician |  | Eaton GFTGCB250CS | Breaker | None | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-26 | 2024-04-24 | 6 Gale Meadow Way |  | Westborough | MA | 1581 | Upon Installation of new Electric Range GFCI Breaker would trip immediately when plugged in. | Electrolux | ECFI3668AS | None | Single Family Dwelling | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16444685283
2024-06-04 10:20 | Thomas | Juzba | 56789 | 28 Jeffrey Circle |  | Southwick | MA | 1077 | 4138871798 | Electrician |  | QO240GFI | Breaker | 2pole | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16446749801 | 2024-06-03 | 2024-06-03 | [5 empty] | The breaker trips when turning on the stove | Kenmore | 79090313014 | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16446749814 | https://www.formstack.com/admin/download/file/16446749815
2024-06-04 15:49 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor |  | Eaton | Breaker | no | 50 |  | 2 Pole | Eaton | Residence |  | 2024-05-31 | 2022-12-22 | 22 Dean Lane |  | Littleton | MA | 1460 | Installed the beaker two years ago. Home owner had no problem until they tried to use the broil setting. Installed new breaker. No change. | GE | J B256R M2SS |  | Single family | Kitchen. | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16448829688
2024-06-05 10:14 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-05-17 | 2024-05-16 | 231 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT THE GFCI BREAKER, ONCE THE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16452184963
2024-06-05 10:15 | BRIAN | MCSWINEY | 57199 | 104 ADAMS ST |  | MEDFIELD | MA | 2052 | 5083597954 | ELECTRICIAN |  | EATON GFTCB230 | Breaker | NONE | 30 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/16452187710 | 2024-05-31 | 2024-05-02 | 120 SEAVER ST |  | BROOKLINE | MA |  | DRYER KEPT TRIPPING BREAKER. CHECKED ALL CONNECTIONS AND METERED OUT THE WIRING. CHECKED DRYER FOR GROUNDS OR SHORTS AND MADE SURE THE JUMPER WAS REMOVED.DID NOT FIND ANYTHING WRONG. | LG | DLE7400WE | NONE | SINGLE FAMILY HOME | DRYER IN LAUNDRY ROOM | No | No | No | No | https://www.formstack.com/admin/download/file/16452187731 | https://www.formstack.com/admin/download/file/16452187732
2024-06-06 06:49 | Michael | todd | 13793 | 4 Hugh Ter |  | Peabody | MA | 1960 | 6172573537 | Electrician |  | Siemens 0150544E82617 | Breaker | Gfci only | 30 |  | 2 Pole | Siemens | Residence |  | 2024-06-05 | 2024-06-05 | 4 Hugh Ter |  | Peabody | MA | 1960 | GFCI breaker cleared to dryer receptacle. Then trips when plugging in new speed queen dryer ground and neutral wires are both isolated on dry cord terminations | Speed queen | ADEE9RYS178TW01 |  | Home | Laundry room dryer only | No | No | No | No |  | https://www.formstack.com/admin/download/file/16457044382
2024-06-07 15:15 | Brian | Ferreira | 53423 | 124 shady brook lane |  | Springfield | MA | 2780 | 4133349561 | Electrician |  | Square d | Breaker | Homeline | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-03 | 2024-06-07 | [5 empty] | When stove gets brought to temperature the breaker swapped out breaker now no more issues | General Electric | 164D3871P008-9 |  | Home | Kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/16464595994
2024-06-11 11:46 | AJ | Tabrizi | 21477 | 10 Regis Rd |  | Andover | MA | 1810 | 9787193610 | president |  | Siemens QPF30 | Breaker | 30 AMP 2 pole GFI | 30 |  | 2 Pole | Siemens | Residence |  | 2024-05-22 | 2024-05-22 | 45 Hidden Rd |  | Westin | MA | 2493 | we used a 2 pole -30 amp GFI for a double stacked washer and dryer.¦the breaker hold if nothing connected to it. as soon as washer is connected it trips.¦if we replace the breaker with normal it would hold even with appliance conncted. | LG Single unit washtower Design | LG Studio |  | single family house | Laundry room | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16478045173
2024-06-11 14:11 | Alex | Lopez | 51952 | 203 Orchard Street |  | Belchertown | MA | 1007 | 4138871798 | Electrician |  | Hom240gfci | Breaker | Stove breaker | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16478997736 | 2024-04-24 | 2024-04-26 | [5 empty] | Breaker was tripping when customer used stove | General Electric Company | R B758D P1WW | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16478997749 | https://www.formstack.com/admin/download/file/16478997750
2024-06-13 08:27 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 165 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16487913390
2024-06-13 08:30 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 167 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16487923728
2024-06-13 08:33 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 171 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16487931838
2024-06-13 08:43 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 1 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 175 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16487968138
2024-06-13 08:45 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 177 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16487977150
2024-06-13 08:50 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 179 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KICTHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16487995188
2024-06-13 08:53 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 183 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488004580
2024-06-13 08:55 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 185 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488012446
2024-06-13 09:01 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 187 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488034186
2024-06-13 09:06 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 174 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488058458
2024-06-13 09:09 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 180 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488069415
2024-06-13 09:11 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 182 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488080123
2024-06-13 09:13 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 184 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488088466
2024-06-13 09:15 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 190 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488096992
2024-06-13 09:17 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 276 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488106342
2024-06-13 09:19 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 278A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488116254
2024-06-13 09:24 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 278B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488137485
2024-06-13 09:37 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 280A BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488196735
2024-06-13 09:39 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 280B BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488206291
2024-06-13 09:41 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 282 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488215733
2024-06-13 10:11 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 284 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488380670
2024-06-13 10:24 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 286 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488452509
2024-06-13 10:28 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 290 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSIN | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488474657
2024-06-13 10:30 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREKAER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 292 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488486584
2024-06-13 10:32 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 294 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488497710
2024-06-13 11:06 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | master electrician |  | ge appliance | Breaker | breaker |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 298 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488691803
2024-06-13 11:11 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 300 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488724020
2024-06-13 11:13 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 302 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16488735777
2024-06-14 09:32 | Eric | Caldon | 21306 | 100 DEANVILLE RD |  | ATTLEBORO | MA | 2703 | 7742296409 | owner |  | cutler hammer BR | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/16493438394 | 2024-06-03 | 2024-06-11 | 469 south worcester st |  | norton | MA | 2766 | range will not turn on and instanely trips | whirlpool | ksis730psso | none | kitchen | kitchen appliance | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16493438408 | https://www.formstack.com/admin/download/file/16493438409
2024-06-14 09:42 | Eric | Caldon | 21306 | 100 DEANVILLE RD |  | ATTLEBORO | MA | 2703 | 7742296409 | owner |  | cutler hammer br | Breaker | N/A | 30 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/16493488936 | 2024-06-03 | 2024-06-11 | 469 south worcester st |  | norton | MA | 2766 | wall oven will not operate immediately trips | whirlpool | kose500ess21 | none | kitchen | kitchen wall oven | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16493488950 | https://www.formstack.com/admin/download/file/16493488951
2024-06-17 11:26 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 41 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16503129905
2024-06-17 11:29 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRCIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 43 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16503147203
2024-06-17 11:31 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 45 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AAFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16503163447
2024-06-17 11:33 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 47 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16503178784
2024-06-17 11:36 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 49 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16503197618
2024-06-17 11:39 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 51 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16503212522
2024-06-17 11:41 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 57 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655AK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16503223208
2024-06-17 11:53 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | JB655SK355 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 53 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16503301233
2024-06-17 11:54 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 55 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16503312895
2024-06-17 11:56 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 59 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655AK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16503325227
2024-06-17 11:59 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 61 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16503345303
2024-06-17 12:09 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 63 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16503410091
2024-06-17 12:12 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 65 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16503425246
2024-06-17 13:39 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | master electrician |  | gftcb250 | Breaker | breaker |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 67 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16504294481
2024-06-17 13:42 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 71 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JN655AK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16504320949
2024-06-17 13:44 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 5 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16504333361
2024-06-17 13:49 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 15 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16504359250
2024-06-17 13:51 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 19 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16504375739
2024-06-17 13:53 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 21 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16504388658
2024-06-17 13:55 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 25 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16504399051
2024-06-17 13:57 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 29 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | G E APLLIANCE | JB655SK355 |  | AFFORDABLE | KITCHNE | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16504410261
2024-06-17 13:59 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 31 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER, ONCE FULL LOAD AMPERAGE IS REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16504421333
2024-06-18 08:46 | Aramis | Weimann | 59274 | 1 Rocky Brook Dr |  | Huntington | MA | 1050 | 4136855169 | Electrician |  | 4884006004 | Breaker | Breaker | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16508074481 | 2024-06-18 | 2024-06-18 | 34 Elaine Drive |  | Pittsfield | MA | 1201 | Nuisance tripping | Maytag | MER5770AAA | None | Single Family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16508074495 | https://www.formstack.com/admin/download/file/16508074496
2024-06-18 12:15 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | master electrician |  | gftcb250 | Breaker | breaker |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 42 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509255776
2024-06-18 12:17 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 46 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509266955
2024-06-18 12:19 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 48 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDBALE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509281621
2024-06-18 12:21 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 50 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509292360
2024-06-18 12:25 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 56 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509321441
2024-06-18 12:28 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 58 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509336435
2024-06-18 13:31 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | master electrician |  | gftcb250 | Breaker | breaker |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 60 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509714508
2024-06-18 13:33 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 62 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509725142
2024-06-18 13:34 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 64 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509735016
2024-06-18 13:43 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 66 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509786455
2024-06-18 13:46 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 68 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509805840
2024-06-18 13:48 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 70 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509815453
2024-06-18 13:50 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 72 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509826970
2024-06-18 13:52 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 74 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509842984
2024-06-18 13:54 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 80 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE HAS BEEN REACHED. | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16509852951
2024-06-18 14:15 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor |  | Semiens | Breaker | Arc fault | 20 |  | 1 Pole | Siemens | Residence |  | 2024-06-11 | 2024-06-14 | 103 Pilgrim Rd. |  | Concord | MA | 1742 | Installed a new 20 amp seperate circuit. Installed a dual function breaker, for the fridge. It continues to trip. Installed a new breaker. No change. | Samsung | RF 28T5105R |  | Single family | Kitchen. | No | No | No | No |  | https://www.formstack.com/admin/download/file/16509981010
2024-06-18 15:25 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor |  | Siemens | Breaker | no | 20 |  | 2 Pole | Siemens | Commercial |  | 2024-06-12 | 2024-06-11 | 508 Groton Rd. |  | Westford, | MA | 1460 | Installed a new 20 amp 240 volt circuit for a new Sanitizer. It continuously¦trips. Checked the breaker. No change. | Fagor | 19058739 |  | Commercial. | Kitchen. | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16510425401
2024-06-19 08:02 | Ryan | LaBrache | 22042 | 1 Summer Street |  | Watertown | MA | 2472 | 617-924-8866 | Onwer |  | QF250A | Breaker | NA | 50 |  | 2 Pole | Siemens | Residence |  | 2024-06-18 | 2024-06-10 | 32 Highland St |  | Cambridge | MA | 2138 | Breaker will trip during preheat | GE appliance | ZTDX1DSSN2SS |  | single family home | Kitchen wall oven | No | No | No | No |  | https://www.formstack.com/admin/download/file/16513323656
2024-06-19 18:19 | Tony | Marroquin | 14426 | 22 Whalen Rd |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB230 | Breaker | GFCI | 30 |  | 2 Pole | Eaton | Residence |  | 2024-06-14 | 2024-02-02 | 28 Whalen Rd |  | Hopkinton | MA | 1748 | LG Dryer consistently trips breaker when used. | LG | DLEX8600BE |  | Single Family | Laundry Room | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/16516155500
2024-06-20 14:51 | Brooke | Heisler-Leary | 58767 | 283 Poole St |  | Ludlow | MA | 1056 | 4132658094 | Electrician |  | QF240A | Breaker | Breaker 40amp siemens | 40 |  | 2 Pole | Siemens | Residence |  | 2024-06-20 | 2024-06-20 | 36 Line St |  | Easthampton | MA | 1027 | Breaker tripped while oven was preheating | Samsung | NE59K3310SB/AA |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16520806472
2024-06-21 15:49 | Alexander | Bielunis | 8653 | 8 Sequoia Dr |  | Holyoke | MA | 1040 | 4135622988 | Manager |  | Leviton LB120-DFT | Breaker | GFCI | 20 |  | 1 Pole | Leviton | Residence |  | 2024-06-05 | 2024-06-05 | 1325 South East St |  | Amherst | MA | 1002 | Refrigerator constantly trip the GFCI | Dacor | DRF367500AP | None | 1 Family Home | Refrigerator Only | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16526400530
2024-06-21 16:46 | Alexander | Bielunis | 8653 | 8 Sequoia Dr |  | Holyoke | MA | 1040 | 4135622988 | Master Electrician |  | Leviton LB120-DFT | Breaker | GFCI | 20 |  | 1 Pole | Leviton | Residence |  | 2024-06-05 | 2024-06-05 | 1325 South East St |  | Amherst | MA | 1002 | Refrigerator constantly trip GFCI breaker | Dacor | DRF367500AP | none | 1 Family home | Only the Refrigerator | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16526686346
2024-06-21 17:03 | Alexander | Bielunis | 8653 | 8 Sequoia Dr |  | Holyoke | MA | 1040 | 4135622988 | Master Electrician |  | Leviton LB230-GF | Breaker | GFCI | 40 |  | 2 Pole | Leviton | Residence |  | 2024-06-05 | 2024-06-05 | 1325 South East St |  | Amherst | MA | 1040 | Electric Range constantly trip the GFCI breaker | Wolf | IR36550/S/Tp | None | 1 Family home | Only the Range | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16526765131
2024-06-21 17:23 | Alexander | Bielunis | 8653 | 8 Sequoia Dr |  | Holyoke | MA | 1040 | 4135622988 | Master Electrician |  | Leviton | Breaker | GFCI | 30 |  | 2 Pole | Leviton | Residence |  | 2024-06-05 | 2024-06-05 | 1325 South East St |  | Amherst | MA | 1040 | Dryer constantly trip the GFCI breaker | Electrolux | Elite 76ooAT | None | 1 Family Home | Dryer Constantly Trips the GFCI breaker | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16526850692
2024-06-23 12:45 | Jonathan | Rossborough | 35645 | 12 CEDAR LN |  | KINGSTON | MA | 2364 | 6175293755 | Electrician |  | ITE QF250A | Breaker | Siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-06-21 | 2024-06-19 | 44 Hawthorne Rd |  | Hanover | MA | 2339 | breaker trips once oven is turned on in pre-heat | Bosch | HIS8655U |  | Single family with in-law | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16530909157
2024-06-24 10:48 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | master electrician |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 169 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16534070556
2024-06-24 10:50 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 193 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16534085057
2024-06-24 10:52 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 203 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16534096554
2024-06-24 10:54 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 172 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16534112371
2024-06-24 10:57 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-06 | 2024-06-05 | 74 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16534128248
2024-06-25 16:37 | Eugeniu | Bodron | 56889 | 22 Carl Ghilani Cir |  | Ashland | MA | 1721 | 9072295711 | Electrician |  | Siemens qf250a | Breaker | None | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-07 | 2024-05-01 | 153 Randlett park |  | Newton | MA | 2465 | Electric stove and kitchen constantly tripped GFCI breaker tried to replacing with two other new circuit breakers, which did not solve the problem. | Bertazzoni | Mas365inmbiv | None | Single family dwelling | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16541728535 | https://www.formstack.com/admin/download/file/16541728536
2024-06-26 11:12 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | master electrician |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 10 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16544981483
2024-06-26 11:14 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 12 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16544993100
2024-06-26 11:16 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 14 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545004351
2024-06-26 11:18 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 16 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545016721
2024-06-26 11:20 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 18 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545027465
2024-06-26 11:22 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 20A HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545037477
2024-06-26 11:23 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 20B HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545047977
2024-06-26 11:26 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 24 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545064109
2024-06-26 11:28 | GERALD | MCGRAW | 18146 | 5 MINNESOTA AVE | UNIT 6 | WARWICK | RI | 2888 | 4017399473 | OWNER |  | HOM250GFI | Breaker | 0 | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16545075802 | 2024-06-05 | 2024-05-02 | 3102 CRANBERRY HIGHWAY |  | WAREHAM | MA |  | WHEN STOVE TURNS ON IT IMMEDIATELY TRIPS THE BREAKER IN BOTH BUILDINGS E & F ALL 63 UNITS | GE | JBS460DM4BB | 0 | APARTMENT | KITCHEN | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16545075816 | https://www.formstack.com/admin/download/file/16545075817
2024-06-26 11:28 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 26A HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545077248
2024-06-26 11:30 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 26B HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545089378
2024-06-26 11:32 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 28A HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545102147
2024-06-26 11:34 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 28B HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545113859
2024-06-26 11:49 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 30 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545207210
2024-06-26 11:51 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 32A HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545220645
2024-06-26 11:53 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 32B HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545229696
2024-06-26 11:55 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 34A HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545240548
2024-06-26 11:57 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 34B HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545253122
2024-06-26 11:59 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 36 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545266753
2024-06-26 12:02 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 38 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545282862
2024-06-26 12:03 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 40 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545291577
2024-06-26 12:21 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 7 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545399145
2024-06-26 12:25 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 1 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 9 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545418766
2024-06-26 12:56 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 11 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545603988
2024-06-26 12:58 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 19 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545616278
2024-06-26 13:00 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 21 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545627996
2024-06-26 13:02 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 25 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545645178
2024-06-26 13:04 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 27 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSINF=G | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545658091
2024-06-26 13:06 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 29 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545673132
2024-06-26 13:08 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 31 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545686760
2024-06-26 13:09 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 33 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545702100
2024-06-26 13:11 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 35 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545717188
2024-06-26 13:13 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 37 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545731156
2024-06-26 13:19 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 37 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545773729
2024-06-26 13:22 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5085358001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREKAER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 43 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545789347
2024-06-26 13:24 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 25 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545803877
2024-06-26 13:50 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 74 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545974687
2024-06-26 13:52 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 80 HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16545989559
2024-06-26 13:54 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 20A HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16546006103
2024-06-26 13:56 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 20B HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16546016577
2024-06-26 13:57 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 22A HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16546027646
2024-06-26 13:59 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 22B HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16546038475
2024-06-26 14:01 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 24 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16546047825
2024-06-26 14:02 | MICHAEL | ONEIL | 2365 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 188 BLUE LEDGE DR |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16546058683
2024-06-27 08:52 | Paul | Bergeron Jr. | 21807 | 20 Burncoat Ter |  | Worcester | MA | 1605 | 5087357245 | Owner |  | Eaton BR | Breaker | breaker | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/16549570946 | 2024-06-01 | 2024-06-01 | 18 Sawmill Drive |  | Northborough | MA | 1532 | installed GFCI protection for range. Client attempted to cook dinner and the breaker tripped multiple times. Swapped to standard breaker. | GE | PHS930YPAFS |  | single-family | kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16549570959 | https://www.formstack.com/admin/download/file/16549570960
2024-06-28 18:00 | Corey | Hood | 8228 | 55 Anne Road |  | Norwood | MA | 2062 | 781-915-7358 | Owner |  | Eaton/Cutler Hammer | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-05-24 | 2024-05-23 | 43 Heath Hill Street |  | Brookline | MA | 2445 | New installation of residential free standing range. Breaker would trip instantly when oven was turned on. Allowed oven to run on standard 2 pole breaker for 2-3 hours, then retried GFCI breaker. Same problem occured. | Miele | H7840BM/HR1955-3G DFGR | None | Single Family Home | Main kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16557436358
2024-06-28 18:11 | Corey | Hood | 8228 | 55 Anne Road |  | Norwood | MA | 2062 | 7819157358 | Owner |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-05-24 | 2024-05-23 | 43 Heath Hill Street |  | Brookline | MA | 2445 | New residential electric range. Would trip GFCI breaker after starting oven. Tried to allow oven to run on standard breaker for 2-3 hours. Retried GFCI breaker. Same issue occured | Miele | H7840BM/HR1955-3G-DFGR | None | Single Family Home | Main Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16557474929
2024-06-28 18:16 | Corey | Hood | 8228 | 55 Anne Road |  | Norwood | MA | 2062 | 7819157358 | Owner |  | GFTCB250 | Breaker | Circuit Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-05-22 | 2024-05-22 | 363 Far Reach Road |  | Westwood | MA | 2090 | New free standing range installation. Breaker continuously tripped when oven was in use | Wolf | IR36550/S/T | none | Single Family Home | Main Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16557494413
2024-07-02 08:56 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 22A HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16570243429
2024-07-02 08:58 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 22B HIGHCREST TERRACE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16570253598
2024-07-02 09:00 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 74 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16570262568
2024-07-02 09:04 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 76 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16570276449
2024-07-02 09:06 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 78 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16570285896
2024-07-02 09:08 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICAIN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 5 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16570294817
2024-07-02 09:11 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 15 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16570308554
2024-07-02 09:13 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 17 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/16570321189
2024-07-02 09:16 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 23 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16570331435
2024-07-02 09:20 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-15 | 2024-06-14 | 37 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16570353161
2024-07-02 09:22 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-16 | 2024-06-15 | 39 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/16570365627
2024-07-02 09:25 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-16 | 2024-06-15 | 41 HIGHCREST ROAD |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16570377766
2024-07-02 09:26 | Michael | Pupa | 22876 | 43 Donna ave |  | Gardner | MA | 1440 | 781-724-6244 | Owner-President |  | Eaton brn120df | Breaker | Gfci | 20 |  | 1 Pole | Eaton | Residence |  | 2023-02-09 | 2022-11-02 | 5 valerie circle |  | Ashburnham | MA | 1430 | Would trip breaker before dishwasher completes washing | Samsung | Dw8om2020us |  | Single family dwelling | Only the dishwasher which is on a dedicated circuit | No | No | No | No | https://www.formstack.com/admin/download/file/16570386268 | https://www.formstack.com/admin/download/file/16570386269
2024-07-02 09:28 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-16 | 2024-06-15 | 27 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16570391498
2024-07-02 09:29 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-16 | 2024-06-15 | 29 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16570399935
2024-07-02 09:32 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-16 | 2024-06-15 | 31 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16570412707
2024-07-02 13:19 | joe | silverio | 17118 | 32 franklin street |  | lowell | MA | 1844 | 9788514900 | electrician |  | eaton | Breaker | na | 50 |  | 2 Pole | Eaton | Residence |  | 2024-06-29 | 2024-06-24 | unit 80 J parker street |  | acton | MA | 1720 | burners will work and when oven is turned on, after few minutes breaker will trip | general electric | RAS200DM2WW | na | apartment | kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/16571840810
2024-07-02 13:54 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-16 | 2024-06-15 | 33 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16572074177
2024-07-02 13:57 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-16 | 2024-06-15 | 35 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APPLIANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16572087763
2024-07-02 13:58 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-16 | 2024-06-15 | 37 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLIANCE | JB655SK355 |  | KITCHEN | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16572100084
2024-07-02 14:00 | MICHAEL | ONEIL | 23465 | 14 NORFOLK AVE | Norfolk Ave | EASTON | MA | 2375 | 5082308001 | MASTER ELECTRICIAN |  | GFTCB250 | Breaker | BREAKER |  |  | 2 Pole | Eaton | Residence |  | 2024-06-16 | 2024-06-15 | 39 BLUE LEDGE DRIVE |  | ROSLINDALE | MA | 2131 | RANGE TRIPS OUT GFCI BREAKER ONCE FULL LOAD AMPERAGE IS REACHED | GE APLLANCE | JB655SK355 |  | AFFORDABLE HOUSING | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16572110152
2024-07-02 14:11 | [11 empty] | HOLF IR30450/S/T | Panel | GFCI | 50 |  | 2 Pole | Eaton | Residence |  | 2024-06-28 | 2024-06-28 | 300 VIRGINIA RD |  | CONCORD | MA |  | FOUR WIRE INSTALLATION ASK TO INSTALL A WIRE NUT ON THE WHITE NEUTRAL WIRE. GFCI KEEPS TRIPPING. | HOLF | IR30450/S/T |  | Kitchen STOVE | FOUR WIRE INSTALLATION ASK TO INSTALL A WIRE NUT ON THE WHITE NEUTRAL WIRE. GFCI KEEPS TRIPPING. | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/16572180286 | https://www.formstack.com/admin/download/file/16572180287
2024-07-03 08:13 | Alex | Lopez | 51952 | 203 Orchard Street |  | Belchertown | MA | 1007 | 4138871798 | Electrician |  | Hom240gfci | Breaker | Stove breaker | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16575625821 | 2024-04-24 | 2024-04-26 | [5 empty] | Breaker was tripping when customer used stove | General Electric Company | R B758D P1WW | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16575625845 | https://www.formstack.com/admin/download/file/16575625846
2024-07-03 08:25 | Thomas | Juzba | 56789 | 470 East State Street |  | Granby | MA | 1033 | 4138871798 | Electrician |  | Hom240gfi | Breaker | 2 pole breaker | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16575669584 | 2024-07-02 | 2024-07-01 | [5 empty] | Breaker tripped stove | Maytag | Mer8700ds1 | None | Single family home | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16575669606 | https://www.formstack.com/admin/download/file/16575669607
2024-07-03 10:08 | Michael | Pupa | 22876 | 43 Donna ave |  | Gardner | MA | 1440 | 781-724-6244 | Owner-President |  | Eaton brn120df | Breaker | Gfci | 20 |  | 1 Pole | Eaton | Residence |  | 2023-02-09 | 2022-11-02 | 5 valerie circle |  | Ashburnham | MA | 1430 | Would trip breaker before dishwasher completes washing | Samsung | Dw8om2020us |  | Single family dwelling | Only the dishwasher which is on a dedicated circuit | No | No | No | No | https://www.formstack.com/admin/download/file/16576110589 | https://www.formstack.com/admin/download/file/16576110590
2024-07-08 08:42 | [11 empty] | Eaton Breaker | Receptacle | n/a | 30 | n/a | 2 Pole | Eaton | Residence |  | 2024-07-01 | 2024-06-30 | 47 Birchtree Road |  | Westwood | MA | 2090 | When the dryer is in the ""on"" position it keeps tripping the GFCI | GE | GFD85ESPN1RS | n/a | Single Family | laundry room dryer plug | No | No | No | No |  | https://www.formstack.com/admin/download/file/16592266405
2024-07-08 09:14 | Hugo | Lucero | 22526 | 88 -Maple st |  | 88-maple st | MA | 2451 | 6179352779 | Owner |  | 2F2508 | Breaker | No | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16592406641 | 2024-07-08 | 2024-07-08 | 390 HurÃ³n ave |  |  | MA | 2138 | Kitchen electric cooktop GFCI breaker is tripping the cooktop it does not have a neutral. | GEA Electric cooktop | PHP9036DT1BB | No | Two family | Kitchen cooktop only | No | No | No | Yes | https://www.formstack.com/admin/download/file/16592406655 | https://www.formstack.com/admin/download/file/16592406656
2024-07-08 12:03 | Hugo | Lucero | 22526 | 88 -Maple st |  | 88-maple st | MA | 2451 | 6179352779 | Owner |  | 2F2508 | Breaker | No | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16593427942 | 2024-07-08 | 2024-07-08 | 390 HurÃ³n ave |  |  | MA | 2138 | Kitchen electric cooktop GFCI breaker is tripping the cooktop it does not have a neutral. | GEA Electric cooktop | PHP9036DT1BB | No | Two family | Kitchen cooktop only | No | No | No | Yes | https://www.formstack.com/admin/download/file/16593427963 | https://www.formstack.com/admin/download/file/16593427964
2024-07-08 12:52 | Jake | Carlan | 58120 | 895 Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | M2206070023 | Breaker | n/a | 40 |  | 2 Pole | Siemens | Residence |  | 2024-06-03 | 2024-07-03 | 29 Victor Street Unit 4 |  | Haverhill | MA |  | Breaker trips when stove is turned on to preheat | GE | JB256DM3BB |  | Apartment | Kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/16593747680
2024-07-08 13:59 | Hugo | Lucero | 22526 | 88 -Maple st |  | 88-maple st | MA | 2451 | 6179352779 | Owner |  | 2F2508 | Breaker | No | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16594178264 | 2024-07-08 | 2024-07-08 | 390 HurÃ³n ave |  |  | MA | 2138 | Kitchen electric cooktop GFCI breaker is tripping the cooktop it does not have a neutral. | GEA Electric cooktop | PHP9036DT1BB | No | Two family | Kitchen cooktop only | No | No | No | Yes | https://www.formstack.com/admin/download/file/16594178278 | https://www.formstack.com/admin/download/file/16594178279
2024-07-09 14:02 | Mike | Melchione | 22847 | 1 Royson Dr | Bldg1 Unit 7 | Kingston | MA | 2364 | 781-585-4900 | Managing Member |  | Eaton/CHN250GF | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/16600022705 | 2024-06-23 | 2024-06-23 | 4 Great Pine Dr |  | Bourne | MA | 2532 | Trips When Range Is On Broil | Samsung | NE58K9850WS | N/A | Single Family Dwelling | Range In Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16600022719 | https://www.formstack.com/admin/download/file/16600022720
2024-07-10 11:21 | Larry | Difoggio | 17422 | 55 POND | Unit 2a | Waltham | MA | 2451 | 7813309011 | Director of operations |  | wolf Wall oven S03060PE-S-P | Breaker | none | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-02 | 2024-07-01 | 120 Seaver st Brookline |  |  |  |  | Oven will not function with GFCI protection | Wolf wall Oven | S03060PE-S-P |  | condo | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16605182144
2024-07-10 12:43 | Eric | Caldon | 21306 | 100 Deanville Ave |  | Attleboro | MA | 2703 | 774-229-6409 | Owner |  | CAFE/CTD70DP2N4S1 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/16605844909 | 2024-06-25 | 2024-06-25 | 105 Ronald C Meyer |  | North Attleboro | MA |  | Oven will not turn on and instantly turns off | CAFE | CTD70DP2N4S1 | double oven | Kitchen | Kitchen oven | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16605844924 | https://www.formstack.com/admin/download/file/16605844925
2024-07-10 12:52 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor |  | Eaton | Breaker | No | 60 |  | 2 Pole | Eaton | Residence |  | 2024-07-08 | 2024-07-03 | 241 Depot Rd |  | Boxborough | MA | 1719 | Installed a new 60 GFCI breaker on a new range. Breaker continued to trip. Checked breaker no change. | BSH Home appliance. | HIS8655U |  | Single family | Kitchen. | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16605899633
2024-07-10 12:59 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor |  | Eaton | Breaker | No | 30 |  | 2 Pole | Eaton | Residence |  | 2024-07-08 | 2024-07-03 | 241 Depot Rd. |  | Boxborough | MA | 1719 | Installed a new 30 amp GFCI breaker on the existing Dryer. Breaker continues to trip. Checked breaker no change. | LG | DLEX8000W |  | Single Family | Laundry room. | No | No | No | No |  | https://www.formstack.com/admin/download/file/16606204654
2024-07-10 14:10 | MICHAEL | CAMPANIELLO | 23649 | 86 Walkeen Koziol Rd | 1391 | Warren | MA | 1083 | 7742391539 | CO OWNER |  | HOM240GFI | Breaker | PUSH IN | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16607819633 | 2024-07-10 | 2024-07-10 | 3 NIBLICK RD |  | SHREWSBURY | MA | 1545 | INSTANT TRIP | BOSCH | HBL87M53UC/05 | NONE | KITCHEN | JUST OVEN | No | No | No | No | https://www.formstack.com/admin/download/file/16607819651 | https://www.formstack.com/admin/download/file/16607819652
2024-07-10 14:10 | MICHAEL | CAMPANIELLO | 23649 | 86 Walkeen Koziol Rd | 1391 | Warren | MA | 1083 | 7742391539 | CO OWNER |  | HOM240GFI | Breaker | PUSH IN | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16607822321 | 2024-07-10 | 2024-07-10 | 3 NIBLICK RD |  | SHREWSBURY | MA | 1545 | INSTANT TRIP | BOSCH | HBL87M53UC/05 | NONE | KITCHEN | JUST OVEN | No | No | No | No | https://www.formstack.com/admin/download/file/16607822335 | https://www.formstack.com/admin/download/file/16607822336
2024-07-11 12:43 | Eddie | Stack | 17422 | 55 pond st | Unit 2a | Waltham | MA | 2451 | 7813309011 | director of operations |  | Sqaure D /Q0260 | Breaker | 2 pole | 60 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-10 | 2024-07-04 | 120 Seaver st Brookline |  | brookline | MA | 2445 | Breaker will not hold while oven is being used | Wolf | IR36550/s/p |  | Kitchen | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16612763153
2024-07-11 12:49 | Eddie | Stack | 17422 | 55 pond st | Unit 2a | Waltham | MA | 2451 | 7813309011 | director of operations |  | Square D | Breaker | 2 pole | 60 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-10 | 2024-07-03 | 120 Seaver st Brookline |  | brookline | MA | 2445 | Breaker will not hold during use of oven | wolf | S03060pm/s/p |  | condo | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16612799104
2024-07-12 14:20 | [11 empty] | 1597TRW | Receptacle | N/A | 15 |  | 1 Pole | Legrand | Residence |  | 2024-07-01 | 2024-06-17 | 19 Kettle Drum Lane |  | Chatham | MA | 2633 | GFCI outlets trip for Miele washer and dryer when wash/dry cycles begin | Miele | W1 Excellence / T1 Excellence | N/A | Single Family | Laundry Closet | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/16618723606
2024-07-12 17:32 | Steve | Laurencio | 18079 | PO BOX 645 |  | Bedford | MA | 1730 | 978 621-7221 | Owner |  | Siemens QF250 | Breaker | 0 | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-12 | 2024-07-12 | 874 Strawberry Hill Rd. |  | Concord | MA | 1742 | Circuit breaker tripped instantly when plugged in. | Bosch | HI58655U/05 | No | Single family | Electric stove in kitchen. | No | No | No | No |  | https://www.formstack.com/admin/download/file/16619829003
2024-07-15 14:54 | Thomas | Juzba | 56789 | 107 hudson st |  | Springfield | MA | 1118 | 4138871798 | Electrician |  | Hom240 gfci | Breaker | 2 pole | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16628656044 | 2024-07-15 | 2024-07-03 | 107 hudson st |  | Springfield | MA | 1118 | Breaker tripped as homeowner tried to use range | Fridgidare | VF91608884 | None | Single family home | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16628656058 | https://www.formstack.com/admin/download/file/16628656059
2024-07-17 07:52 | Andrew | Woodford | 21637 | 74 SAND ST |  | GARDNER | MA | 1440 | 9787308870 | President |  | Square D Homeline | Breaker | none | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-08 | 2024-05-24 | 13 Fisher St |  | Baldwinville | MA | 1436 | GFI breaker trips when built in oven is turned on. | GE | JT3000SF3SS |  | Single family | Kitchen appliance | No | Yes | No | No | https://www.formstack.com/admin/download/file/16637197064 | https://www.formstack.com/admin/download/file/16637197068
2024-07-17 08:48 | Thomas | Juzba | 56789 | 107 hudson st |  | Springfield | MA | 1118 | 4138871798 | Electrician |  | Hom240 gfci | Breaker | 2 pole | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16637382555 | 2024-07-15 | 2024-07-03 | 107 hudson st |  | Springfield | MA | 1118 | Breaker tripped as homeowner tried to use range | Fridgidare | VF91608884 | None | Single family home | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16637382569 | https://www.formstack.com/admin/download/file/16637382570
2024-07-17 10:04 | Chri | Polny | 11660 | 325 Hopping Brook |  | Holliston | MA | 1746 | 7742178986 | VP Electrical Operations |  | Siemens QF120A | Breaker | N/A | 20 |  | 1 Pole | Siemens | Residence |  | 2024-07-12 | 2024-07-12 | 10 Nichols St |  | Southborough | MA | 1746 | Installed new circuit for exterior sump pump. Went to test pump and GFCI tripped immediately. Tried different GFCI breaker still tripped. Checked wiring and pump. Removed GFCI breaker and held on standard breaker. | Basement Technololgy | BDSHD-NS |  | Single family | Exterior sump pump | No | No | No | No |  | https://www.formstack.com/admin/download/file/16637727597
2024-07-18 06:41 | Andre | Marnet | 58597 | 273 #2 | Lexington St | Boston | MA | 2128 | 6175108617 | Electrician |  | CH240GF | Breaker | NA | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/16642290137 | 2024-07-11 | 2024-07-11 | 12 Newbury St |  | Somerville | MA | 2144 | When the range is plugged into the receptacle, the breaker trips immediately. | Miele | HR 1622-3 |  | Residential | Kitchen | No | No | Yes | No | https://www.formstack.com/admin/download/file/16642290150 | https://www.formstack.com/admin/download/file/16642290151
2024-07-18 08:55 | MICHAEL | BELL | 17374 | PO Box 1038 |  | Plymouth | MA | 2362 | 5082948148 | President |  | Eaton BR 250GFCI | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2024-07-17 | 2024-03-08 | 15 Haven Road |  | Plymouth | MA | 2360 | This cooktop has had multiple tripping with no consistent timing. Yale electric looked at unit and deemed it fine. I installed 2 different (same model) GFI breakers and have had the issue with both. | GE Monogram | ZHU35RSTSS | NONE | Single family home | Kitchen induction cooktop | No | No | No | No |  | https://www.formstack.com/admin/download/file/16642662312
2024-07-18 08:58 | Thomas | Juzba | 56789 | 107 hudson st |  | Springfield | MA | 1118 | 4138871798 | Electrician |  | Hom240 gfci | Breaker | 2 pole | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16642676742 | 2024-07-15 | 2024-07-03 | 107 hudson st |  | Springfield | MA | 1118 | Breaker tripped as homeowner tried to use range | Fridgidare | VF91608884 | None | Single family home | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16642676756 | https://www.formstack.com/admin/download/file/16642676757
2024-07-18 09:16 | Thomas | Juzba | 56789 | 213 east stahl road |  | Sheffield | MA | 1222 | 4138871798 | Electrician |  | HOM250GFCI | Breaker | 2pole | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16642768676 | 2024-07-17 | 2024-07-18 | [5 empty] | Over kept tripping when homeowner went to use it | GE | JBP25bom1wh | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16642768689 | https://www.formstack.com/admin/download/file/16642768690
2024-07-18 12:07 | Serghei | Morari | 55932 | 31 bay rd |  | Sharon | MA | 2067 | 617 642 1712 | electrician |  | THQL2150GFT GE | Breaker | double pole | 50 |  | 2 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/16643782029 | 2024-06-28 | 2024-06-04 | 16 falcon st |  | Sharon | MA | 2067 | When the range is in use there is no tripping. When the oven is used to bake there is no tripping. However when the convention bake feature is used the breaker is tripping. | GE appliances | PSS93YP9FS | not applicable | single family | kitchen | No | Yes | No | No | https://www.formstack.com/admin/download/file/16643782043 | https://www.formstack.com/admin/download/file/16643782044
2024-07-18 19:17 | Steve | Laurencio | 18079 | 32 Wildwood Drive |  | Bedford | MA | 1730 | 978621-7221 | Electrician |  | Siemens QF 250A | Breaker | 0 | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-18 | 2024-07-18 | 16 Wyncrest Circle |  | Andover | MA | 1810 | Circuit breaker tripped when ignition for burner is turned on or when oven is turned on. | Wolf Appliance. | DF48650G/S/P/LP | No | Single Family | Kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/16646128738
2024-07-19 09:29 | Christine | Miller | 60582 | 92 Massachusetts Ave |  | Ludlow | MA | 1056 | 4138871798 | Electrician |  | Thql2140gft | Breaker | 2pole | 40 |  | 2 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/16647956052 | 2024-07-18 | 2024-07-15 | [5 empty] | Oven trips when homeowner tries to use it | Kenmore | 79092202016 | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16647956065 | https://www.formstack.com/admin/download/file/16647956066
2024-07-22 13:31 | Jennifer | Sweet | 18329 | 525 | Coronation Drive | Franklin | MA | 2038 | 5085414117 | Owner/operator |  | WFE550S0HZ1 | Breaker | Square D homeline | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-22 | 2023-12-14 | 2 Summer hill rd |  | Medway | MA | 2053 | Oven trips breaker when broiler option is used | Whirlpool | WFE550S0HZ1 | None | House | Kitchen stove only | No | No | No | No | https://www.formstack.com/admin/download/file/16658471122 | https://www.formstack.com/admin/download/file/16658471124
2024-07-22 16:42 | Jennifer | Sweet | 18329 | 525 | Coronation Drive | Franklin | MA | 2038 | 5085414117 | Owner/operator |  | WFE550S0HZ1 | Breaker | Square D homeline | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-22 | 2023-12-14 | 2 Summer hill rd |  | Medway | MA | 2053 | Oven trips breaker when broiler option is used | Whirlpool | WFE550S0HZ1 | None | House | Kitchen stove only | No | No | No | No | https://www.formstack.com/admin/download/file/16659732290 | https://www.formstack.com/admin/download/file/16659732291
2024-07-22 16:59 | Mike | Melchione | 22847 | 1 Royson Dr | Bldg1 Unit 7 | Kingston | MA | 2364 | 5083602886 | Managing Member |  | Siemens | Breaker | n/a | 50 |  | 2 Pole | Siemens | Residence |  | 2024-03-19 | 2024-03-19 | 15 Driftwood Lane |  | Plymouth | MA | 2360 | tripping on bake | Chef | RC17 |  | Range | Range | No | No | No | No |  | https://www.formstack.com/admin/download/file/16659827419
2024-07-22 19:41 | Jennifer | Sweet | 18329 | 525 | Coronation Drive | Franklin | MA | 2038 | 5085414117 | Owner/operator |  | WFE550S0HZ1 | Breaker | Square D homeline | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-22 | 2023-12-14 | 2 Summer hill rd |  | Medway | MA | 2053 | Oven trips breaker when broiler option is used | Whirlpool | WFE550S0HZ1 | None | House | Kitchen stove only | No | No | No | No | https://www.formstack.com/admin/download/file/16660539038 | https://www.formstack.com/admin/download/file/16660539039
2024-07-23 06:29 | David | DeGrazia | 17119 | PO Box 299 |  | E. Freetown | MA | 2717 | 5085420174 | MASTER ELECTRICIAN/OWNER |  | EATON | Breaker | NA | 40 |  | 2 Pole | Eaton | Residence |  | 2024-06-24 | 2024-04-01 | 5 KINGSLEY WAY |  | REHOBOTH | MA | 2769 | when appliance is turned on breaker trips shortly thereafter | whirlpool | WOES 3030LS00 | NA | RESIDENTIAL | KITCHEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/16662067436
2024-07-23 06:40 | DAVID | DEGRAZIA | 17119 | 5 KINGSLEY WAY |  | Rehoboth | MA | 2769 | 8085420174 | MASTER ELECTRICAN/OWNER |  | EATON | Breaker | NA | 30 | NA | 2 Pole | Eaton | Residence |  | 2024-06-24 | 2024-06-03 | 5 Long Neck Rd |  | Rehoboth | MA | 2769 | WHEN APPLIANCE IS TURNED ON CIRCUITS ARE TRIPPED SHORTLY THERE AFTER THIS IS AN ON GOING PROBLEM | WHIRLPOOL | WED 5605MWO | NA | RESIDENTAIL GROUP HOME | LAUNDRY ROOM | No | No | No | No |  | https://www.formstack.com/admin/download/file/16662089326
2024-07-23 11:09 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 774.551.6061 | Project Manager |  | Siemens 0129539 E82617 | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-03 | 2024-06-14 | [5 empty] | Breaker repeatedly trips with range oven heating. | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1423 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16663195350
2024-07-23 14:22 | Mark | Flores | 52255 | 97 Groveland Ave |  | South Weymouth | MA | 2190 | 7816643215 | Electrician |  | BRN230GFCS | Breaker | N/A | 30 |  | 2 Pole | Eaton | Residence |  | 2024-07-02 | 2024-06-25 | 4 Pioneer Rd |  | Hingham | MA | 2043 | CUSTOMER INSTALLED THERMADOR OVEN, OVEN CONSISTANTLY TRIPS GFCI BREAKER, WHILE RUNNING. | THERMADOR | MED301LWS/03 | NONE | SINGLE FAMILY RESIDENCE KITCHEN | KITCHEN | No | No | No | No | https://www.formstack.com/admin/download/file/16664402477 | https://www.formstack.com/admin/download/file/16664402478
2024-07-23 18:25 | Hugo | Lucero | 22526 | 88 |  | Maple st | MA | 2451 | 617-935-2779 | Owner |  | Qpf2 | Breaker | No | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16665784323 | 2024-07-23 | 2024-07-23 | 390 HurÃ³n ave |  |  | MA | 2138 | GFCI breaker is tripping for electric cooktop that doesn't have a neutral 240 volts Electric cooktop . | Electric cooktop GE | PHP9036DTIBB | No | Two family | Only kitchen cooktop countertop | No | No | No | Yes | https://www.formstack.com/admin/download/file/16665784337 | https://www.formstack.com/admin/download/file/16665784338
2024-07-23 18:39 | ALAN | GILLIGAN | 11296 | 22 hyde st |  | quincy | MA | 2169 | 6172932562 | Electrician |  | Siemens | Breaker | NO | 50 | NO | 2 Pole | Siemens | Residence |  | 2024-07-22 | 2024-07-22 | 23 Chisholm Road |  | Roslindle | MA | 2131 | BREAKER TRIPS WHEN OVEN TURNED ON | GE | JB655SK3SS |  | SINGLE FAMILY HOME | KITCHEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/16665837939
2024-07-23 19:03 | ALAN | GILLIGAN | 11296 | 22 HYDE STREET |  | QUINCY | MA | 2169 | 6172932562 | ELECTRICIAN |  | SIEMENS | Breaker | NO | 50 | NO | 2 Pole | Siemens | Residence |  | 2024-07-22 | 2024-07-22 | 23 CHISOLM ROAD |  | ROSLINDALE | MA | 2131 | BREAKER TRIPS WHEN OVEN TURNS ON | SIEMENS | JB655SK3SS | NO | SINGLE FAMILY HOME | KITCHEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/16665931605
2024-07-24 08:16 | Duane | Rego | 22902 | 128 | Sonnys Way | Dighton MA 02715 | MA | 2715 | 5088379464 | owner |  | BRN250GF | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2024-04-10 | 2024-04-10 | 15 Fairfield Avenue |  | Malden | MA | 2148 | Breaker trips when appliance is plugged in. | Whirlpool | WFE320M0JS0 | None | Residential | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16667716098 | https://www.formstack.com/admin/download/file/16667716099
2024-07-24 13:04 | Joshua | Lathrop | 53880 | 121 Maple st |  | northborough | MA | 1532 | 617-595-2429 | Electrician |  | GFTCB250 | Breaker | none | 50 |  | 2 Pole | Eaton | Residence |  | 2024-06-07 | 2023-12-13 | 11 Harris Ave |  | Northborough | MA | 1532 | The tripping incident has been happening ever since the install. This is the 3rd GFCI circuit breaker that i have installed at this location. The circuit breaker trips almost every day. | GE | PHS93OYPFS |  | Residential Home | This circuit breaker trips the stove.¦¦Homeowner has contacted GE and had a Tehnician come out to check the stove out. They said this happens a lot. | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/16669259431
2024-07-25 10:10 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 774.551.6061 | Owner PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-04 | 2024-06-14 | Unit 1422 |  | Weymouth | MA | 2189 | With over heating | Whirlpool | WEE515SOLS2 |  | Apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16673642111
2024-07-25 10:18 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 774.551.6061 | Owner PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-06 | 2024-06-14 | Unit 1424 |  |  |  |  | With over heating | Whirlpool | WEE515SOLS2 |  | Apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16673683746
2024-07-25 10:21 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 774.551.6061 | Owner PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-06 | 2024-06-14 | Unit 1420 |  |  |  |  | with oven warming | Whirlpool | WEE515SOLS2 |  | apartment | Unit 1420 kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16673700503
2024-07-25 10:23 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 774.551.6061 | Owner PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-07 | 2024-06-14 | [5 empty] | when oven warming | Whirlpool | WEE515SOLS2 |  | apartment | Unit 1200 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16673714464
2024-07-25 10:26 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 774.551.6061 | Owner PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-08 | 2024-06-14 | Unit 1203 |  |  |  |  | When over warming | Whrilpool | WEE515SOLS2 |  | apartment | Unit 1203 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16673729745
2024-07-25 10:28 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 774.551.6061 | Owner PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-09 | 2024-06-14 | [5 empty] | When over warming | Whirlpool | WEE515SOLS2 |  | apartment | Unit 1230 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16673742840
2024-07-25 10:30 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 774.551.6061 | Owner PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-10 | 2024-06-14 | [5 empty] | When over warming | Whirlpool | WEE515SOLS2 |  | apartment | Unit 1232 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16673756425
2024-07-25 10:32 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 774.551.6061 | Owner PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-11 | 2024-06-14 | [5 empty] | When over warming | Whirlpool | WEE515SOLS2 |  | apartment | Unit 1303 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16673770347
2024-07-25 10:34 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 774.551.6061 | Owner PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-12 | 2024-06-14 | [5 empty] | When over warming | Whirlpool | WEE515SOLS2 |  | apartment | Unit 1330 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16673782611
2024-07-25 10:37 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 774.551.6061 | Owner PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-13 | 2024-06-14 | [5 empty] | When over warming | Whrilpool | WEE515SOLS2 |  | apartment | unit 1113 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16673800913
2024-07-26 06:38 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 774.551.6061 | owner PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-12 | 2024-06-14 | [5 empty] | while warming oven | Whrilpool | WEE515SOLS2 |  | apartment | Unit 1327 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16678057622
2024-07-26 08:22 | Nicholas | Rafferty | 59205 | 64 W Water St |  | Rockland | MA | 2370 | 6175153999 | Journeyman |  | #HOM250GFICP | Breaker |  | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-19 | 2024-07-15 | 40 Reservior |  | Cambridge | MA | 2138 | The breaker instant trips right after installation. | Wolf | CI365TF/S |  | House | The induction top in kitchen | No | No | No | Yes | https://www.formstack.com/admin/download/file/16678295709 | https://www.formstack.com/admin/download/file/16678295710
2024-07-26 08:32 | Nicholas | Rafferty | 59205 | 64 W Water St |  | Rockland | MA | 2370 | 6175153999 | Journeyman |  | HOM230GFIC | Breaker |  | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-19 | 2024-07-15 | 40 Reservior |  | Cambridge | MA | 2138 | Trips after a minute or two of being on | Wolf | SO3050TM/S/T |  | House | Wall oven in Kitchen | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/16678327837
2024-07-26 09:37 | Nicholas | Rafferty | 59205 | 64 W Water St |  | Rockland | MA | 2370 | 6175153999 | Journeyman |  | HOM230GFIC | Breaker |  | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-19 | 2024-07-15 | 40 Reservior |  | Cambridge | MA | 2138 | Trips after a minute or two of being on | Wolf | SO3050TM/S/T |  | House | Wall oven in Kitchen | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/16678580814
2024-07-26 13:21 | Nicholas | Rafferty | 59205 | 64 W Water St |  | Rockland | MA | 2370 | 6175153999 | Journeyman |  | HOM230GFIC | Breaker |  | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-19 | 2024-07-15 | 40 Reservior |  | Cambridge | MA | 2138 | Trips after a minute or two of being on | Wolf | SO3050TM/S/T |  | House | Wall oven in Kitchen | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/16679782059
2024-07-26 20:08 | Nicholas | Rafferty | 59205 | 64 W Water St |  | Rockland | MA | 2370 | 6175153999 | Journeyman |  | #HOM250GFICP | Breaker |  | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-19 | 2024-07-15 | 40 Reservior |  | Cambridge | MA | 2138 | The breaker instant trips right after installation. | Wolf | CI365TF/S |  | House | The induction top in kitchen | No | No | No | Yes | https://www.formstack.com/admin/download/file/16682528512 | https://www.formstack.com/admin/download/file/16682528513
2024-07-29 11:23 | William | Kellicker | 12197 | 1100 Old Hardwick Road |  | Barre | MA | 1005 | 5082775670 | Owner |  | Siemens Type QPF | Breaker | n/a | 20 |  | 2 Pole | Siemens | Residence |  | 2024-07-26 | 2024-07-15 | 29 Wheeler Road |  | Westborough | MA | 1581 | Installed a 20 amp 2-pole GFCI breaker for a new stove as part of a kitchen renovation. The home owner attempted to turn on the stove and the breaker tripped. They reset the breaker, and the stove preheated for approximately 2 minutes and then the breaker tripped again. | General Electric | JTS5000EN2ES | None | Single family home | Kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/16689342438
2024-07-29 16:04 | John | A Orso | 31977 | 3 West Street |  | Georgetown | MA | 1833 | 978-457-6118 | Owner |  | Siemans QF230AP | Breaker | no | 30 |  | 2 Pole | Siemens | Residence |  | 2024-07-19 | 2024-07-19 | 11 Day Street Unit1 |  | Cambridge | MA | 2138 | Trips immediately. | Samsung | DVE45T6000V | None | Residental Dwelling | New Electric Dryer. | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16691326890
2024-07-29 16:09 | John | A Orso | 31977 | 3 West Street |  | Georgetown | MA | 1833 | 9784576118 | Owner |  | Siemans QF230AP | Breaker | no | 30 |  | 2 Pole | Siemens | Residence |  | 2024-07-19 | 2024-07-19 | 11 Day Street Unit2 |  | Cambridge | MA | 2138 | Trips immediately. | Samsung | DVE45T6000V | no | Residental Dwelling | Electric Dryer. | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16691360462
2024-07-30 15:28 | Robert | Burkett | 14236 | 193 L Street |  | Boston | MA | 2127 | 617-389-2257 | Manager |  | Siemens QF250A | Breaker | None | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-29 | 2024-07-10 | 101 Baldwin St |  | Charlestown | MA | 2127 | Breaker trips when stove is turned on | AGA | AMC48INOYS |  | single family | None, Just the stove circuit | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16696531437
2024-07-31 08:36 | Aramis | Weimann | 59274 | 1 Rocky Brook Dr |  | Huntington | MA | 1050 | +1 (413) 505-9515 | Electrician |  | 4884006004 | Breaker | Square D | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16699475806 | 2024-07-31 | 2024-07-31 | 187 Brickyard Road |  | Southampton | MA | 1073 | Nuisance tripping | Frigidaire | FGEF3042KFB | None | 2-family House | 2nd floor kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16699475820 | https://www.formstack.com/admin/download/file/16699475821
2024-07-31 09:48 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7745516061 | owner PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-29 | 2024-06-14 | [5 empty] | while oven warming | Whirlpool | WEE515SOLS2 |  | apartment | Unit 1232 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16699795589
2024-07-31 09:50 | Ryan | Maloney | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7745516061 | owner PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-29 | 2024-06-14 | [5 empty] | while warming oven | Whirlpool | WEE515SOLS2 |  | apartment | Unit 1331 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16699807227
2024-07-31 11:56 | Eric | Caldon | 21306 | 100 Deanville Ave |  | Attleboro | MA | 2703 | 774-229-6409 | President |  | Cutler Hamer | Breaker | 30 am | 30 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/16700558121 | 2024-07-24 | 2024-07-29 | 14 Berson Rd |  | Seekonk | MA | 1772 | dryer would not turn on - tripped breaker | Electrolux | ELFE7537AW1 | none | laundry room | dryer would not turn on | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16700558135 | https://www.formstack.com/admin/download/file/16700558136
2024-07-31 12:02 | Eric | Caldon | 21306 | 100 Deanville Ave |  | Attleboro | MA | 2703 | 774-229-6409 | President |  | EATON | Breaker | none | 30 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/16700594250 | 2024-07-18 | 2024-02-06 | 2 Berson Rd |  | Seekonk | MA | 1772 | dryer would not turn on | LG | DLE7400WE | none | Laundry room | Dryer would not turn on and tripped the breaker when started | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16700594264 | https://www.formstack.com/admin/download/file/16700594265
2024-07-31 16:09 | jg | jack griffin | 418 | 26 JOANNA DR |  | South Yarmouth | MA | 2664 | 9784792521 | owner |  | siemans 2 pole 50 | Breaker | ? | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-15 | 2024-02-05 | 11 Portsmouth ter. |  | Yarmouth port | MA | 2664 | as i have been experiencing when the oven runs for about 20 minutes the breaker trips. I have been finding this on all the ranges and wall oven problems are due to the oven. | whirlpool | rf262lxsb3 | none | kitchen | oven in kitchen doesn't work. | No | No | No | No |  | https://www.formstack.com/admin/download/file/16702186010
2024-07-31 18:26 | MICHAEL | HALEY | 29364 | 510 REVERE BCH BLVD | # 804 | REVERE | MA | 2151 | 7812646479 | ELECTRICIAN |  | Siemens QFGA2 | Breaker | arc / ground fault breaker | 20 |  | 1 Pole | Siemens | Residence |  | 2024-06-05 | 2024-06-04 | 19 brimmer st unit 5 |  | boston | MA | 2108 | The unit trips a couple of hours after running . | bosc | b36ct80sns | none | residential | Refrigerator . | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/16702921029
2024-08-01 12:22 | Keegan | Kelly | 55736 | 136 squanto rd |  | Quincy | MA | 2169 | 4137702589 | Foreman |  | Qfga2n | Breaker | Tried every breaker they make gfci | 20 | 15 | 1 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16706201222 | 2024-07-01 | 2024-05-24 | 1 nevins hill |  | Brighton | MA | 2135 | Original drawing calls for a combo breaker arc/gfci it will trip. Have also tried all the way up to a 22kva only gfci breaker and it still trips. When plugged into a regular 20 amp single pole or an arc fault only single pole 20 the tripping will stop. Every type of gfci I have tried to use the unit will trip. | Miele | Wxd160 | Dedicated circuits | Condo building | Every condo unit is tripping 55 units total in building everyone has there on laundry room in their unit. Tripping daily. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/16706201236 | https://www.formstack.com/admin/download/file/16706201237
2024-08-01 12:22 | Keegan | Kelly | 55736 | 136 squanto rd |  | Quincy | MA | 2169 | 4137702589 | Foreman |  | Qfga2n | Breaker | Tried every breaker they make gfci | 20 | 15 | 1 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16706202818 | 2024-07-01 | 2024-05-24 | 1 nevins hill |  | Brighton | MA | 2135 | Original drawing calls for a combo breaker arc/gfci it will trip. Have also tried all the way up to a 22kva only gfci breaker and it still trips. When plugged into a regular 20 amp single pole or an arc fault only single pole 20 the tripping will stop. Every type of gfci I have tried to use the unit will trip. | Miele | Wxd160 | Dedicated circuits | Condo building | Every condo unit is tripping 55 units total in building everyone has there on laundry room in their unit. Tripping daily. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/16706202832 | https://www.formstack.com/admin/download/file/16706202833
2024-08-01 14:36 | joe | silverio | 17118 | 32 franklin street |  | lowell | MA | 1844 | 9788514900 | electricvian |  | Eaton THQL2150GFT2P | Breaker | na | 50 |  | 2 Pole | Eaton | Residence |  | 2024-07-25 | 2024-07-18 | unit 78 E parker street |  | acton | MI | 1718 | burners working fine, preheat oven turned on breaker trips immediately | General Electric | RAS200DM2WW |  | kitchen | kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/16707040402
2024-08-01 22:16 | Bryant | Smith | 23214 | 251 Grove Street |  | Norwell | MA | 2061 | 781-291-9360 | Electrician |  | GFTCB230 | Breaker | NA | 30 |  | 2 Pole | Eaton | Residence |  | 2023-11-29 | 2023-11-29 | 121 Tower Ave |  | Marshfield | MA | 2050 | Installed Breaker.¦¦Tested receptacle for voltage with meter. Breaker Holds and trips properly. Turned breaker back on. ¦¦Plug in appliance and breaker trips. ¦¦Checked appliance cord terminations. Verified correct. Plugged Appliance in and breaker trips. | WHIRLPOOL | Wet4024HW | N/A | Single Family Home | Laundry Room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16709098599
2024-08-02 12:03 | Jake | Carlan | 1971 | 895Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Q120DFN | Breaker | AFCI- per inspector fill out report | 20 |  | 1 Pole | Siemens | Residence |  | 2024-07-24 | 2024-07-24 | 13 Joanne Dr Unit 23 |  | Ashland | MA | 1721 | Breaker trips when air fryer is on for 2 minutes, drawing 14 amps. Electrical inspector ok changing AFCI breaker and fill out report | Ninja | AD150 |  | Kitchen | Kitchen dedicated counter outlet | No | No | No | No |  | https://www.formstack.com/admin/download/file/16711297260
2024-08-02 14:29 | Kay | Bernon | 21730 | 38 Woodbridge Rd |  | South Hadley | MA | 1075 | 4136256356 | Administrative Assistant |  | Eaton | Breaker | GFTCB250 |  | 50 | 2 Pole | Eaton | Residence |  | 2024-02-29 | 2024-02-28 | [5 empty] | Turn oven on and within 60 seconds trips breaker.¦Tried 2nd GFI breaker and same thing.¦Installed regular 2P 50 and oven works great. | Whirlpool | KSEG700ESS6 | none | House | Kitchen (Stove) | No | No | No | No |  | https://www.formstack.com/admin/download/file/16712134478
2024-08-02 14:58 | Cindy | Tolan | 21730 | 47 Vernon Street |  | Northampton | MA | 1060 | 917-370-5498 | owner |  | Square D Homeline | Breaker | n/a |  |  | 2 Pole | ABB | Residence |  | 2024-07-20 | 2024-07-01 | [5 empty] | Occasionally Trips even when not in use. | F. Bertazzoni | MAST304INMXE |  | House | Kitchen Oven | No | No | No | No |  | https://www.formstack.com/admin/download/file/16712299275
2024-08-02 15:15 | Palmeri | Electric | 21730 | 5 High St |  | Shelburne Falls | MA | 1370 | 4136256356 | owner |  | BC 30"" Induction | Breaker | n/a |  |  | 2 Pole | Eaton | Residence |  | 2024-07-15 | 2024-07-24 | 5 High St |  | Shelburne Falls | MA | 1370 | circuit breaker (GFCI) 50A would trip soon as range is plugged in | Big Chill | BC 30"" Induction |  | Residential | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16712390368
2024-08-05 13:38 | Josh | Leclair | 88681 | 9 KIDDER RD | Suite C | CHELMSFORD | MA | 01824-3398 | 978-256-4845 | CEO |  | QF250AP | Breaker | n/a | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-05 | 2024-08-05 | 45 Wesley St |  | Lawrence | MA | 1841 | Breaker trips when oven is turned on and passes 200f | Whirlpoolo | MR8700DS1 | NONE | Residential Multi-family | 2nd Floor Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16721152952
2024-08-06 19:01 | Robert | Simon | 2701 | 80 Brown Ave |  | Roslindale | MA | 2131 | 8573123859 | Journeyman |  | T021211118 | Breaker | Ground fault breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-02 | 2024-08-02 | 8 Wachusett Drive |  | Lexington | MA | 2474 | Trips on initial activation. | Frigidaire | FGIC3666TB |  | Single Family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16729836128
2024-08-08 15:17 | Mauricio | Da Silva | 23396 | 24 Hamilton St | #31 | Saugus | MA | 1906 | (781)469-5555 | Owner |  | 11614130 | Breaker | N/A | 15 |  | 1 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16739989800 | 2024-07-19 | 2024-07-19 | 65 E India Row, Unit PHB |  | Boston | MA |  | Washer constantly tripping. | Miele | WXF660 |  | Apartment | Laundry Closet | No | No | Yes | No | https://www.formstack.com/admin/download/file/16739989813 | https://www.formstack.com/admin/download/file/16739989814
2024-08-08 15:43 | Mauricio | Da Silva | 23396 | 24 Hamilton St | #31 | Saugus | MA | 1906 | 7814695555 | Owner |  | Q115DFP | Breaker | N/A | 15 | N/A | 1 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16740149625 | 2024-07-19 | 2024-07-19 | 65 E India Row, Unit PH-B |  | Boston | MA |  | Dryer constantly tripping. | Miele | 11619850 | N/A | Apartment | Laundry closet | No | No | Yes | No | https://www.formstack.com/admin/download/file/16740149647 | https://www.formstack.com/admin/download/file/16740149649
2024-08-09 14:20 | Corey | Hood | 8228 | 16 Sagamore Road |  | Wellesley | MA | 2481 | 7819157358 | Owner |  | GFTCB230 | Breaker | GFCB | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-08 | 2024-08-08 | [5 empty] | New electric oven trips GFCI breaker once oven is pre heated. Replaced breaker and same occured | Thermador | PRD366WHU/07 |  | Single Family Home | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16744604006
2024-08-12 12:38 | Daniel | Murphy | 21565 | 24 Pinecrest Lane |  | Ashland | MA | 1721 | 508-641-6925 | President |  | Siemens / QF250A | Breaker | BR style circuit breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2024-06-05 | 2024-06-03 | 4 Darlene Drive |  | Southborough | MA | 1772 | The oven trips intermittently when connected to the Siemens GFCI breaker. | Frigidaire | GCFE3060BD |  | Single family home | The oven trips intermittently when connected to the Siemens GFCI breaker. | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16753756058
2024-08-13 08:48 | Giombetti | Electric Inc | 13678 | 401 SOUTH STREET | Marlboro | MARLBOROUGH | MA | 1752 | 5084813299 | PRESIDENT |  | THQL2140GFT2 | Breaker | NA | 40 | NA | 2 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/16758098150 | 2024-08-12 | 2024-08-12 | 1610 WORCESTER ROAD APARTMENT 148 |  | FRAMINGHAM | MA | 1702 | WHEN THE STOVE IS TURNED ON THE BREAKER TRIPS | GENERAL ELECTRIC | JB258RT4SS | NA | APARTMENT IN A MULTI FAMILTY BUILDING | KITCHEN STOVE | No | No | No | No | https://www.formstack.com/admin/download/file/16758098164 | https://www.formstack.com/admin/download/file/16758098165
2024-08-13 09:28 | Matt | Broadway | 21540 | 2550 main st |  | Tewksbury | MA | 1876 | 18009774737 | Electrician |  | Siemens type QPF GFCI 50amp 2pole | Breaker | Siemens QP 45amp 2pole | 50 | 45amp | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16758291124 | 2024-08-02 | 2024-07-02 | 14 Purcell dr |  | Chelmsford | MA | 1824 | Was described by homeowner that after installation of range circuit with GFCI protection. Electric stove cooktop would function normal. But oven would be turned on and would trip GFCI breaker within minutes. ¦So, GFCI circuit breaker was removed & standard circuit breaker was installed. | Frigid Aire | FCF13083ASA |  | 1 family home | Kitchen stove | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16758291137 | https://www.formstack.com/admin/download/file/16758291138
2024-08-13 11:39 | Darren | Cyr | 16791 | 19 Mill Street | Mill Street | Auburn | MA | 1501 | 5087551110 | Owner |  | QF250A | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-19 | 2024-07-19 | 92 Worthington Ave |  | Shrewsbury | MA | 1545 | As soon as the oven turns on, it trips. | Whirlpool | GGE388LXS04 |  | Single family | Kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/16759122661
2024-08-13 14:45 | Thai | Nguyen | 22299 | 10 Ashland st |  | Quincy | MA | 2169 | 8573432181 | Electrician/Supervisor |  | Eaton BRN250GF | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-12 | 2024-08-12 | 140 Cherry Brook rd |  | Weston | MA | 2493 | We installed a 4 prongs 50A outlet cause the range came with 4 prongs cord, the GFCI breaker trip as soon we plugged the range in the outlet¦We checked and tested the range circuit and confirmed outlet, breaker and wiring are fine¦We checked range's cord wiring , neutral and ground wires are separated | La Cornue | 110 Induction: C1-I |  | Single family home | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/16760434167
2024-08-14 12:21 | Anthony | Priego | 56729 | 499 walnut st |  | Lynn | MA | 1905 | 6176055264 | Electrician |  | Seimens QPF2 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16766692065 | 2024-08-12 | 2024-08-10 | 91 walker rd |  | Swampscott | MA | 1907 | Breaker trips about 2 minutes into preheating the oven.¦This happens every time preheating is attempted | Frigidaire Range | FCFI3083ASA |  | Single family home | Kitchen electric range circuit | No | Yes | No | No | https://www.formstack.com/admin/download/file/16766692081 | https://www.formstack.com/admin/download/file/16766692082
2024-08-15 08:06 | Robert | Beaulieu | 38953 | 7 Pine Grove RD |  | Westford | MA | 1886 | 6172011874 | Owner |  | Simens | Breaker | Simens | 40 |  | 2 Pole | Siemens | Residence |  | 2024-08-08 | 2024-08-01 | 44 Winslow ST |  | Cambridge | MA | 2138 | When stove is turned on, the circuit breaker will trip shortly thereafter. ¦Wire, breaker and outlet are new. | Frigidaire | FGIF3061NFC |  | Kitchen | Kitchen | No | Yes | No | No | https://www.formstack.com/admin/download/file/16771052949 | https://www.formstack.com/admin/download/file/16771052950
2024-08-15 10:17 | george | martineau | 16808 | 133 congress st |  | lowell | MA | 1852 | 9784596852 | general manager |  | siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-15 | 2024-08-15 | 61 juniper rd |  | andover | MA | 1810 | installed new breaker for oven. customer called next day stated | whirlpool | gr396lx | nothing | single family home | kitchen oven | No | No | No | No |  | https://www.formstack.com/admin/download/file/16771720967
2024-08-15 15:19 | HELEN | WATT | 21730 | 400 BARDSWELL FERRY RD |  | SHELBURNE | MA | 1370 | 413-834-4398 | OWNER |  | GENERAL ELECTRIC | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-15 | 2024-08-15 | 679 C Mohawk Trail |  | Shelburne Falls | MA | 1370 | BREAKER TRIPS WHEN STOVE IS USED | FISHER AND PAYKEL | DR30SCI6XI |  | HOUSE | KITCHEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/16773696949
2024-08-16 11:49 | Emilio | DeAngelis | 16037 | 5 Conn St, Unit G |  | Woburn | MA | 1801 | 7816469250 | Master Electrician |  | QF240A | Breaker | none | 40 |  | 2 Pole | Siemens | Residence |  | 2024-08-13 | 2024-07-31 | 54 Eastern Ave |  | Malden | MA | 2148 | Tripping of the GFCI Breaker occurring when turning on the oven of the Hotpoint stove.¦Happened repeatedly, wiring and terminations were inspected and found in order. | Hotpoint | RAS200DMWW | None | Institutional | (13) Studio apartments | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/16777740350
2024-08-17 12:21 | Douglas | McGovern | 16552 | 3 Elm Place |  | Marlborough | MA | 1752 | 5084815707 | owner |  | qpf 50 2 pole gfi | Breaker | none | 50 | none | 2 Pole | Siemens | Residence |  | 2024-08-15 | 2024-08-14 | 3 Oregon road |  | southboro | MA | 1772 | Turn on oven trips gfci | LG ELECTRIC RANGE | LRE3061ST/00 | NONE | 1 FAMILY HOUSE | KITCHEN RANGE | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16781955964
2024-08-20 11:29 | Christine | Miller | 60582 | 727 Williams st |  | Pittsfield | MA | 1201 | 4134858510 | Electrician |  | HOM240GFI | Breaker | 2pole | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16795610548 | 2024-08-19 | 2024-08-19 | [5 empty] | Breaker tripped when oven was set to bake | Whirlpool | Wfe745h0fs0 | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16795610561 | https://www.formstack.com/admin/download/file/16795610562
2024-08-21 10:10 | brad | patrick | 16808 | 133 congress st |  | lowell | MA | 1852 | 9784596852 | master electrician |  | siemens | Breaker | siemens | 40 |  | 2 Pole | Siemens | Residence |  | 2024-08-21 | 2024-08-16 | 15 carter lane |  | andover | MA | 1810 | oven tripping on new gfci breaker | whirlpool | mw8100x | none | single fam home | oven in kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16801066776
2024-08-21 13:51 | Steve | Daniels | 16467 | 895 Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Siemens | Breaker | Siemens |  |  | 2 Pole | Siemens | Residence |  | 2024-08-20 | 2024-08-20 | 440 North Ave, unit 237 |  | Haverhill | MA | 1830 | Trips when oven is on | GE | JB258DM5BB |  | Apartment | Stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/16802490325
2024-08-22 08:02 | Emily | Berg | 0 | 52 West St |  | Douglas | MA | 1516 | 7164506947 | Homeowner |  | QPF2 | Breaker | None | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16806001365 | 2023-07-29 | 2023-07-29 | [5 empty] | Tripping occurs when using the oven and the pre-heat temperature gets about 200 degrees. Stovetop and fan work as expected. | KitchenAid | KSEG950ESS2 |  | Single Family Home | Kitchen | No | No | Yes | No | https://www.formstack.com/admin/download/file/16806001380 | https://www.formstack.com/admin/download/file/16806001381
2024-08-22 12:53 | William | Peters | 56543 | 43 Franklin Street |  | Peabody | MA | 1960 | 8573125402 | Journey man electrician |  | Lb-250gs | Breaker | Gfci | 50 |  | 2 Pole | Leviton | Residence |  | 2024-08-22 | 2024-08-22 | 2 Dudley at |  | Peabody | MA | 1960 | Breaker trips when oven used | LG | MBM64916763 |  | Kitchen | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16807535656 | https://www.formstack.com/admin/download/file/16807535657
2024-08-26 11:52 | Jesse | Kuhlman | 21804 | 313 Eastern Avenue |  | Lynn | MA | 1902 | 781-544-6447 | Manager |  | Square D, Homeline | Breaker | none | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-22 | 2024-06-17 | 31 Kidder Ave |  | Somerville | MA | 2144 | Breaker trips when oven is turned on. | Fridgidare | FCFI3083ASB |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16822159359
2024-08-26 13:35 | Matt | Elder | 20748 | 40 Bedford Park, Unit 2 |  | Bridgewater | MA | 2324 | 6175933008 | President |  | Tipo-HOM 120/240 volt - AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-21 | 2024-03-25 | 872 Morton Street, Unit 407 |  | Boston | MA |  | Breaker keeps randomly tripping when cooking or warming up stove. | G.E. | JB645RK9SS |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16822834479
2024-08-26 13:42 | Matt | Elder | 2078 | 40 Bedford Park, Unit 2 |  | Bridgewater | MA | 2324 | 6175933008 | President |  | Tipo-HOM 120/240 volt - AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-21 | 2024-03-25 | 872 Morton Street, Unit 405 |  | Boston | MA |  | Breaker keeps randomly tripping when cooking or warming up stove. | G.E. | JB645RK9SS |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16822880638
2024-08-26 14:15 | Matt | Elder | 20748 | 40 Bedford Park, Unit 2 |  | Bridgewater | MA | 2324 | 6175933008 | President |  | Tipo-HOM 120/240 volt - AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-21 | 2024-03-25 | 872 Morton Street, Unit 408 |  | Boston | MA |  | Breaker keeps randomly tripping when cooking or warming up stove. | G.E. | JB645RK9SS |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16823131153
2024-08-26 14:17 | Matt | Elder | 20748 | 40 Bedford Park, Unit 2 |  | Bridgewater | MA | 2324 | 6175933008 | President |  | Tipo-HOM 120/240 volt - AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-21 | 2024-03-25 | 872 Morton Street, Unit 404 |  | Boston | MA |  | Breaker keeps randomly tripping when cooking or warming up stove. | G.E. | JB645RK9SS |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16823147526
2024-08-26 14:20 | Matt | Elder | 20748 | 40 Bedford Park, Unit 2 |  | Bridgewater | MA | 2324 | 6175933008 | President |  | Tipo-HOM 120/240 volt - AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-21 | 2024-03-25 | 872 Morton Street, Unit 403 |  | Boston | MA |  | Breaker keeps randomly tripping when cooking or warming up stove. | G.E. | JB645RK9SS |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16823166289
2024-08-26 14:22 | Matt | Elder | 20748 | 40 Bedford Park, Unit 2 |  | Bridgewater | MA | 2324 | 6175933008 | President |  | Tipo-HOM 120/240 volt - AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-21 | 2024-03-25 | 872 Morton Street, Unit 409 |  | Boston | MA |  | Breaker keeps randomly ripping when cooking or warming up stove. | G.E. | JB645RK9SS |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16823180805
2024-08-26 14:24 | Matt | Elder | 20748 | 40 Bedford Park, Unit 2 |  | Bridgewater | MA | 2324 | 6175933008 | President |  | Tipo-HOM 120/240 volt- AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-21 | 2024-03-25 | 872 Morton Street, Unit 401 |  | Boston | MA |  | Breaker keeps randomly tripping when cooking or warming up stove. | G.E | JB645RK9SS |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16823196437
2024-08-26 14:26 | Matt | Elder | 20748 | 40 Bedford Park, Unit 2 |  | Bridgewater | MA | 2324 | 6175933008 | President |  | Tipo-HOM 120/240 volt - AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-21 | 2024-03-25 | 872 Morton Street, Unit 301 |  | Boston | MA |  | Breaker keeps randomly tripping when cooking or warming up stove. | G.E. | JB645RK9SS |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16823211763
2024-08-26 14:28 | Matt | Elder | 20748 | 40 Bedford Park, Unit 2 |  | Bridgewater | MA | 2324 | 6175933008 | President |  | Tipo-HOM 120/240 volt - AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-21 | 2024-03-25 | 872 Morton Street, Unit 302 |  | Boston | MA |  | Breaker keeps randomly tripping when cooking or warming up stove. | G.E. | JB645RK9SS |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16823224902
2024-08-26 14:31 | Matt | Elder | 20748 | 40 BEDFORD PARK, UNIT 2 |  | Bridgewater | MA | 2324 | 6175933008 | President |  | Tipo-HOM 120/240 volt - AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-05-21 | 2024-03-25 | 872 Morton St, Unit 312 |  | Boston | MA |  | Breaker keeps randomly tripping when cooking or warming up stove. | G.E. | JB645RK9SS |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16823246715
2024-08-26 15:30 | STEPHEN | cappadona | 54255 | 128 essex st |  | marlborough | MA | 1752 | 508 397 0009 | electrician |  | QF250AP | Breaker | outlet | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-26 | 2024-08-26 | 9 WARD RD |  | southborough | MA | 1772 | when the oven was plugged in the breaker tripped immediately. | LG electric stove | LSIL6336FE |  | single family house | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16823643296
2024-08-27 08:55 | David | DeVincentis | 12838 | po box 373 | P.O. Box 373 | Brookline NH 03033 | NH | 3033 | 9789732637 | Owner |  | GFTCB220 | Breaker | n/a | 20 | N/A | 2 Pole | Eaton | Residence |  | 2024-08-02 | 2024-08-01 | 2 Worthen Pl |  | Andover | MA |  | The air blower will run for couple minutes and then trip, reset GFCI breaker and unit will do same, contacted manufacturer and was told this unit does not require a GFI it s double insulated and will continue to trip | Air supply of the future, INC. | 2HP/220v/6A | none | Swimming pool | Swimming pool air blower for hot tub | No | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/16826986928 | https://www.formstack.com/admin/download/file/16826986929
2024-08-27 09:18 | David | DeVincentis | 12838 | PO Box 373 |  | Brookline | NH | 3033 | 9789732637 | Owner |  | GFTCB220 | Breaker | N/A | 20 | N/A | 2 Pole | Eaton | Residence |  | 2024-08-02 | 2024-08-01 | 2 Worthern PL |  | Andover | MA |  | GFI breaker for Hot tub blower¦When init is turned on it will run for minute and trip GFI breaker, when reset it will do the same, contacted manufacturer and was told Air blower does not go on GFI it is double insulated and not required and will keep nuisance tripping | Air supply of the future, LLC | AB2HP2206A | None | Swimming pool | Swimming pool Hot tub air blower | No | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/16827085244 | https://www.formstack.com/admin/download/file/16827085245
2024-08-27 09:34 | David | DeVincentis | 12838 | po box 373 | P.O. Box 373 | Brookline NH 03033 | NH | 3033 | 9789732637 | owner |  | GFTCB250 | Breaker | none | 50 | N/A | 2 Pole | Eaton | Residence |  | 2024-08-02 | 2024-08-01 | 2 Worthern PL |  | Andover | MA |  | This is a dual fuel pool heater, both Gas and Electric¦When running in the Electric mode it continually trips the GFCI breaker | Pentair | Ultratemp ETI Hybrid Heater 460969 | none | Swimming pool | Heat pump dual fuel heater for swimming pool | No | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/16827164110
2024-08-27 11:39 | Michael | Perkins | 14342 | p.o. box 142, main st |  | Millis | MA | 2054 | 5084290815 | PRESIDENT |  | SIEMENS QF250AP | Breaker | NONE | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-20 | 2024-08-20 | 10 APPLEGROVE LN |  | CARLISLE | MA | 1741 | OVEN TRIPS THE GFI BREAKER THE MOMENT YOU PLUG IT IN | WOLF | IR36550/S/T | NONE | SINGLE FAMILY | KITCHEN | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16827952772
2024-08-27 11:44 | Michael | Perkins | 14132 | p.o. box 142, main st |  | Millis | MA | 2054 | 5084290815 | PRISEDENT |  | QF250AP | Breaker | NONE | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-22 | 2024-08-22 | 78 WESTGATE RD |  | WELLESLEY | MA | 2481 | APPLIANCE TRIPS APON PLUGGING IT IN | WOLF | IR30450/S/T | NONE | SINGLE FAMILY | KITCHEN | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16827984779
2024-08-27 12:18 | Josh | Leclair | 22548 | 9 KIDDER RD | Suite C | CHELMSFORD | MA | 01824-3398 | 9782564845 | Master Electrician |  | QF250AP | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16828215703 | 2024-08-27 | 2024-08-27 | 31 Harding St |  | Chelmsford | MA | 1863 | GFCI Breaker trips instantly upon plugging in range. Standard breaker holds without incident. | Whirlpool | MER4800PZO | None | Single Family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16828215717 | https://www.formstack.com/admin/download/file/16828215718
2024-08-28 10:27 | Mark | Flores | 52255 | 97 Groveland Ave |  | South Weymouth | MA | 2190 | 7816643215 | President |  | Eaton BRN230GFCS | Breaker | other | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-28 | 2024-08-28 | 17 Mordecai Lincoln Rd |  | Scituate | MA | 2066 | Breaker would Randomly trip off during running | Thermador | MC30WP/01 | none | Single Family Dwelling | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16833347682 | https://www.formstack.com/admin/download/file/16833347683
2024-08-28 13:25 | Steve | Daniels | 16467 | 895Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Square D | Breaker | Breaker |  |  | 2 Pole | Eaton | Residence |  | 2024-08-27 | 2024-08-27 | 2 School House Road |  | Gloucester | MA | 1930 | Contiuous tripping with oven | GE | JB645RK6SS |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16834477182
2024-08-28 16:52 | Sally | Poveromo | 34387 | 349 Commonwealth Ave |  | Boston | MA | 2115 | 6178991212 | Home owner |  | Thermador ME301YP Wall Oven and CIT304YB Cook Top | Breaker | Breaker | 50 | 30 | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16835781347 | 2024-08-28 | 2024-08-28 | [5 empty] | When turning on the cook top and oven, the breaker trips. | Thermador | Thermador ME301YP Wall Oven and CIT304YB Cook Top |  | Residential | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16835781359
2024-08-29 05:51 | Michael | Tobio | 27470 | 119 Waverley St |  | Belmont | MA | 2478 | 617 866 2391 | Journeyman |  | Siemens QF250AP | Breaker | 240V | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-28 | 2024-08-29 | 36 Prince St |  | Boston Jamaica Plain | MA | 2130 | GFCI breaker described was installed as required but doesn't work on the equipment in which it is connected to.¦The equipment is described by the manufacturer as ""GFCI incompatible"" | WOLF | C1365T/S |  | Residential dwelling unit | Wolf induction coocktop in the kitchen | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/16837840211 | https://www.formstack.com/admin/download/file/16837840212
2024-08-29 12:11 | Daniels | Electric | 16467 | 895 Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | HOM2P50GFCI | Breaker | n/a | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-01 | 2024-08-01 | 2 Schoolhouse Rd |  | Gloucester | MA | 1930 | Tripping while heating or cleaning | GE | JRS3000SN1SS |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16839450252
2024-08-29 12:14 | Daniels | Electric | 16467 | 895 Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | EatonGFCB | Breaker | n/a | 50 |  | 2 Pole | Eaton | Residence |  | 2024-07-02 | 2024-08-02 | 3 boston way unit 401 |  | newburyport | MA | 1950 | tripping while heating ¦ | GE | JB645ER9ES |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16839470714
2024-08-29 20:00 | Steven | Doherty | 21370 | PO Box 177 |  | Sturbridge, MA | MA | 1566 | 5083661119 | Owner/Operator |  | Square D Homeline/ HOM240GFCI | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-20 | 2024-08-20 | 5 Chiltern Hill Dr N |  | Worcester | MA | 1609 | Breaker immediately trips when the oven turns on | Bosch | HII8057U/02 | NONE | Kitchen | Unit in kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16841915484 | https://www.formstack.com/admin/download/file/16841915485
2024-08-30 02:59 | Michael | Tobio | 27470 | 119 Waverley St |  | Belmont | MA | 2478 | 617 866 2391 | Journeyman |  | Siemens QF250AP | Breaker | 240V | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-28 | 2024-08-29 | 36 Prince St |  | Boston Jamaica Plain | MA | 2130 | GFCI breaker described was installed as required but doesn't work on the equipment in which it is connected to.¦The equipment is described by the manufacturer as ""GFCI incompatible"" | WOLF | C1365T/S |  | Residential dwelling unit | Wolf induction coocktop in the kitchen | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/16842803202 | https://www.formstack.com/admin/download/file/16842803203
2024-08-30 12:31 | Jake | Carlan | 1971 | 895 Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | L1812221047 | Breaker | na | 40 |  | 2 Pole | Siemens | Residence |  | 2024-08-28 | 2024-08-28 | 23 Victor unit 1 |  | Haverhill | MA | 1832 | Trips when stove reaches baking temp | GE | JB258DM1BB |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16844609289
2024-09-03 12:48 | CHRISTOPHER | CLAPP | 15946 | PO BOX 213 |  | Hanover | MA | 2339 | 6175928508 | Owner |  | Cutler Hammer | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2024-09-03 | 2024-08-05 | 2 Feeley Ln |  | Hingham | MA | 2043 | New Wolf 48"" Duel Fuel oven/cooktop tripping when using the oven | Wolf | conappwm | 0 | Kitchen | Kitchen | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/16857193732
2024-09-04 19:08 | Alfredo | Cedrone | 11556 | 13 Chapel St. |  | Newton | MA | 2458 | 6172449675 | Owner |  | Seimens Q230GF | Breaker | 2 pole 30 amp | 30 |  | 2 Pole | Siemens | Residence |  | 2024-09-04 | 2024-09-04 | 69 Trapelo Rd. |  | Waltham | MA | 2454 | Breaker will not reset for dual fuel stove | Whirlpool | KSDB900ESS3 | NONE | Single family house | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16866111995 | https://www.formstack.com/admin/download/file/16866111996
2024-09-05 14:51 | Keith | Whittaker | 2810 | 14 nottingham Dr |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BR250 | Breaker | GFCI Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-16 | 2024-06-05 | 282 bremen st |  | Boston | MA | 2128 | trips while heating up | GE | JS645SL9SS |  | kitchen | this breaker serves the oven in the kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16870569040
2024-09-05 22:00 | GUSTAVO | SILVA | 14788 | 53 TEMI RD |  | HOLLISTON | MA | 1746 | 5087402698 | PRESIDENT |  | EATON/GFTCB250CS | Breaker | CLASSIFIED | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-01 | 2024-08-01 | [5 empty] | WONT HOLD 15 SECONDS | KITCHE AID | KODE500ESS04 |  | SINGLE FAMILY | JUST THE KITCHJEN OVEN | Yes | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/16872688836
2024-09-06 08:37 | Sam | Ostrow | 16992 | 9 Mason Street |  | WORCESTER | MA | 1609 | 5087542641 | Vice President |  | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/16873923066 | 2024-09-02 | 2024-05-01 | 280 Western Ave |  | Allston | MA | 2134 | When the oven and range are turned on the GFCI trips. | Whirlpool | W11027385BLK | None | Apartment | 33 apartment units in a new building have the identical oven and breaker setup. | No | No | No | No | https://www.formstack.com/admin/download/file/16873923080 | https://www.formstack.com/admin/download/file/16873923081
2024-09-06 10:16 | DAVID | DEGRAZIA | 17119 | P.O. BOX 299 |  | E. FREETOWN | MA | 2717 | 585420179 | MASTER ELECTRICIAN |  | GE ELECTRIC DRYER COMBO | Breaker | NA | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-19 | 2024-07-31 | 17 BRIDLE PATH RD |  | BREWSTER | MA | 2631 | WHEN APPLIANCE IS TURNED ON BREAKER TRIPS SHORTLY THEREAFTER | GE ELECTRIC DRYER COMBO | DRYER COMBO | NA | SINGLE FAMILY | LAUNDRY ROOM | No | No | No | No |  | https://www.formstack.com/admin/download/file/16874389561
2024-09-06 10:40 | Mark | Roussel | 21100 | 33 old forge Ln |  | Sudbury | MA | 1776 | 9784438888 | Owner |  | GE Model # THQL1120DFP | Breaker | Breaker | 20 |  | 1 Pole | ABB | Residence |  | 2024-09-06 | 2024-09-06 | 51 Normandy Rd |  | Sudbury | MA | 1776 | The circuit breaker works fine if just the display clock and the internal light is in use ---- At the instant you start the microwave up the circuit breaker opens | Bosch | HMC54151UC/07 | nothing | Residential | Kitchen | No | Yes | Yes | No | https://www.formstack.com/admin/download/file/16874527831 | https://www.formstack.com/admin/download/file/16874527832
2024-09-06 11:34 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN250GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | boston | MA | 2128 | tripping while oven is heating up | General Electric | JS645SL9SS | none | Appartment | The oven in the kitchen is tripping the breaker | No | No | No | No |  | https://www.formstack.com/admin/download/file/16874851655
2024-09-06 11:41 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN250GF | Breaker | Oven | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 bremen st |  | Boston | MA | 2128 | The Oven trips while heating up | General Electric | JAS640RM4SS | none | Appartment | The oven it tripping in the Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16874892621
2024-09-06 11:45 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen St |  | Boston | MA | 2128 | While the dryer is running it randomly trips off | General Electric | GFT14ESSM3WW | none | Apartment 217 | The dryer that trips is in the laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16874921304
2024-09-06 11:57 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN250GF | Breaker | Oven | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 bremen st |  | Boston | MA | 2128 | The oven trips while heating up | General Electric | JS645SL9SS | none | Apartment 218 | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16874989538
2024-09-06 12:08 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 bremen st |  | Boston | MA | 2128 | Dryer trips mid cycle while drying | General Electric | GFT14ESSM3WW |  | Apartment 218 | Laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16875065400
2024-09-06 12:13 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 bremen st |  | Boston | MA | 2128 | The dryer trips mid cycle while drying | General Electric | GFT14ESSM3WW |  | Apartment 233 | Laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16875095801
2024-09-06 12:19 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN259GF | Breaker | Range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 bremen st |  | Boston | MA | 2128 | Range trips while the oven is heating | General Electric | JS645SL9SS | none | Apartment 238 | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16875136258
2024-09-06 12:22 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 bremen st |  | Boston | MA | 2128 | The dryer keeps tripping mid cycle | General Electric | GFT14ESSM3WW |  | Apartment 238 | Laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16875158088
2024-09-06 12:31 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 bremen st |  | Boston | MA | 2128 | The dryer trips mid cycle while drying | General Electric | GFT14ESSM1WW |  | Apartment 301 | Laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16875209747
2024-09-06 13:11 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250GF | Breaker | Range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 bremen st |  | Boston | NH | 2128 | The range trips while heating up the oven | General Electric | JS645SL9SS |  | Apartment 307 | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16875456498
2024-09-06 13:21 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN250GF | Breaker | GFCI | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 bremen st |  | Boston | MA | 2128 | The oven trips while heating up | General Electric | JS645SL9SS |  | Apartment 308 | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16875514827
2024-09-06 13:27 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250GF | Breaker | GFCI | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 bremen st |  | Boston | MA | 2128 | Oven trips while heating up | General Electric | JAS640RM4SS |  | Apartment 311 | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16875550665
2024-09-06 13:33 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 781.701.0028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | apartment | 1300 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16875588672
2024-09-06 13:38 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250GF | Breaker | GFCI | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 bremen st |  | Boston | MA | 2128 | The oven trips while heating up | General Electric | JASG4ORMASS |  | Apartment 312 | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16875617493
2024-09-06 13:38 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-23 | 2024-06-14 | 1325 Washington Street |  |  |  |  | while warming oven | Whirlpool | WEE515SOLS2 |  | apartment | 1117 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16875619652
2024-09-06 13:39 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-23 | 2024-06-14 | 1325 Washington Street |  |  |  |  | while warming oven | Whirlpool | WEE515SOLS2 |  | apartment | 1117 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16875622180
2024-09-06 13:41 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-31 | 2024-06-14 | 1325 Washington Street |  |  |  |  | while warming oven | Whirlpool | WEE515SOLS2 |  | apartment | 1128 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16875634608
2024-09-06 13:42 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250GF | Breaker | GFCI | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 bremen st |  | Boston | MA | 2128 | The oven trips while heating up | General Electric | JAS640RM4SS |  | Apartment 314 | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16875639674
2024-09-06 13:43 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-01 | 2024-06-14 | 1325 Washington Street |  |  |  |  | while warming oven | Whirlpool | WEE515SOLS2 |  | apartment | 1408 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16875645502
2024-09-06 13:46 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-31 | 2024-06-14 | 1325 Washington Street |  |  |  |  | while warming oven | Whirlpool | WEE515SOLS2 |  | apartment | 1412 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16875665382
2024-09-06 13:48 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-23 | 2024-06-14 | 1325 Washington Street |  |  |  |  | while warming oven | Whirlpool | WEE515SOLS2 |  | apartment | 1210 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16875677513
2024-09-06 13:50 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250GF | Breaker | GFCI | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 bremen st |  | Boston | MA | 2128 | The oven trips while heating up | General Electric | KAS640RM4SS |  | Apartment 321 | The Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16875689517
2024-09-06 13:50 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | PM |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-08-20 | 2024-06-14 | 1325 Washington Street |  |  |  |  | while warming oven | Whirlpool | WEE515SOLS2 |  | apartment | 1208 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16875690419
2024-09-06 14:16 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230GF | Breaker | GFCI | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | The dryer trips while heating up | General Electrical | GFW148SSM1WW |  | Apartment 322 | The Laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16875843452
2024-09-06 14:21 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250GF | Breaker | GFCI | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | The oven trips the breaker while heating up | General Electric | JS645SL9SS |  | Apartment 324 | The Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16875872662
2024-09-09 14:00 | DAVID | LEWIS | 22693 | 27 RYLER COURT |  | NORTH GROSVENORDALE | CT | 6255 | 7742309515 | OWNER |  | ETN GFTCB250 | Breaker | GFCB-HAGF | 50 |  | 2 Pole | Eaton | Residence |  | 2024-06-12 | 2023-11-08 | 96 PARK RD |  | CHARLTON | MA |  | HOMEOWNER WOULD WAKE UP TO RANGE OFF | GE | PHS930YPAFS |  | SINGLE FAMILY | COOKING EQUIPMENT | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/16885909016
2024-09-09 14:09 | DAVID | LEWIS | 22693 | 27 RYLER COURT |  | NORTH GROSVENORDALE | CT | 6255 | 7742309515 | OWNER |  | ETN GFTB250 | Breaker | GFCB-HAGF | 50 |  | 2 Pole | Eaton | Residence |  | 2024-09-09 | 2023-12-08 | 9 WESTWOOD RD |  | WEBSTER | MA | 1570 | BROILER SETTING ¦PREHEAT SETTING | GE | J BP65D M2WW |  | SINGLE FAMILY | COOKING EQUIPMENT | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/16885969354
2024-09-09 16:49 | Tony | Marroquin | 14426 | 52 Chamberlain |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB230 | Breaker | none | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-26 | 2024-07-15 | [5 empty] | Built in Wall oven tripping with normal use. | JennAir | JJW3430LL |  | Single Family | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/16887073024
2024-09-09 16:52 | Tony | Marroquin | 14426 | 22 Whalen Rd |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB230 | Breaker | none | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-26 | 2024-07-15 | [5 empty] | built in wall oven trips with normal use. | Jennair | JJW3430LL | none | Single Family | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/16887088651
2024-09-09 16:55 | Tony | Marroquin | 14426 | 48 Chamberlain |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB230 | Breaker | None | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-26 | 2024-07-15 | [5 empty] | Built in wall oven trips with normal use. | KitchenAid | KOSE500ESS |  | Single Family | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/16887110065
2024-09-09 18:20 | Thien | Nguyen | 56980 | 14 Dewey Ave |  | woburn | MA | 1801 | 6178333708 | Electrician |  | Eaton BR GFCI circuit breaker / BRN240GF | Breaker | Eaton BR GFCI circuit breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2024-05-02 | 2024-04-15 | 562 Massachusetts Ave |  | Boston | MA | 2118 | According to the homeowner it just randomly trip. I went back to check the wiring and replaced the breaker twice and it still happen. | Cafe | CHS950P2MS1 |  | Kitchen | Unit 1 in basement. As soon as walk in the kitchen right there. | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/16887570121
2024-09-10 12:14 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250GF | Breaker | Range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-22 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Breaker Keeps tripping intermittently while range is running | General Electric | JAS640RM4SS | none | Apartment 327 | The Kitchen is where the range is located | No | No | No | No |  | https://www.formstack.com/admin/download/file/16891161880
2024-09-10 12:20 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-22 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | The Dryer breaker trips intermittently while running | General Electric | GFT14ESSM3WW |  | Apartment 327 | The Laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16891199040
2024-09-10 12:24 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250GF | Breaker | Range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-22 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | The breaker trips intermittently while the range is running | General Electric | JS645SL9SS | none | Apartment 333 | The Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16891227660
2024-09-10 12:34 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250GF | Breaker | Range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-22 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | The breaker trips intermittently while the range is running | General Electric | JS645SL9SS | None | Apartment 336 | The Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16891294253
2024-09-10 12:54 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250GF | Breaker | Range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-22 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | The Range trips the breaker intermittently. | General Electric | JS645SL9SS | None | Apartment 338 | The Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16891429150
2024-09-10 12:58 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-22 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | The breaker trips intermittently while the dryer is running | General Electric | GFT14ESSM3WW | None | Apartment 338 | The Laundry Room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16891460651
2024-09-10 14:33 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-22 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | The breaker trips intermittently while the dryer is running | General Electric | GFT14ESSM1WW | none | Apartment 407 | The Laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16892106901
2024-09-11 10:23 | Robert | Dean | 21730 | 110 Elm Street |  | Shelburne Falls | MA | 1370 | 4136256404 | Electrician |  | Eaton GFTCB250 | Breaker | 2 Pole | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-06 | 2024-08-05 | [5 empty] | trips while using occasionally | Frigidaire | GCF13060BF |  | Residential | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16896260606
2024-09-12 07:23 | Keith | Whittaker | 2810 | 16 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | Brn230gf | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Breaker trips intermittently while operating | General electric | Gft14essm1ww | None | Apartment 407 | The laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16901265870
2024-09-12 07:29 | Keith | Whittaker | 2810 | 16 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | Gfn230 | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen |  | Boston | MA | 2128 | Breaker trips intermittently while running | General electric | Gft14essm3ww | None | Apartment 410 | Laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/16901281110
2024-09-12 07:34 | Keith | Whittaker | 2810 | 16 perimeter rd |  | Nashua | NH | 3062 | 3068804601 | Project manager |  | Bren250gf | Breaker | Range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Breaker trips intermittently while running | General electric | Js645sl9ss | None | Apartment 410 | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16901294505
2024-09-12 14:46 | Mark | Roussel | 21100 | 33 old forge Ln |  | Sudbury | MA | 1776 | 978 443 8888 | owner |  | GE THQL dual function breaker | Breaker | Breaker | 40 |  | 2 Pole | ABB | Residence |  | 2024-09-12 | 2024-09-12 | 8 Glen Ln |  | Sudbury | MA | 1776 | Breaker trips immediately upon turning unit on | Bosch cooktop | NIT8660UC | none | kitchen | kitchen cooking equipment | No | No | Yes | No | https://www.formstack.com/admin/download/file/16903710549 | https://www.formstack.com/admin/download/file/16903710550
2024-09-12 15:00 | Mark | Roussel | 21100 | 33, Old Forge Lane | Old Forge Lane | Sudbury | MA | 1776 | 978 443 8888 | owner |  | ABB THQL 40amp 2 pole breaker | Breaker | Breaker | 40 |  | 2 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/16903798614 | 2024-09-12 | 2024-09-12 | 15 Moore Rd |  | Sudbury | MA | 1776 | When the connected unit is turned on the circuit immediately trips | Bosch | NIT8660UC | NONE | Kitchen ,single family residence | none | No | No | Yes | No | https://www.formstack.com/admin/download/file/16903798628 | https://www.formstack.com/admin/download/file/16903798629
2024-09-12 15:04 | Mark | Roussel | 21100 | 33, Old Forge Lane | Old Forge Lane | Sudbury | MA | 1776 | 978 443 8888 | owner |  | GE 40 amp THQL 2 pole GFCI breaker | Breaker | breaker | 40 |  | 2 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/16903829825 | 2024-09-12 | 2024-09-12 | 15 Moore Rd |  | Sudbury | MA | 1776 | When the connected unit is turned on the circuit immediately trips | Bosch Oven | HBL8753UC/05 | none | Kitchen in a residential home | none | No | No | Yes | No | https://www.formstack.com/admin/download/file/16903829839 | https://www.formstack.com/admin/download/file/16903829840
2024-09-12 17:51 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-03 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 | . | apartment | 1214 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16904784648
2024-09-12 17:52 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-03 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 | . | apartment | 1214 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16904786218
2024-09-12 18:02 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-08-23 | 2024-06-14 | 2024-06-14 |  | 1325 Washington Street | MA | 2189 | while oven is warming | Whirlpool | WEE515SOLS2 | . | apartment | 1402 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16904831185
2024-09-12 20:21 | Jack | NEMENSKY | 11039 | 61 edgewood rd, Southborough, MA | JUNIPER CIR | Southborough | MA | 1772 | 508-208-6015 | electrical contractor |  | siemens type QPF | Breaker | 2 pole GFCI breaker | 60 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16905348027 | 2024-09-05 | 2024-09-05 | 4, JUNIPER CIR |  | WESTBOROUGH | MA | 1581 | Nuisance tripping of GFCI breaker for stove.¦Standard breaker, i.e., none GFCI breaker, has no issues. | samsung | NJE59K3310SS/AA | none | single family | kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/16905348041 | https://www.formstack.com/admin/download/file/16905348042
2024-09-12 20:43 | Steve | Laurencio | 18079 | 15 Cote Hill Rd. |  | Bedford | MA | 1730 | 978 621-7221 | Owner |  | BRN230GFCS | Breaker | 0 | 30 |  | 2 Pole | Eaton | Residence |  | 2024-09-12 | 2024-09-12 | [5 empty] | Circuit breaker tripped when stove is turned On. | Wolf Appliance | C130460T/S | no | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16905419695
2024-09-12 21:09 | Steve | Laurencio | 18079 | 30 Plain Rd |  | Wayland | MA | 1778 | 978 621-7221 | Electrician |  | Siemens Q120DFP | Breaker | . | 20 |  | 1 Pole | Siemens | Residence |  | 2024-09-12 | 2024-09-12 | [5 empty] | Circuit breaker trips a couple of times a day. | Thermador | T36FT820NS/04 |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16905500942
2024-09-12 21:20 | Steve | Laurencio | 18079 | 30 Plain Rd |  | Wayland | MA | 1778 | 978 621-7221 | Electrician |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-02 | 2024-09-02 | [5 empty] | Circuit breaker tripped when stove is turned On. | Bosch | HIS8655U |  | Single Family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16905530808
2024-09-12 21:27 | Steve | Laurencio | 18079 | 4 Upland Rd. |  | Andover | MA | 1886 | 978 621-7221 | Electrician |  | Siemens Q120DF | Breaker | . | 20 |  | 1 Pole | Siemens | Residence |  | 2024-09-02 | 2024-09-02 | [5 empty] | Circuit breaker trips a couple of times a day. | Sub ZERO | DET3650CIR |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16905553710
2024-09-12 21:33 | Steve | Laurencio | 18079 | 4 Upland Rd. |  | Andover | MA | 1886 | 978 621-7221 | Electrician |  | Siemens Q120DF | Breaker | . | 20 |  | 1 Pole | Siemens | Residence |  | 2024-09-02 | 2024-09-02 | [5 empty] | Circuit breaker trips on spin cycle. | Miele | WXD160 | no | Single family | Laundry closet. | No | No | No | No |  | https://www.formstack.com/admin/download/file/16905570831
2024-09-12 21:45 | Steve | Laurencio | 18079 | 4 Upland Rd. |  | Andover | MA | 1886 | 978 621-7221 | Electrician |  | Siemens Q120DF | Breaker | . | 20 |  | 1 Pole | Siemens | Residence |  | 2024-09-02 | 2024-09-02 | [5 empty] | Circuit breaker trips at the end of drying cycle. | Miele | TXD160WP |  | Single Family | Laundry closet. | No | No | No | No |  | https://www.formstack.com/admin/download/file/16905608944
2024-09-13 07:23 | jg | jack griffin | 418 | 26 JOANNA DR |  | South Yarmouth | MA | 2664 | 9784792521 | owner |  | siemans 2 pole 20 | Breaker | siemens 2 pole 20 | 20 |  | 2 Pole | Siemens | Residence |  | 2024-09-11 | 2024-06-29 | 269 Seapuit rd. |  | cotuit | MA |  | breaker trips when unit starts the fan. | intertek | hf5840tc | none | garage | garage unit heater | No | No | No | No |  | https://www.formstack.com/admin/download/file/16906657711
2024-09-15 11:26 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2076 | 508-297-7700 | Foreman |  | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-11 | 2024-08-13 | 660 Main St. |  | Worcester | MA |  | Apt 411 ¦sn hz917954r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | GE | RAS240DM2WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16914080945
2024-09-15 11:29 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2076 | 508-297-0070 | Foreman |  | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-11 | 2024-08-06 | 660 Main St. |  | Worcester | MA |  | Apt 413 ¦sn hz915726R¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16914087351
2024-09-15 11:34 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2076 | 508-297-0070 | Foreman |  | hom240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-11 | 2024-08-06 | 660 Main St. |  | Worcester | MA |  | Apt 415¦sn hz915689r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16914097292
2024-09-15 11:37 | Sean | Matthies | 3671 | 1667 Central St. |  | West Bridgewater | MA | 2072 | 508-297-0070 | Foreman |  | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-10 | 2024-08-13 | 660 Main St. |  | Worcester | MA |  | Apt 111 ¦sn hz915671R¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | RAS240DM2WW | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16914102851
2024-09-15 11:40 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | hom240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-10 | 2024-08-01 | 660 Main St. |  | Worcester | MA |  | Apt 113¦sn hz915713r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16914108551
2024-09-15 11:42 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-10 | 2024-08-01 | 660 Main St. |  | Worcester | MA |  | Apt 115 ¦sn hz915698r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | RAS240DM2WW | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16914112793
2024-09-15 11:44 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-10 | 2024-08-13 | 660 Main St. |  | Worcester | MA |  | Apt 211 ¦sn hz917877r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16914117889
2024-09-15 11:46 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | home240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-10 | 2024-08-01 | 660 Main St. |  | Worcester | MA |  | Apt 213 ¦sn hz917884r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | Apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16914122008
2024-09-15 11:49 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-10 | 2024-08-05 | 660 Main St. |  | Worcester | MA |  | Apt 215 ¦sn hz915628r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16914127253
2024-09-15 11:51 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-11 | 2024-08-13 | 660 Main St. |  | Worcester | MA |  | Apt 311 ¦sn hz917886r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16914132024
2024-09-15 11:54 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-11 | 2024-08-05 | 660 Main St. |  | Worcester | MA |  | Apt 313¦sn hz915687r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16914136422
2024-09-15 11:56 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-11 | 2024-08-05 | 660 Main St |  | Worcester | MA |  | Apt 315¦sn hz915709r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16914140623
2024-09-15 21:40 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-10 | 2024-08-13 | 660 Main St. |  | Worcester | MA |  | Apt 511 ¦sn hz915733r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16915576779
2024-09-15 21:42 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-10 | 2024-08-06 | 660 Main St. |  | Worcester | MA |  | Apt 513 ¦sn hz915727r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16915581228
2024-09-15 21:44 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-10 | 2024-08-07 | 660 Main St. |  | Worcester | MA |  | Apt 515 ¦sn hz915679r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16915586292
2024-09-15 21:47 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-11 | 2024-08-13 | 660 Main St. |  | Worcester | MA |  | Apt 611 ¦sn hz917958r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16915592769
2024-09-15 21:50 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-11 | 2024-08-07 | 660 Main St. |  | Worcester | MA |  | Apt 613 ¦sn hz917401r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | Apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16915598041
2024-09-15 21:52 | Sean | Matthies | 3671 | 1667 Central St. |  | Stoughton | MA | 2072 | 508-297-0070 | Foreman |  | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-11 | 2024-08-07 | 660 Main St. |  | Worcester | MA |  | Apt 615¦sn hz917896r¦Oven portion cannot be used without tripping the breaker. Have contacted GE before they have stated it is an issued with stove and they cannot fix it. | ge | ras240dm2ww | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16915603476
2024-09-16 08:45 | Michael | Hughes | 18156 | 1152 Main St |  | Reading | MA | 1867 | 7817109912 | Master Electrician/Owner |  | BRN120DF | Breaker | N/A | 20 |  | 1 Pole | Eaton | Residence |  | 2024-09-06 | 2024-08-17 | 69 Temple St |  | Reading | MA | 1867 | Multiple Nuisance Trips | Kitchen Aid | KRSC703HPS04 | None Dedicated Circuit | Single Family Kitchen | Dedicated Circuit to the Kitchens Refrigerator | No | Yes | No | Yes |  | https://www.formstack.com/admin/download/file/16916872641
2024-09-16 10:10 | Michael | Hughes | 18156 | 1152 Main St |  | Reading | MA | 1867 | 7817109912 | Master Electrician/Owner |  | QF250A | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2024-07-18 | 2022-10-28 | 9 Churchill Dr |  | Falmouth | MA | 2536 | Tripping when broiling or when the oven reaches over 425 degrees. Replaced breaker 4 times and still tripping. | Frigidaire | FFEH3054USD | None dedicated circuit | Single Family | Kitchen, dedicated circuit to oven. | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/16917326715
2024-09-16 10:59 | Michael | Hughes | 18156 | 1152 Main St |  | Reading | MA | 1867 | 7817109912 | Master Electrician/Owner |  | THQL2150GFT2 | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2024-06-25 | 2024-03-18 | 60 Main St |  | Wakefeild | MA | 1880 | Stove nuisance tripping. Replaced breaker twice. | Frigidaire | GEF13060BFA | None dedicated circuit | Single Family | Kitchen, dedicated circuit to the stove. | No | Yes | No | Yes |  | https://www.formstack.com/admin/download/file/16917658276
2024-09-17 08:32 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen St |  | Boston | MA | 2128 | Intermittent NuisanceG Tripping | General Electric | GFT14ESSM3WW | none | Unit 216 | Laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16922777545
2024-09-17 08:36 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen St |  | Boston | MA | 2128 | Intermittent NuisanceG Tripping | General Electric | GFT14ESSM3WW | none | Unit 216 | Laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16922792572
2024-09-17 08:52 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250 GF | Breaker | Range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent Nuisance Tripping | General Electric | JS645SL9SS | none | Unit 233 | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16922867876
2024-09-17 09:06 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250 GF | Breaker | Range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent Nuisance Tripping | General Electric | JS645SL9SS |  | Unit 301 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16922936082
2024-09-17 09:06 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250 GF | Breaker | Range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent Nuisance Tripping | General Electric | JS645SL9SS |  | Unit 301 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16922939626
2024-09-17 09:07 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250 GF | Breaker | Range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent Nuisance Tripping | General Electric | JS645SL9SS |  | Unit 301 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16922942149
2024-09-17 09:07 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250 GF | Breaker | Range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent Nuisance Tripping | General Electric | JS645SL9SS |  | Unit 301 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16922943637
2024-09-17 09:25 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent Nuisance Tripping | General Electric | GFT14ESSM1WW | none | Unit 307 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923035701
2024-09-17 09:25 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent Nuisance Tripping | General Electric | GFT14ESSM1WW | none | Unit 307 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923039115
2024-09-17 09:31 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent Nuisance tripping | General Electric | GFT14ESSM1WW | none | unit 308 | Laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923069670
2024-09-17 09:32 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent Nuisance tripping | General Electric | GFT14ESSM1WW | none | unit 308 | Laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923072632
2024-09-17 09:38 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | General Electric | GFT14ESSM1WW | none | unit 311 | Laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923105789
2024-09-17 09:38 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | General Electric | GFT14ESSM1WW | none | unit 311 | Laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923108707
2024-09-17 09:51 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 312 | Laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923188866
2024-09-17 09:51 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 312 | Laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923193358
2024-09-17 09:58 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 314 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923246800
2024-09-17 09:59 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 314 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923251494
2024-09-17 10:05 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 321 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923296643
2024-09-17 10:29 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250 GF | Breaker | oven | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | Frigidaire | FGEW276SPFH | none | unit 322 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923465006
2024-09-17 10:37 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 324 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923520525
2024-09-17 10:42 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 333 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923561262
2024-09-17 10:49 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 336 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923606194
2024-09-17 10:52 | William | Santiago | 13881 | 72B concord st |  | North Reading | MA | 1864 | 781-315-3972 | superintendent |  | RS28A500ASR | Breaker | arc fault/GFCI combo breaker | 20 |  | 1 Pole | Leviton | Commercial |  | 2024-09-16 | 2024-09-12 | 30 Island st |  | lawrence | MA | 1840 | Frigs are tripping the GFCI breaker in the panel. We have done many test and found out this Samsung frig only works with the arc fault breaker. We have 21 in the building. Was verified by electrical inspector.¦Units¦103,104,105,107,108,109,¦203,204,205,208,209,¦303,304,305,308,309,¦403,404,405,408,409 | Leviton | LB120-DFT |  | apartments | Kitchen frig | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16923621898
2024-09-17 11:04 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | General electric | GFT14ESSM1WW | none | unit 405 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923711859
2024-09-17 11:22 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | General electric | JS645SL9SS | none | unit 407 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923832816
2024-09-17 11:34 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | General electric | JS645SL9SS | none | unit 413 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923928843
2024-09-17 11:39 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 413 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16923968626
2024-09-17 11:48 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | Intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 415 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924042483
2024-09-17 11:53 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project Manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 416 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924081225
2024-09-17 11:59 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 416 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924122703
2024-09-17 12:05 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | JS645SL9SS | none | unit 419 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924163703
2024-09-17 12:10 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 419 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924190295
2024-09-17 12:32 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 433 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924330519
2024-09-17 12:37 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 433 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924364582
2024-09-17 12:44 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 437 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924413451
2024-09-17 12:49 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 437 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924443512
2024-09-17 12:56 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | JS645SL9SS | none | unit 438 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924487308
2024-09-17 13:01 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 438 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924523318
2024-09-17 13:08 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS640RM4SS | none | unit 527 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924565717
2024-09-17 13:13 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 527 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924594382
2024-09-17 13:18 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-08-23 | 2024-06-14 | 2024-06-14 |  | 1325 Washington Street | MA | 2189 | while oven is warming | Whirlpool | WEE515SOLS2 | . | apartment | 1402 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16924626712
2024-09-17 13:47 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | JAS640RM4SS | none | unit 211 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924819459
2024-09-17 13:51 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | GFT14ESSM1WW | none | unit 211 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924844178
2024-09-17 13:56 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | JAS640RM4SS | none | unit 214 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924875270
2024-09-17 13:59 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-17 | 2024-06-14 | 2024-06-14 |  | 1325 Washington Street | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 |  | apartment | 2409 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16924891436
2024-09-17 14:00 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 214 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924899313
2024-09-17 14:03 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-17 | 2024-06-14 | 2024-06-14 |  | 1325 Washington Street | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | 1326 | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/16924920077
2024-09-17 14:11 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN250 GF | Breaker | Dryer | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | JAS640RM4SS | none | unit 220 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924970285
2024-09-17 14:11 | Paul | Eklund | 54252 | 210 Lisle St. |  | Braintree | MA | 2184 | 617-750-8798 | Owner / Sole Proprietor |  | Cutler Hammer CHN230GF | Breaker | Gfci | 30 |  | 2 Pole | Eaton | Residence |  | 2024-09-02 | 2024-09-02 | 138 Fox Lane |  | Falmouth | MA | 2536 | GFCI breaker trips instantly due to 8 milli-amps on appliance | AGA | AEL361DFABCWG | No | Kitchen | It's on a dedicated circuit in the kitchen. | No | No | Yes | No | https://www.formstack.com/admin/download/file/16924971299 | https://www.formstack.com/admin/download/file/16924971300
2024-09-17 14:15 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 220 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16924993010
2024-09-17 14:19 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS640RM4SS |  | unit 223 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925021001
2024-09-17 14:23 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 223 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925047195
2024-09-17 14:35 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | Project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 225 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925121224
2024-09-17 14:39 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | General electric | GFT14ESSM3WW | none | unit 225 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925152612
2024-09-17 14:43 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS640RM4SS | none | unit 228 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925179169
2024-09-17 14:47 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 228 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925204019
2024-09-17 14:55 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 302 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925255562
2024-09-17 14:58 | Michael | Gallerane | 559 | 149 Uxbridge Rd | #3 | Mendon | MA | 1756 | 508-922-0599 | Owner |  | BRN250 | Breaker | none | 50 | no | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/16925278685 | 2024-08-14 | 2024-08-14 | 73 Puritan Rd |  | Newton | MA | 2468 | Trips at night almost every night since installed when not in use.¦ Appliance technician said it can't be on a GFCI. ¦Checked the power cord into the unit & the electrical wiring from the range to the panel. | Fisher & Paykel | OR36SDI6X1 | no | Single Family | Kitchen | No | Yes | Yes | No | https://www.formstack.com/admin/download/file/16925278699 | https://www.formstack.com/admin/download/file/16925278700
2024-09-17 14:59 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 302 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925282069
2024-09-17 15:03 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 305 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925308939
2024-09-17 15:07 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 305 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925337361
2024-09-17 15:11 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS640RM4SS | none | unit 309 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925362580
2024-09-17 15:16 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 309 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925391137
2024-09-17 15:20 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645L9SS | none | unit 315 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925417060
2024-09-17 15:24 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 315 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925444399
2024-09-17 15:28 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JASGAORMASS | none | unit 329 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925469862
2024-09-17 15:31 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 329 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925492498
2024-09-17 15:43 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JASGAORMASS | none | unit 404 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925567759
2024-09-17 15:46 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 404 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925588915
2024-09-17 15:51 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645S9SS | none | unit 406 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925616988
2024-09-17 15:55 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 406 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925644801
2024-09-17 15:59 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 408 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925672262
2024-09-17 16:03 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 408 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925697722
2024-09-17 16:08 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS6AORMASS | none | unit 409 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925726739
2024-09-17 16:12 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 435 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925753621
2024-09-17 16:17 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 435 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925781777
2024-09-17 16:22 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 510 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925814366
2024-09-17 16:26 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 510 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925839079
2024-09-17 16:31 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 515 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925873034
2024-09-17 16:35 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 515 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16925895760
2024-09-17 22:08 | Jesse | Kuhlman | 21804 | 313 Eastern Avenue |  | Lynn | MA | 1902 | 7817256594 | Owner |  | Eaton | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2024-09-13 | 2024-08-27 | 242 Whitney Road |  | Medford | MA | 2155 | Breaker would trip when oven not in use. | LG | 403KMJQO4052 | NO | single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16927230500
2024-09-18 07:52 | Robert | Davidson | 14373 | 8 South St | 2 | Taunton | MA | 2780 | 7742539280 | Owner |  | Qf240a | Breaker | Breaker | 40 |  | 2 Pole | Siemens | Residence |  | 2024-08-22 | 2024-08-12 | 8 South St, 2 |  | Taunton | MA | 2780 | Will not hold with customers Range | Kenmore | 790.9901 | None | Single family home | Electric range in kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16928284281
2024-09-18 11:32 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-17 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | while oven is warming | Whirlpool | WEE515SOLS2 |  | apartment | 1401 | Yes | Yes | No | Yes |  | https://www.formstack.com/admin/download/file/16929682283
2024-09-18 11:34 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-17 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 | . | apartment | 1323 | Yes | Yes | No | Yes |  | https://www.formstack.com/admin/download/file/16929697820
2024-09-18 11:48 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-17 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 | . | apartment | 2409 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16929798370
2024-09-18 11:52 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-17 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 | . | apartment | 2343 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16929826847
2024-09-18 11:56 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-17 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 | . | apartment | 2104 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16929849832
2024-09-18 11:58 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-17 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 | . | apartment | 1302 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16929868161
2024-09-18 12:11 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-17 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 | . | Apartment | 2410 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16929950246
2024-09-18 12:13 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-17 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 | . | apartment | 2210 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16929962353
2024-09-18 12:16 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-17 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 | . | apartment | 1419 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16929981012
2024-09-18 12:37 | Daniel | Tomaz | 56869 | 480 snake hill rd |  | Harrisville | RI | 2830 | 4016789900 | Journeyman |  | Brn240gf | Breaker | . | 40 |  | 2 Pole | Eaton | Residence |  | 2024-09-09 | 2024-08-23 |  |  | 10 plimpton farm rd | MA | 2054 | Breaker trips without using oven | Jenn air | JMC2430LL00 |  | Town house | Kitchen oven | No | No | No | No | https://www.formstack.com/admin/download/file/16930111835 | https://www.formstack.com/admin/download/file/16930111836
2024-09-18 14:11 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-17 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 | . | apartment | 1413 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16930684999
2024-09-18 17:35 | Robert | Davidson | 14373 | 8 South St | 2 | Taunton | MA | 2780 | 7742539280 | Owner |  | Qf240a | Breaker | Breaker | 40 |  | 2 Pole | Siemens | Residence |  | 2024-08-15 | 2024-08-10 | 7 woodhaven rd |  | marshfield | MA | 2050 | Won't work with customers new range | Kenmore | 790.9901 | None | Single family house | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16931885899
2024-09-19 09:32 | Daniel | Tomaz | 56869 | 480 Snake Hill Rd |  | Harrisville | RI | 2830 | 4016789900 | Journeyman |  | BRN250GFCS | Breaker | . | 50 |  | 2 Pole | Eaton | Residence |  | 2024-09-13 | 2024-09-06 | 53 richardson drive |  | Millis | MA | 2054 | Car charger keeps tripping | Car charger | . |  | Garage | Garage car charger | No | No | No | No |  | https://www.formstack.com/admin/download/file/16934529460
2024-09-19 15:19 | Tariq | Simmons | 57369 | 69 allied st |  | Manchester | NH | 3109 | 6177508043 | Electrician |  | QF250A | Breaker | Gfci combo breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16936664771 | 2024-04-02 | 2024-04-01 | 4 park rd |  | Winchester | MA | 1890 | Breaker trips immediately after being reset and turned on | Bosch | HIIP057U | None | 2 family | Kitchen stove on first floor | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16936664796 | https://www.formstack.com/admin/download/file/16936664797
2024-09-19 15:20 | Tariq | Simmons | 57369 | 69 allied st |  | Manchester | NH | 3109 | 6177508043 | Electrician |  | QF250A | Breaker | Gfci combo breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16936667523 | 2024-04-02 | 2024-04-01 | 4 park rd |  | Winchester | MA | 1890 | Breaker trips immediately after being reset and turned on | Bosch | HIIP057U | None | 2 family | Kitchen stove on first floor | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16936667547 | https://www.formstack.com/admin/download/file/16936667549
2024-09-20 08:54 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | Project Manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS |  | unit 201 | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16939841776
2024-09-20 09:01 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | Project Manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit201 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16939895935
2024-09-20 09:10 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | Project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 202 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16939961640
2024-09-20 09:20 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | Project manager |  | BRN230 GF | Breaker | Dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 203 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940030066
2024-09-20 09:28 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 204 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940092130
2024-09-20 09:34 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 205 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940122736
2024-09-20 09:39 | Lucas | M Lowney | 14566 | 90 Douglas Pike |  | Smithfield | RI | 2917 | 5084558547 | President |  | GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-13 | 2024-09-05 | 21 West 2nd Str |  | Boston | MA | 2127 | All 2 pole GFI breakers are tripping simultaneously between 11pm - 2am once a month since building started to become occupied over the last 1.5yrs | Blomberg, GE | BERU24202SS, BERU30422SS, JKS3000SN1SS |  | 55 Unit Apartment Building | 201, 202, 203, 204, 205, 206, 207, 208, 209, 210, & 211¦301, 302, 303, 304, 305, 306, 307, 308, 309, 310, & 311¦401, 402, 403, 404, 405, 406, 407, 408, 409, 410, & 411¦501, 502, 503, 504, 505, 506, 507, 508, 509, 510, & 511¦601, 602, 603, 604, 605, 606, 607, 608, 609, 610, & 611¦ | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/16940148745 | https://www.formstack.com/admin/download/file/16940148746
2024-09-20 09:44 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 206 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940171969
2024-09-20 10:05 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 207 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940279393
2024-09-20 10:10 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 210 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940301854
2024-09-20 10:14 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 212 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940322800
2024-09-20 10:18 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 213 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940346476
2024-09-20 10:24 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 224 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940375602
2024-09-20 10:28 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 224 | lanudry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940401884
2024-09-20 10:34 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | CR4B242BL | none | unit 227 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940433128
2024-09-20 10:38 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 227 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940455832
2024-09-20 10:58 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN250GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS640RM4SS | none | unit 229 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940563055
2024-09-20 11:28 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | projected manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 229 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940734486
2024-09-20 11:33 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JP3030SW1SS | none | unit 230 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940765041
2024-09-20 11:40 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 231 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940802761
2024-09-20 11:45 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS640RM4SS | none | unit 231 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940830184
2024-09-20 11:49 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 231 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940852177
2024-09-20 11:52 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS640RM4SS | none | unit 232 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940873205
2024-09-20 11:56 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 232 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940895206
2024-09-20 12:02 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-20 | 2024-06-14 | [5 empty] | while warming oven | Whirpool | WEE515SOLS2 |  | Apartment | unit 1407 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16940929771
2024-09-20 12:10 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 603-880-4601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS640RM4SS | none | unit 234 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940970601
2024-09-20 12:14 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSN3WW | nnone | unit 234 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16940991966
2024-09-20 12:18 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 235 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941012368
2024-09-20 12:22 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 235 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941033262
2024-09-20 12:25 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 236 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941052066
2024-09-20 12:28 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 236 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941068648
2024-09-20 12:31 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 237 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941087490
2024-09-20 12:35 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 237 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941108065
2024-09-20 12:38 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 303 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941128400
2024-09-20 12:41 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 303 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941143789
2024-09-20 12:44 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS640RM4SS | none | unit 304 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941159816
2024-09-20 12:47 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 304 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941176941
2024-09-20 12:50 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 306 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941197226
2024-09-20 12:53 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 306 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941214318
2024-09-20 12:58 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS640RM4SS | none | unit 323 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941238122
2024-09-20 13:02 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 325 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941261796
2024-09-20 13:05 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 325 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941281592
2024-09-20 13:09 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS640RM4SS | none | unit 331 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941307522
2024-09-20 13:13 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 331 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941327489
2024-09-20 13:17 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS640RM4SS | none | unit 334 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941351348
2024-09-20 13:21 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 335 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941371518
2024-09-20 13:34 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 335 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941448190
2024-09-20 13:37 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 335 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941463592
2024-09-20 13:40 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 402 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941481148
2024-09-20 13:43 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 402 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941498799
2024-09-20 13:46 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 403 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941518277
2024-09-20 13:50 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 403 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941538700
2024-09-20 13:54 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JAS640RM4SS | none | unit 411 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941564802
2024-09-20 13:58 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM1WW | none | unit 411 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941586467
2024-09-20 13:59 | Steven | Rooney | 50969 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service Manager |  | Eaton BR BRN250 | Breaker | n/a | 50 |  | 2 Pole | Eaton | Residence |  | 2024-09-10 | 2024-09-10 | 14 West brook Rd |  | Northborough | MA | 1532 | trips after 3 minutes of using the cook top | GE appliances / range stove top | jbs160dm5ww |  | single family | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941596027
2024-09-20 14:01 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 418 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941607951
2024-09-20 14:05 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 418 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941628094
2024-09-20 14:10 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | JS645SL9SS | none | unit 530 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941654054
2024-09-20 14:11 | Steven | Rooney | 50969 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service manager |  | Siemens QF250a | Breaker | n/a | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-19 | 2024-09-19 | 3 Farm House Lane Building 10 unit 7 |  | Marlborough | MA | 1752 | Trips right away, when powered on | GE | J BS460D M5WW |  | Apartment / kitchen | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941661835
2024-09-20 14:13 | keith | Whittaker | 2810 | 116 Perimeter RD |  | Nashua | NH | 3063 | 6038804601 | project manager |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen Street |  | Boston | MA | 2128 | intermittent nuisance tripping | general electric | GFT14ESSM3WW | none | unit 530 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16941673545
2024-09-20 15:58 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-20 | 2024-06-14 | 1325 Washington Street |  |  |  |  | while warming oven | Whirpool | WEE515SOLS2 |  | Apartment | unit #1207 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16942250856
2024-09-23 09:52 | Joseph | Rocheleau | 38838 | 58A Central st |  | Hudson | MA | 1749 | 9782658006 | Electrician |  | SEIMANS Q 120 DF | Breaker | No other type | 20 |  | 1 Pole | Siemens | Residence |  | 2024-08-21 | 2024-06-17 | [5 empty] | A Seimans duel function breaker kept tripping during a wash cycle of a Miele washer, also the breaker tripped during a cycle on a 120v Miele dryer.¦The circuits ran fine when i installed a regular Q 120.¦I discovered through trouble shooting the problem that the circuits both ran fine when i installed a Seimans arc fault 120v breaker.¦So i was happy that the circuits had arc fault protection. | Miele | WXD160 | Miele TXD 160 WP | Laundry closet | The only things effected by the tripping were the washer and dryer | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16949629385 | https://www.formstack.com/admin/download/file/16949629386
2024-09-23 14:49 | Tijana | Alibegovic | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 7817010028 | Property Manager |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-17 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | while warming oven | Whirlpool | WEE515SOLS2 |  | apartment | Unit #1323 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16951581842
2024-09-24 08:34 | Joseph | Garnhum | 23401 | 18 Oak Ridge Ave | apt 2 | Salem | NH | 3079 | 6172858248 | Owner/Master Electrician |  | QF250A | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-19 | 2024-09-17 | 8 Whittier Road |  | Billerica | MA | 1821 | When stove or cooktop is turned on, after a few minutes the breaker trips. Holds fine without stove on. | Frgidaire | FCFI3083AS | N/A | Single Family Home | Oven receptacle in kitchen. Nothing else on circuit. Its dedicated. | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/16954987778
2024-09-24 09:02 | Penney | Smith | 8999 | 99 Wilkens Lane |  | Hyannis | MA | 2601 | 508-838-1260 | Superintendent |  | Siemens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 1101 |  | Hyannis | MA | 2601 | Breaker would not hold when turning on the range | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955102940
2024-09-24 09:10 | Penney | Smith | 8999 | 99 Wilkens Lane |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 1102 |  | Hyannis | MA | 2601 | breaker tripped when starting the range | whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955133529
2024-09-24 09:12 | Penney | Smith | 8999 | 99 Wilkens Lane |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane |  | Hyannis | MA | 2601 | Breaker tripped when range was turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955144554
2024-09-24 09:19 | Penney | Smith | 8999 | 99 Wilkens Lane |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1103 |  | Hyannis | MA | 2601 | Breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955182086
2024-09-24 09:22 | Penney | Smith | 8999 | 99 Wilkens Lane |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1104 |  | Hyannis | MA | 2601 | Breaker tripped when range was turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955195724
2024-09-24 09:25 | Penney | Smith | 8999 | 99 Wilkens Lane |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-29 | 2024-07-08 | 99 Wilkens Lane, Unit 1105 |  | Hyannis | MA | 2601 | Breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955211024
2024-09-24 09:28 | Penney | Smith | 8999 | 99 Wilkens Lane |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-29 | 2024-07-08 | 99 Wilkens Lane, Unit 1106 |  | Hyannis | MA | 2601 | Breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955224215
2024-09-24 09:30 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1105 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1107 |  |  |  |  | Breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955234107
2024-09-24 09:32 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1107 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1109 |  |  |  |  | Breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955244679
2024-09-24 09:35 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1110 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1110 |  |  |  |  | breaker trips when range is turned on | whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955257726
2024-09-24 09:39 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1111 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1111 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955281934
2024-09-24 09:43 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1120 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1120 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955300497
2024-09-24 09:47 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1121 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1121 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955324646
2024-09-24 09:51 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1122 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1122 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955344134
2024-09-24 09:52 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1123 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1123 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955353554
2024-09-24 10:02 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1201 |  | Hyannis | MA | 2601 | 5088381260 | superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1201 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955409003
2024-09-24 10:12 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1202 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1202 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955466405
2024-09-24 10:13 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1203 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1203 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955477973
2024-09-24 10:16 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1204 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1204 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955491434
2024-09-24 10:17 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1205 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1205 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955503023
2024-09-24 10:19 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1206 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1206 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955512421
2024-09-24 10:21 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1207 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1207 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955525785
2024-09-24 10:23 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1209 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1209 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955537166
2024-09-24 10:25 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1210 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1210 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955550413
2024-09-24 10:27 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1211 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1211 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955561597
2024-09-24 10:29 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1212 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1212 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955573530
2024-09-24 10:31 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1213 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1213 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955586426
2024-09-24 10:33 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1214 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1214 |  |  |  |  | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955598948
2024-09-24 10:36 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1215 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1215 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955617228
2024-09-24 10:38 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1216 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1216 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955625752
2024-09-24 10:39 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1217 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1217 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955636697
2024-09-24 10:41 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1218 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimen | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1218 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955647636
2024-09-24 10:43 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1219 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1219 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955658095
2024-09-24 10:46 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1220 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1220 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955679897
2024-09-24 10:48 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1221 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1221 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955689331
2024-09-24 10:50 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1222 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1222 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955700712
2024-09-24 10:51 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1223 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1223 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955711040
2024-09-24 10:55 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1301 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1301 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955735697
2024-09-24 10:57 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1302 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1302 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955750238
2024-09-24 11:00 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1303 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1303 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955765113
2024-09-24 11:02 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1304 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1304 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955779086
2024-09-24 11:05 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1305 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1305 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955805294
2024-09-24 11:07 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1306 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1306 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955819549
2024-09-24 11:09 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1307 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1307 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955830317
2024-09-24 11:11 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1309 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1309 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955842781
2024-09-24 11:12 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1310 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1310 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955852138
2024-09-24 11:15 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1311 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1311 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955867701
2024-09-24 11:16 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1312 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1312 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955878175
2024-09-24 11:18 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1313 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1313 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955889868
2024-09-24 11:20 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1314 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1314 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955900708
2024-09-24 11:22 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1315 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1315 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955916414
2024-09-24 11:24 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1316 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1316 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955931461
2024-09-24 11:26 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1317 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1317 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955941737
2024-09-24 11:27 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1318 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1318 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955949854
2024-09-24 11:29 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1319 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1319 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955960280
2024-09-24 11:30 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1320 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1320 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955969569
2024-09-24 11:32 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1321 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1321 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955981260
2024-09-24 11:34 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1322 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1322 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16955991010
2024-09-24 11:35 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1323 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1323 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956001230
2024-09-24 11:37 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1401 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1401 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | wee515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956012264
2024-09-24 11:39 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1402 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1401 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956023536
2024-09-24 11:41 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1403 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1403 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956037619
2024-09-24 11:42 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1405 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1405 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956050473
2024-09-24 11:44 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1406 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seiens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1406 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956063919
2024-09-24 11:46 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1407 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1407 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956074359
2024-09-24 11:47 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1409 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1409 |  | Hyannis | MA | 2601 | Breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956083884
2024-09-24 11:49 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1410 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1410 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956094127
2024-09-24 11:50 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1411 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1411 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956105105
2024-09-24 11:52 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1412 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1412 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956114681
2024-09-24 11:53 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1413 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1413 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956125843
2024-09-24 11:55 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1414 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1414 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956137641
2024-09-24 11:57 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1415 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1415 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | wee515sols2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956147981
2024-09-24 11:59 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1416 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1416 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956159225
2024-09-24 12:03 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1417 |  | Hyannis | MA | 2601 | 5088381260 | Superitendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1417 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956187623
2024-09-24 12:05 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1418 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1418 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956197510
2024-09-24 12:06 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1419 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1419 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956209017
2024-09-24 12:08 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1420 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1420 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956219181
2024-09-24 12:10 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1421 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1420 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956228079
2024-09-24 12:11 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1422 |  | Hyannis | MA | 2601 | 5088381260 | superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1422 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956240520
2024-09-24 12:13 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 1423 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 1423 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956251098
2024-09-24 12:33 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2101 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2101 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956402563
2024-09-24 12:36 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2102 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2102 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16956419640
2024-09-24 14:09 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2103 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2103 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957035218
2024-09-24 14:11 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2104 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2104 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957048914
2024-09-24 14:13 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2105 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2105 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957064208
2024-09-24 14:15 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2106 |  | Hyannis | MA | 2601 | 5088381260 | superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2106 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957077269
2024-09-24 14:17 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2107 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2107 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957090716
2024-09-24 14:47 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2108 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2108 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957277210
2024-09-24 14:49 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2109 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2109 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957290789
2024-09-24 14:50 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2110 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2110 |  | Hyannis | MA | 2601 | Breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957302463
2024-09-24 14:52 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2111 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2111 |  | Hyannis | MA | 2601 | Breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957314762
2024-09-24 14:55 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2112 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2112 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957333014
2024-09-24 14:59 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2113 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2113 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957360002
2024-09-24 15:02 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2114 |  | Hyannis | MA | 2601 | 5088381260 | supervisor |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2114 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957375228
2024-09-24 15:03 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2115 |  | Hyannis | MA | 2601 | 5088381260 | superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2115 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957387499
2024-09-24 15:07 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2116 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2116 |  | Hyannis | MA | 2601 | breaker trips when the range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957413852
2024-09-24 15:09 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2117 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2117 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | breaker trips when range is turned on | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957426924
2024-09-24 15:11 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2118 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2118 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957437979
2024-09-24 15:15 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2119 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2119 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957464912
2024-09-24 15:18 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2120 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2120 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16957483730
2024-09-24 15:57 | Alexander | Bielunis | 8653 | 8 Sequoia Drive |  | Holyoke | MA | 1040 | 4132043762 | Mgr. |  | R13-LB240-GFR | Breaker | GFCI | 40 |  | 2 Pole | Leviton | Residence |  | 2024-09-24 | 2024-09-24 | 10 Bellview Circle |  | Amherst | MA | 1002 | continuously trips the breaker | LG | LSIL6334FE |  | Kitchen | kitchen Electric Range | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/16957752242
2024-09-25 09:35 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | pm |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 202 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961060868
2024-09-25 09:39 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 203 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961080800
2024-09-25 09:43 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 204 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961105217
2024-09-25 09:47 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 205 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961123985
2024-09-25 09:52 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 206 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961147388
2024-09-25 09:53 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2201 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2201 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961157379
2024-09-25 09:55 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2202 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | Seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2202 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961166647
2024-09-25 09:56 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2203 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2203 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961175234
2024-09-25 09:58 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2204 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2204 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961184641
2024-09-25 10:00 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2205 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2205 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961195664
2024-09-25 10:02 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2206 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2206 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961205362
2024-09-25 10:04 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2207 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2207 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961215123
2024-09-25 10:04 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | FGEW276SPFH | none | unit 207 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961220262
2024-09-25 10:06 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2208 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2208 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961229884
2024-09-25 10:08 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JP3030SW1SS | none | unit 208 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961240745
2024-09-25 10:08 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2209 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2209 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961240834
2024-09-25 10:10 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2210 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2210 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961251159
2024-09-25 10:11 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM1WW | none | unit 208 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961257134
2024-09-25 10:11 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2211 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2211 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961261003
2024-09-25 10:13 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2212 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2212 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961267957
2024-09-25 10:14 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2213 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2213 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961277078
2024-09-25 10:14 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GDT630PYR7FS | none | unit 210 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961277144
2024-09-25 10:16 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2214 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2214 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961285932
2024-09-25 10:17 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS540RM4SS | none | unit 212 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961292181
2024-09-25 10:20 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 213 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961307892
2024-09-25 10:21 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2215 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2215 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961316324
2024-09-25 10:23 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 215 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961324550
2024-09-25 10:23 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2216 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2216 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961327308
2024-09-25 10:25 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2217 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2217 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961336580
2024-09-25 10:25 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 215 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961338721
2024-09-25 10:26 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2218 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2218 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961347327
2024-09-25 10:28 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2219 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2219 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961357105
2024-09-25 10:28 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 219 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961359413
2024-09-25 10:30 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2220 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2220 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961368874
2024-09-25 10:32 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 219 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961378579
2024-09-25 10:34 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 221 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961407449
2024-09-25 10:37 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM1WW | none | unit 221 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961425562
2024-09-25 10:39 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 222 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961440662
2024-09-25 10:42 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 222 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961455497
2024-09-25 10:46 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 310 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961478843
2024-09-25 10:49 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM1WW | none | unit 310 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961495569
2024-09-25 10:56 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2301 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2301 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961538840
2024-09-25 11:00 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 313 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961564004
2024-09-25 11:00 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2302 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2302 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961567642
2024-09-25 11:02 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 313 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961579326
2024-09-25 11:03 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2303 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2303 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | breaker trips when range is turned on | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961585010
2024-09-25 11:05 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2304 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2304 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961595102
2024-09-25 11:06 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 316 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961599275
2024-09-25 11:07 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2305 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2305 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515sOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961609210
2024-09-25 11:09 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 316 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961618888
2024-09-25 11:09 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2306 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2306 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961619306
2024-09-25 11:11 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2307 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2307 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961636191
2024-09-25 11:11 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 317 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961637479
2024-09-25 11:13 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2308 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2308 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLs2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961646642
2024-09-25 11:14 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 317 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961654155
2024-09-25 11:17 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 318 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961672932
2024-09-25 11:20 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 318 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961691355
2024-09-25 11:21 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2309 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2309 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961700523
2024-09-25 11:23 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 319 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961710958
2024-09-25 11:24 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2310 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2310 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961714792
2024-09-25 11:26 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 319 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961728278
2024-09-25 11:26 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2311 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2311 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961729361
2024-09-25 11:29 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 320 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961744980
2024-09-25 11:31 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 320 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961762092
2024-09-25 11:34 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 323 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961779525
2024-09-25 11:38 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 328 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961799642
2024-09-25 11:40 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 328 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961841167
2024-09-25 11:43 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 330 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961930491
2024-09-25 11:45 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 330 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961948216
2024-09-25 11:48 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 332 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961969239
2024-09-25 11:50 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2312 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2312 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961976884
2024-09-25 11:52 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2313 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2313 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16961989428
2024-09-25 11:52 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 332 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16961989541
2024-09-25 11:53 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2314 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2314 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962000766
2024-09-25 11:55 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 337 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962011611
2024-09-25 11:55 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2315 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2315 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962011802
2024-09-25 11:56 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2316 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2316 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962021770
2024-09-25 11:58 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2317 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2317 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962032122
2024-09-25 11:58 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 337 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962032721
2024-09-25 11:59 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2318 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2318 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962041594
2024-09-25 12:01 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2319 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2319 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962050869
2024-09-25 12:01 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 401 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962051581
2024-09-25 12:03 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2320 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2320 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962060879
2024-09-25 12:04 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 401 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962067607
2024-09-25 12:07 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 412 | range | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962087157
2024-09-25 12:10 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 412 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962103961
2024-09-25 12:23 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 414 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962191017
2024-09-25 12:27 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 414 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962210869
2024-09-25 12:30 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | Frigidaire | FGEW276SPFH | none | unit 417 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962233487
2024-09-25 12:33 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFW148SSM1WW | none | unit 417 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962248981
2024-09-25 12:36 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 420 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962268020
2024-09-25 12:39 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 420 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962285452
2024-09-25 12:42 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 421 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962303408
2024-09-25 12:44 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 421 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962319152
2024-09-25 12:47 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 422 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962337950
2024-09-25 12:50 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 422 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962355183
2024-09-25 12:53 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 423 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962370589
2024-09-25 12:54 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2401 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2401 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962377935
2024-09-25 12:56 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 423 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962391486
2024-09-25 12:58 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 424 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962406518
2024-09-25 13:01 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 424 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962421008
2024-09-25 13:04 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 425 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962438327
2024-09-25 13:06 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 425 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962453500
2024-09-25 13:20 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 427 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962538647
2024-09-25 13:22 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2402 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2402 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962551844
2024-09-25 13:24 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2403 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2403 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962566707
2024-09-25 13:25 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 427 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962573733
2024-09-25 13:26 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2404 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2404 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962578321
2024-09-25 13:27 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2405 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2405 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962588382
2024-09-25 13:28 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 428 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962592888
2024-09-25 13:29 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2406 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2406 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962599424
2024-09-25 13:31 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 428 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962609188
2024-09-25 13:31 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2407 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | seimens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2407 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962614403
2024-09-25 13:34 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 429 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962626204
2024-09-25 13:34 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2408 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2408 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962628218
2024-09-25 13:36 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2409 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2409 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962638832
2024-09-25 13:36 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 429 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962643778
2024-09-25 13:38 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2410 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2410 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962654352
2024-09-25 13:39 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 430 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962658932
2024-09-25 13:41 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2411 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2411 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962673081
2024-09-25 13:41 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW |  | unit 430 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962673482
2024-09-25 13:44 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 431 | range | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962689931
2024-09-25 13:47 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 431 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962705075
2024-09-25 13:49 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 432 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962721473
2024-09-25 13:52 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 432 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962738492
2024-09-25 13:54 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 | . | 2 Pole | Siemens | Residence |  | 2024-09-25 | 2024-06-14 | 1325 Washington Street |  | Weymouth | MA | 2189 | While warming oven | Whirlpool | WEE515SOLS2 | . | apartment | 1400 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962749094
2024-09-25 13:55 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 434 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962756863
2024-09-25 13:55 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2412 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2412 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962759432
2024-09-25 13:58 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2413 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2413 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962774190
2024-09-25 13:58 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 434 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962774324
2024-09-25 13:59 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2414 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2414 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962786170
2024-09-25 14:00 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 436 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962793340
2024-09-25 14:01 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2415 |  | Hyannis | MA | 2601 | Superintendent | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2415 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962799193
2024-09-25 14:03 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2416 |  | Hyannis | MA | 2601 | 5088381260 | superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2416 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962808878
2024-09-25 14:03 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 436 | dryer | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962809411
2024-09-25 14:04 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2417 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2417 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962817938
2024-09-25 14:06 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2418 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2418 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962830867
2024-09-25 14:08 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2419 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2419 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962841616
2024-09-25 14:10 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 2420 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 2420 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLs2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962853651
2024-09-25 14:14 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-25 | 2024-06-14 | [5 empty] | When warming oven | Whirlpool | WEE515SOLS2 |  | apartment | unit 1209 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962877316
2024-09-25 14:14 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 505 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962877672
2024-09-25 14:14 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-25 | 2024-06-14 | [5 empty] | When warming oven | Whirlpool | WEE515SOLS2 |  | apartment | unit 1209 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962878236
2024-09-25 14:17 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM1WW | none | unit 505 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962894723
2024-09-25 14:17 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-25 | 2024-06-14 | [5 empty] | When warming oven | Whirlpool | WEE515SOLS2 |  | apartment | unit 1322 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16962897961
2024-09-25 14:20 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 507 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962912718
2024-09-25 14:22 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM1WW | none | unit 507 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962930275
2024-09-25 14:25 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 1 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 508 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962945741
2024-09-25 14:27 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM1WW | none | unit 508 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962959853
2024-09-25 14:29 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 509 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962974143
2024-09-25 14:32 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM1WW | none | unit 509 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16962990784
2024-09-25 14:35 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 512 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963007848
2024-09-25 14:38 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 512 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963024791
2024-09-25 14:40 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 513 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963038579
2024-09-25 14:42 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 513 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963051660
2024-09-25 14:45 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 514 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963067055
2024-09-25 14:48 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM1WW | none | unit 514 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963086879
2024-09-25 14:51 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 516 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963105660
2024-09-25 14:53 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | b | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 516 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963121312
2024-09-25 14:56 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 517 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963137709
2024-09-25 14:58 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | DRYER | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 517 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963154330
2024-09-25 15:01 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 518 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963170144
2024-09-25 15:03 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 518 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963184960
2024-09-25 15:06 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | frididaire | FGEW276SPFH | none | unit 519 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963206264
2024-09-25 15:09 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 519 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963223037
2024-09-25 15:19 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS630RM4SS | none | unit 520 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963285176
2024-09-25 15:22 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 520 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963301608
2024-09-25 15:24 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 521 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963318313
2024-09-25 15:26 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM1WW | none | unit 521 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963333368
2024-09-25 15:29 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 522 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963346750
2024-09-25 15:31 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM1WW | none | unit 522 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963361163
2024-09-25 15:34 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 523 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963377803
2024-09-25 15:36 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 523 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963391400
2024-09-25 15:39 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 524 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963405035
2024-09-25 15:41 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 524 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963422127
2024-09-25 15:44 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 525 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963438660
2024-09-25 15:46 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 525 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963454656
2024-09-25 15:49 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 528 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963472041
2024-09-25 15:52 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 528 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963489339
2024-09-25 15:55 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 529 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963505958
2024-09-25 15:57 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 529 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963520706
2024-09-25 16:00 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 531 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963540257
2024-09-25 16:03 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 531 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963554058
2024-09-25 16:06 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 532 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963572936
2024-09-25 16:08 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 532 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963589360
2024-09-25 16:11 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS640RM4SS | none | unit 533 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963605502
2024-09-25 16:14 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 533 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963621381
2024-09-25 16:17 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JAS6404M4SS | none | unit 534 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963641234
2024-09-25 16:20 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 534 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963657355
2024-09-25 16:24 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 535 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963679927
2024-09-25 16:27 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 535 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963697683
2024-09-25 16:30 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN250 GF | Breaker | range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | JS645SL9SS | none | unit 536 | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963714460
2024-09-25 16:33 | Keith | Whittaker | 2810 | 116 perimeter rd |  | Nashua | NH | 3062 | 6038804601 | PM |  | BRN230 GF | Breaker | dryer | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-15 | 2024-06-05 | 282 Bremen st |  | Boston | MA | 2128 | intermittent nuisance tripping | GE | GFT14ESSM3WW | none | unit 536 | laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16963729106
2024-09-26 09:00 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3101 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3101 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966409067
2024-09-26 09:02 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3102 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3102 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966416326
2024-09-26 09:06 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3103 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3103 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966431593
2024-09-26 09:08 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3104 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3104 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966440481
2024-09-26 09:11 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3106 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | Siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3106 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966455811
2024-09-26 09:14 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3107 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3107 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966469097
2024-09-26 09:16 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3109 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3109 |  | Hyannis | MA | 2601 | Breaker trips when range is turned on | whirlpool | WEE515SOLs2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966477262
2024-09-26 09:18 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3110 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3110 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLs2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966486512
2024-09-26 09:46 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3111 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3111 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966622899
2024-09-26 10:03 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3112 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3112 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966712504
2024-09-26 10:05 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3113 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3113 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966721609
2024-09-26 10:07 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3114 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3114 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966731138
2024-09-26 10:12 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3115 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3115 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966759795
2024-09-26 10:13 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3116 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3116 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966768092
2024-09-26 10:15 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3117 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3117 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966780417
2024-09-26 10:16 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3118 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3118 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16966789054
2024-09-26 11:07 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3119 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3119 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16967083353
2024-09-26 11:09 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3120 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3120 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16967095347
2024-09-26 11:10 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3121 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3121 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16967104984
2024-09-26 11:21 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3122 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | Siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3122 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16967167063
2024-09-26 11:27 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3123 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3123 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16967204396
2024-09-26 11:29 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3125 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3125 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16967215344
2024-09-26 11:30 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3127 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3127 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLs2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16967223496
2024-09-26 11:32 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3128 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3128 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16967233987
2024-09-26 11:33 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3129 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3129 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16967243970
2024-09-26 11:35 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3130 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3130 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16967252520
2024-09-26 11:36 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3131 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3131 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16967264440
2024-09-26 11:38 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3132 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3132 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16967279480
2024-09-26 12:46 | Andrew | Harland | 21030 | Harland Electric | PO Box 94 | Littleton, MA | MA | 1460 | 9784868154 | President |  | Eaton BRN250GF | Breaker | 2 POLE 50 GFCI breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-09-12 | 2024-09-12 | 16 Beaverbrook Rd |  | Littleton | MA | 1460 | Installed new 4 wire 50A circuit for electric range on 9/12/24. All burners on stovetop worked. when oven was set to preheat, GFCI breaker tripped. Spoke to the local inspector, I installed a standard 2 pole 50 breaker and instructed the customers to use the oven ove the weekend. Reinstalled the GFCI breaker on 9/17/24, oven continues to trip the GFCI breaker. I notified the local inspector, who instructed me to put the range on a standard 2pole 50A breaker and fill out the tripping report. All wiring to the range is new, no issues with the circuit, outlet or range cord. | Whirlpool | WFE550S0LW3 |  | Single family dwelling | Customer purchase new electric range, fed from new 50A 4 wire circuit. circuit feeds no other loads | No | No | No | No |  | https://www.formstack.com/admin/download/file/16967710976
2024-09-27 14:09 | Christine | Miller | 60582 | 11 Washburn street |  | Springfield | MA | 1107 | 4138871798 | Electrician |  | L1603160246 | Breaker | 2pole | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/16973456851 | 2024-09-27 | 2024-09-27 | [5 empty] | Breaker tripped immediately | LG | Lrel6323s | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/16973456864 | https://www.formstack.com/admin/download/file/16973456865
2024-09-27 14:34 | Paul | Macrina | 15503 | 30 Nebo Street |  | Medfield | MA | 2052 | 508-359-7954 | Technician |  | BRN230GF | Breaker | . | 30 |  | 2 Pole | Eaton | Residence |  | 2024-09-23 | 2024-05-27 | [5 empty] | Dryer stopped and would not turn back on, Reset breaker. Did not work. Replaced GFCI breaker. Continued to trip. Replace with regular breaker. | Whirlpool | WED5010LW1 | None | Single family | Basement laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/16973586516
2024-09-29 21:52 | Mark | Roussel | 20011 | 33 old forge Ln |  | Sudbury | MA | 1776 | 9784438888 | electrician |  | Square D HOM250GFIC | Breaker | GFCI breaker | 50 | 50 | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/16980399960 | 2024-08-02 | 2024-06-08 | 33 Hathorne St |  | Salem | MA | 1970 | this brand new range installed in an newly renovated apartment then rented shortly after completion -¦¦The stove top work without any issues ---- the oven will pre heat but trips the GFCI breaker once the oven is up to temperature (this is a consistent pattern) | Frigidaire Electrolux | FCF13083ASA | no | Kitchen | none | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/16980399974 | https://www.formstack.com/admin/download/file/16980399975
2024-09-30 10:57 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3201 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Seimens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3201 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982585293
2024-09-30 10:59 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3202 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3202 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982597305
2024-09-30 11:01 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3203 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3203 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982609462
2024-09-30 11:03 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3204 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3204 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982624556
2024-09-30 11:05 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3206 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3206 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982637055
2024-09-30 11:11 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3207 |  | Hyannis | MA | 2601 | 5088381260 | superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3207 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982674100
2024-09-30 11:15 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3209 |  | Hyannis | MA | 2601 | 5088381260 | superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3209 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982702337
2024-09-30 11:17 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3210 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3210 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982714770
2024-09-30 11:19 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3211 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3211 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982731284
2024-09-30 11:21 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3212 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3212 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982741857
2024-09-30 11:22 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3213 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3213 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982753192
2024-09-30 11:27 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3214 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3214 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982781593
2024-09-30 11:29 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3215 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3215 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982795423
2024-09-30 11:31 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3216 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3216 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982811131
2024-09-30 11:33 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3217 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3217 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982824050
2024-09-30 11:34 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3218 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3218 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982835967
2024-09-30 11:36 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3219 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3219 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982848089
2024-09-30 11:38 | Craig | Vigeant | 22917 | 64 Kent Dr |  | Hudson | MA | 1749 | 5084226066 | Owner |  | BRN250GFCS | Breaker | breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-22 | 2024-08-22 | 29 Pembrook St |  | Marlborough | MA | 1752 | Breaker Keeps Tripping when using Oven. | Frigidaire | FFEF3012UW |  | Kitchen | Kitchen Oven | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16982858476
2024-09-30 11:38 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3220 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3220 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982862292
2024-09-30 11:40 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3221 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3221 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982874481
2024-09-30 11:42 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3222 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3222 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982885076
2024-09-30 11:43 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3223 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3223 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982896254
2024-09-30 11:45 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3225 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3225 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982906028
2024-09-30 11:46 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3227 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3227 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982918160
2024-09-30 11:48 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3228 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3228 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982930220
2024-09-30 11:50 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3229 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3229 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982940827
2024-09-30 11:51 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3230 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3230 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982951445
2024-09-30 11:53 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3231 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3231 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982963632
2024-09-30 11:54 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3232 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3232 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16982974337
2024-09-30 12:33 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-30 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1202 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16983242949
2024-09-30 12:34 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-30 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1202 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16983244386
2024-09-30 12:34 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-30 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1202 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16983247046
2024-09-30 12:38 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-30 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1225 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16983274465
2024-09-30 12:42 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-30 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2402 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16983296921
2024-09-30 12:44 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-30 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2403 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16983311963
2024-09-30 12:47 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-30 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2409 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16983330319
2024-09-30 12:49 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-30 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1210 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16983347558
2024-09-30 12:53 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-30 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1208 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16983367397
2024-09-30 12:55 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-30 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1214 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16983382237
2024-09-30 13:50 | Alexander | Jennings | 22893 | 31 Telegraph Street |  | Boston | MA | 2127 | 3393682099 | Electrician |  | GFTCB230 | Breaker | NA | 30 |  | 2 Pole | Eaton | Residence |  | 2024-07-09 | 2024-07-09 |  |  | 31 Telegraph | MA | 2127 | Breaker trips within 1 minute of turning on. | Whirlpool | WET4024HWO | None | Residential | Basement Laundry Room | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16983744079
2024-09-30 15:19 | Daniels | Electric | 16467 | 895 Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | GFI 40 amp | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2024-08-01 | 2024-09-13 | 52 Brook st unit 21 |  | haverhill | MA | 1832 | Tripping while heating burners | GE | JB256DM4BB |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16984350214
2024-09-30 15:28 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3301 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3301 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984408558
2024-09-30 15:30 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3302 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3302 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984422019
2024-09-30 15:30 | Daniels | Electric | 16467 | 895 Salem Street 2A |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | L2310020140 | Breaker | n/a | 50 | n/a | 2 Pole | Siemens | Residence |  | 2024-08-01 | 2024-09-27 | 33 woodcock unit 24 |  | haverhill | MA | 1832 | breaker trips when stove reaches temp | GE | JB256D |  | Apartment | Kitchen¦ | No | No | No | No |  | https://www.formstack.com/admin/download/file/16984423805
2024-09-30 15:32 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3303 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3303 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984431649
2024-09-30 15:33 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3304 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3304 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984443559
2024-09-30 15:35 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3306 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3306 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984453653
2024-09-30 15:36 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3307 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3307 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984463469
2024-09-30 15:38 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3309 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3309 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984475551
2024-09-30 15:40 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3310 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3310 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984485898
2024-09-30 15:41 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3311 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3311 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984497492
2024-09-30 15:43 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3312 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3312 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984510058
2024-09-30 15:45 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3313 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3313 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984522003
2024-09-30 15:47 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3314 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3314 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984536035
2024-09-30 15:49 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3315 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3315 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984552435
2024-09-30 15:52 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3316 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3316 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984582524
2024-09-30 15:54 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3317 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3317 |  | Hyannis | MA | 2601 | breaker trips when the range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984597884
2024-09-30 15:56 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3318 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3318 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984611420
2024-09-30 15:59 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3319 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3319 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984635607
2024-09-30 16:00 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3320 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3320 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984647923
2024-09-30 16:02 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3321 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3321 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984657685
2024-09-30 16:04 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3322 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3322 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984668303
2024-09-30 16:06 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3323 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3323 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984679065
2024-09-30 16:08 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3325 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3325 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984693253
2024-09-30 16:09 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3327 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3327 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kithen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984705476
2024-09-30 16:11 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3328 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3328 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984716130
2024-09-30 16:13 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3329 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3329 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984730207
2024-09-30 16:15 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3330 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3330 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984744356
2024-09-30 16:17 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3331 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3331 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984755273
2024-09-30 16:18 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3332 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3332 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16984764499
2024-10-01 08:54 | Roy | Brooks | 21941 | 12 Bush Pond Road |  | Norfolk | MA | 2056 | 617-645-1348 | Owner |  | GFTCB240 | Breaker |  | 40 |  | 2 Pole | Eaton | Residence |  | 2024-09-26 | 2024-09-26 | 12 Flintlock Road |  | Medfield | MA | 2052 | every time the stove came on - the breaker tripsSamsung | Samsung | NS16DB930012 | none | Single Family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16987784424
2024-10-01 10:59 | RICHARD | CHENEVERT | 14531 | 16 FAIRVIEW ST. |  | LUDLOW | MA | 1056 | 413-883-5350 | PRESIDENT/OWNER |  | Cutler Hammer/QBGFT2050 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2024-09-27 | 2024-06-28 | 586 MILL ST |  | AGAWAM | MA | 1001 | WITHIN THE FIRST COUPLE OF MINUTES BREAKER TRIPS WHEN USING THE OVEN | FRIDGIDAIRE | FCWS2727ASG |  | KITCHEN | KITCHEN RANGE | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/16988564692
2024-10-01 11:25 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3401 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | Siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3401 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988762826
2024-10-01 11:27 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3402 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3402 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988778243
2024-10-01 11:29 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3403 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3403 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988799538
2024-10-01 11:31 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3404 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3404 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988814712
2024-10-01 11:32 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3406 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3406 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988826134
2024-10-01 11:35 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3407 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3407 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988842275
2024-10-01 11:36 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3409 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3409 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988852575
2024-10-01 11:38 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3410 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3410 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988865336
2024-10-01 11:40 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3411 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3411 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988874542
2024-10-01 11:41 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3412 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3412 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988884970
2024-10-01 11:43 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3413 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3413 |  | Hyannis | MA | 2601 | Breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988898970
2024-10-01 11:45 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3414 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | Siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3414 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988910208
2024-10-01 11:46 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3415 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3415 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988921053
2024-10-01 11:48 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3416 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3416 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988935394
2024-10-01 11:50 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3417 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3417 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988945691
2024-10-01 11:51 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3418 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3418 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988957022
2024-10-01 11:53 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3419 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 34190 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988967337
2024-10-01 11:55 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3420 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3420 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988980308
2024-10-01 11:56 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3421 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3421 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16988991895
2024-10-01 11:58 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3422 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3422 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989003032
2024-10-01 11:59 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3423 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3423 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989013999
2024-10-01 12:01 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3425 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3425 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989023440
2024-10-01 12:03 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3427 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3427 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989036795
2024-10-01 12:04 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3428 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | Siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3428 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989046614
2024-10-01 12:06 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3429 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3429 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989057478
2024-10-01 12:07 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3430 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3430 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989067952
2024-10-01 12:08 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3431 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3431 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989076547
2024-10-01 12:10 | Penney | Smith | 8999 | 99 Wilkens Lane, Unit 3432 |  | Hyannis | MA | 2601 | 5088381260 | Superintendent |  | Siemens | Breaker | siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2024-05-20 | 2024-07-08 | 99 Wilkens Lane, Unit 3432 |  | Hyannis | MA | 2601 | breaker trips when range is turned on | Whirlpool | WEE515SOLS2 |  | apartment | kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989085944
2024-10-01 12:37 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-01 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1112 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989261447
2024-10-01 12:40 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-01 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1114 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989277451
2024-10-01 12:43 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-01 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1115 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989299030
2024-10-01 12:44 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-01 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1120 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989309848
2024-10-01 12:49 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-01 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1122 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989339911
2024-10-01 12:51 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-01 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1124 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989349617
2024-10-01 12:52 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-01 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1126 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989359131
2024-10-01 12:54 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-01 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1130 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989368090
2024-10-01 12:55 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-01 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1132 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16989378615
2024-10-01 13:14 | Liniker | Goncalves | 22803 | 222 Turnpike Road SUITE 13 |  | Westborough | MA | 1581 | 8578884280 | owner |  | LB230-G | Breaker | na | 50 |  | 2 Pole | Leviton | Residence |  | 2024-10-01 | 2024-09-05 | 10-18 Bowdoin Street |  | Dorchester | MA | 2121 | total of 35 Breakers is tripping, all wiring and inspections have passed. | GE appliances | JB256DMWW | no | multifamily | kitchen stove | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16989498684
2024-10-02 09:19 | Timothy | Chapman | 54722 | 10 Beacon Ct |  | Clinton | MA | 1510 | 7742877470 | Owner |  | Seimens | Breaker | No other | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-25 | 2024-09-25 | [5 empty] | Electrical Oven | Kenmore | AER6303MMS |  | Home | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/16994399764
2024-10-02 10:43 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1403 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16994938963
2024-10-02 10:45 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1405 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16994948891
2024-10-02 10:47 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1409 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16994958531
2024-10-02 10:49 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1410 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16994971695
2024-10-02 10:51 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1411 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16994982511
2024-10-02 10:53 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1414 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16994995528
2024-10-02 10:54 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1415 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16995006265
2024-10-02 10:56 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1417 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16995016196
2024-10-02 10:58 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1421 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16995025695
2024-10-02 10:59 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1425 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16995037311
2024-10-02 11:01 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1426 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16995048276
2024-10-02 11:03 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1427 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16995059444
2024-10-02 11:04 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1428 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16995069552
2024-10-02 11:06 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1430 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16995081275
2024-10-02 11:08 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1431 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16995091958
2024-10-02 11:10 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-02 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1432 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/16995101249
2024-10-02 12:24 | Iury | Silvestre | 58685 | 85 Linden St | Apt. 4 | Everett | MA | 2149 | 8572932758 | Journeyman Electrician |  | Siemens | Breaker | None | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-01 | 2024-04-10 | Range in kitchen |  | 96 Waltham St, Boston | MA | 2118 | When oven and cooking element are both turned on after a while the 50A GFCI breaker trips. | Wolf | IR36550/S/T | No, its a dedicated circuit | Condo | Only range in kitchen is affected, the 50A circuit is dedicated to range. | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16995571104
2024-10-02 20:53 | michael | young | 36570 | 9 royal crest dr |  | north andover | MA | 1845 | 6176991363 | Eletrician |  | siemens | Breaker | gfci | 50 |  | 2 Pole | Siemens | Residence |  | 2024-09-02 | 2024-09-03 | [5 empty] | Cooktop doesn't work with GFCI Breaker | fisher & paykel | c1365dtb |  | Kitchen | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/16998368356
2024-10-03 06:22 | DAVID | DEGRAZIA | 17119 | P.O. BOX 299 |  | E. FREETOWN | MA | 2717 | 5085420179 | Master Electrician |  | Siemens | Breaker | na | 30 |  | 2 Pole | Siemens | Residence |  | 2024-06-24 | 2024-06-04 | 5 Kingsley Way |  | Rehoboth | MA | 2769 | when appliance is turned on circuits are tripped shortly thereafter this is an on going problem | Speed Queen dryer | ADEE9B4S178TW01 | NA | LAUNDRY ROOM | LAUNDRY ROOM | No | No | No | No |  | https://www.formstack.com/admin/download/file/16999478723
2024-10-03 06:28 | DAVID | DEGRAZIA | 17119 | P.O. BOX 299 |  | E. FREETOWN | MA | 2717 | 5085420179 | MASTER ELECTRICIAN |  | SIEMENS | Breaker | NA | 50 | NA | 2 Pole | Siemens | Residence |  | 2024-06-24 | 2024-06-04 | 5 Kingsley Way |  | Rehoboth | MA | 2769 | WHEN APPLIANCE IS TURNED ON BREAKER TRIPS SHORTLY THEREAFTER | WHIRLPOOL RANGE | WOES5030L201 | NA | KITCHEN | KITCHEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/16999489055
2024-10-03 08:57 | William | Whalen | 11255 | 27 sandra ln |  | Weymouth | MA | 2188 | 7817066908 | Electrician |  | Square d qo | Breaker | None | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-09-13 | 7 baileys causway |  | Scituate | MA |  | Breaker keeps tripping during warm up ¦¦Had manufacturer send out a technician and nothing is wrong with equipment | Wolf | Df-48850/s/p |  | Kitchen | Kitchen range cant cook | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/16999899813 | https://www.formstack.com/admin/download/file/16999899814
2024-10-03 10:39 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1301 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000474231
2024-10-03 10:40 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1305 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000485207
2024-10-03 10:42 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1307 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000494327
2024-10-03 10:43 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1308 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000501138
2024-10-03 10:45 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1309 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000512144
2024-10-03 10:48 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1310 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000529804
2024-10-03 10:50 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1311 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000540142
2024-10-03 10:56 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1312 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000575708
2024-10-03 10:58 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1313 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000586124
2024-10-03 11:00 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1314 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000596234
2024-10-03 11:27 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1315 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000759652
2024-10-03 11:35 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1317 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000806961
2024-10-03 11:37 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1319 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000815084
2024-10-03 11:38 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1320 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000822891
2024-10-03 11:39 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1321 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000829474
2024-10-03 11:40 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1324 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000835812
2024-10-03 11:41 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1325 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000845092
2024-10-03 11:43 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1328 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000854546
2024-10-03 11:44 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-03 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1332 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17000862332
2024-10-06 11:49 | MICHAEL | BELL | 17374 | PO Box 1038 | 33 Davis Street | Plymouth | MA | 2362 | 5082948148 | Master Electrician/president |  | Eaton BR 250GFCI | Breaker | NONE | 50 |  | 2 Pole | Eaton | Residence |  | 2024-09-20 | 2024-09-20 | 25 Thomas Avenue |  | Plymouth | MA | 2360 | 48"" Dual fuel Wolf range. When oven is turned on, breaker trips. Tried multiple breakers, problem persists. Install a non GFI (standard breaker) and range works perfectly | Wolf | DF48650G/S/P | NONE | Single family | Kitchen range | No | No | No | No |  | https://www.formstack.com/admin/download/file/17013677413
2024-10-07 09:25 | Mark | Thibault | 14667 | 1 Industrial Way Unit # 5 |  | Tyngsboro | MA | 1879 | 978-226-5946 | President |  | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-03 | 280 Martins Landing Unit # 306 |  | North Reading | MA | 1864 | While warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17016244683
2024-10-07 09:25 | Mark | Thibault | 14667 | 1 Industrial Way Unit # 5 |  | Tyngsboro | MA | 1879 | 978-226-5946 | President |  | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-03 | 280 Martins Landing Unit # 306 |  | North Reading | MA | 1864 | While warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17016246094
2024-10-07 09:33 | Mark | Thibault | 14667 | 1 Industrial Way Unit # 5 |  | Tyngsboro | MA | 1879 | 978-226-5946 | President |  | Schneider HOM250GFI | Breaker | N/A | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-03 | 15 Archer Drive |  | Woburn | MA | 1801 | When warming oven | Whirlpool | K0CE500ESS23 |  | Town House | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17016291866
2024-10-07 11:03 | Mark | Thibault | 14667 | 1 Industrial Way Unit # 5 |  | Tyngsboro | MA | 1879 | 978-226-5946 | President |  | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-07 | 2 Winslow Lane Unit # 104 |  | Grafton | MA | 1536 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17016861806
2024-10-07 11:15 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17016942154 | 2024-08-13 | 2023-09-15 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI breakers are tripping simultaneously between 11pm-2am once a month since building started to become occupied with residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #201 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17016942167 | https://www.formstack.com/admin/download/file/17016942168
2024-10-07 11:22 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17016982080 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI breakers are tripping simultaneously between 11pm-2am once a month since building started to become occupied with residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #201 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17016982105 | https://www.formstack.com/admin/download/file/17016982108
2024-10-07 11:30 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17017039130 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI breakers are tripping simultaneously between 11pm-2am once a month since building started to become occupied with residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | All 2-pole GFCI breakers are tripping simultaneously between 11pm-2am once a month since building started to become occupied with residents over the last 1.5 years. | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17017039143 | https://www.formstack.com/admin/download/file/17017039144
2024-10-07 11:36 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17017078127 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI breakers are tripping simultaneously between 11pm-2am once a month since building started to become occupied with residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #202 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17017078141 | https://www.formstack.com/admin/download/file/17017078142
2024-10-07 12:15 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17017333096 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI breakers are tripping simultaneously between 11pm-2am once a month since building started to become occupied with residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit 203 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17017333112 | https://www.formstack.com/admin/download/file/17017333113
2024-10-07 12:20 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17017363899 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI breakers are tripping simultaneously between 11pm-2am once a month since building started to become occupied with residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #203 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17017363912 | https://www.formstack.com/admin/download/file/17017363913
2024-10-07 12:30 | Joseph | Spinale | 38463 | 28 Turner Dr |  | North Reading | MA | 1864 | 6178772227 | Owner |  | Schneider Square D Homeline. HOM240GFIC | Breaker | HOM240GFIC | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-03 | 2024-10-02 | 34 Powder House Blvd |  | Somerville | MA |  | The breaker will not hold. Once you turn on Breaker it trips immediatly even without turning the Oven on. We tried a 2nd breaker and same problem. Checked the wiring of Range cord and Range and all wiring is correct. The neutral and ground is separated, there is no strap either. | Boch | HIS8655U | None | 2 Family Residential home | Only Range | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/17017431445
2024-10-07 12:32 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1112 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017442261
2024-10-07 12:34 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1114 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017453966
2024-10-07 12:36 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1115 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017462905
2024-10-07 12:37 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1120 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017473445
2024-10-07 12:39 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1122 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017482450
2024-10-07 12:40 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1124 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017492263
2024-10-07 12:42 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1126 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017501858
2024-10-07 12:44 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1130 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017511500
2024-10-07 12:45 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1132 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017521605
2024-10-07 12:47 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1201 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017530003
2024-10-07 12:48 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1205 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017538507
2024-10-07 12:49 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1212 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017547440
2024-10-07 12:51 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1213 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017555857
2024-10-07 12:52 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1215 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017565350
2024-10-07 12:54 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1217 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017574470
2024-10-07 12:55 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1220 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017583698
2024-10-07 12:57 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1221 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017591989
2024-10-07 12:58 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1222 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017603010
2024-10-07 13:00 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1223 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017611829
2024-10-07 13:03 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1224 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017629384
2024-10-07 13:04 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1226 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017638417
2024-10-07 13:06 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1227 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017648986
2024-10-07 13:08 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1228 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017657841
2024-10-07 13:09 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-07 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 1231 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17017665809
2024-10-07 14:10 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17018045094 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #204 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17018045107 | https://www.formstack.com/admin/download/file/17018045108
2024-10-07 14:14 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17018073187 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #204 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17018073200 | https://www.formstack.com/admin/download/file/17018073201
2024-10-07 14:18 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 401-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17018101114 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #205 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17018101133 | https://www.formstack.com/admin/download/file/17018101134
2024-10-07 14:22 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17018124462 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU2402SS |  | Apartment Building | Unit #205 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17018124475 | https://www.formstack.com/admin/download/file/17018124476
2024-10-07 14:30 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17018173177 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #206 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17018173190 | https://www.formstack.com/admin/download/file/17018173191
2024-10-07 14:35 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17018204521 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #206 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17018204534 | https://www.formstack.com/admin/download/file/17018204535
2024-10-07 14:40 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17018234065 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #207 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17018234078 | https://www.formstack.com/admin/download/file/17018234079
2024-10-07 14:43 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17018258571 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #207 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17018258584 | https://www.formstack.com/admin/download/file/17018258585
2024-10-07 14:48 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17018289199 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #208 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17018289212 | https://www.formstack.com/admin/download/file/17018289213
2024-10-07 14:52 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17018315596 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #208 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17018315609 | https://www.formstack.com/admin/download/file/17018315610
2024-10-07 16:48 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17019053264 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #209 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17019053277 | https://www.formstack.com/admin/download/file/17019053278
2024-10-07 16:51 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17019071712 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #209 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17019071725 | https://www.formstack.com/admin/download/file/17019071726
2024-10-07 17:24 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17019250780 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #210 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17019250793 | https://www.formstack.com/admin/download/file/17019250794
2024-10-07 17:27 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17019264072 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #210 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17019264085 | https://www.formstack.com/admin/download/file/17019264086
2024-10-08 08:12 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2400 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021397839
2024-10-08 08:13 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2404 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021401235
2024-10-08 08:15 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2405 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021405806
2024-10-08 08:16 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2406 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021410869
2024-10-08 08:17 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2407 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021415593
2024-10-08 08:18 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2408 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021419707
2024-10-08 08:20 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2412 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021424528
2024-10-08 08:21 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2414 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021428519
2024-10-08 08:22 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2415 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021433535
2024-10-08 08:23 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . |  |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2416 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021438082
2024-10-08 08:32 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2417 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021472107
2024-10-08 08:35 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2418 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021483846
2024-10-08 08:41 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2419 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021505522
2024-10-08 08:42 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2420 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17021509691
2024-10-08 10:33 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2421 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022067806
2024-10-08 10:34 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2422 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022074231
2024-10-08 10:35 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2423 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022081330
2024-10-08 10:37 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2424 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022089005
2024-10-08 10:38 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2426 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022095769
2024-10-08 10:39 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2428 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022103274
2024-10-08 10:40 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . |  |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2429 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022110849
2024-10-08 10:41 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2430 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022117136
2024-10-08 10:42 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022119230 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #211 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022119243 | https://www.formstack.com/admin/download/file/17022119244
2024-10-08 10:42 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2431 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022123847
2024-10-08 10:44 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2432 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022131932
2024-10-08 10:44 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022136156 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #211 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022136169 | https://www.formstack.com/admin/download/file/17022136170
2024-10-08 10:45 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2433 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022138081
2024-10-08 10:51 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | Tyngsboro | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 4101 Codman Way |  | Wetsborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022174556
2024-10-08 10:53 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022185264 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #301 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022185277 | https://www.formstack.com/admin/download/file/17022185278
2024-10-08 10:55 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 4102 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022197736
2024-10-08 10:56 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022203091 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #301 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022203109 | https://www.formstack.com/admin/download/file/17022203111
2024-10-08 11:00 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1103 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022223433
2024-10-08 11:03 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1104 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022242136
2024-10-08 11:03 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022244419 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #302 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022244432 | https://www.formstack.com/admin/download/file/17022244433
2024-10-08 11:07 | Mark | Thibault | 14467 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1105 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022264309
2024-10-08 11:08 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022272483 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #302 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022272499 | https://www.formstack.com/admin/download/file/17022272501
2024-10-08 11:13 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1106 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022300414
2024-10-08 11:15 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1107 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022315719
2024-10-08 11:18 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1108 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022332152
2024-10-08 11:19 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022339183 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #303 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022339196 | https://www.formstack.com/admin/download/file/17022339197
2024-10-08 11:22 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022363289 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | GE Appliances | JKS3000SN1SS |  | Apartment Building | Unit #303 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022363302 | https://www.formstack.com/admin/download/file/17022363303
2024-10-08 11:27 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022391082 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #304 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022391101 | https://www.formstack.com/admin/download/file/17022391102
2024-10-08 11:27 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1109 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022391972
2024-10-08 11:28 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2434 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022399731
2024-10-08 11:29 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2435 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022406204
2024-10-08 11:30 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022408033 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #304 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022408046 | https://www.formstack.com/admin/download/file/17022408047
2024-10-08 11:31 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . |  |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2436 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022414911
2024-10-08 11:32 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1110 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022419032
2024-10-08 11:32 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2438 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022421573
2024-10-08 11:38 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2440 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022456206
2024-10-08 11:39 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2441 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022463108
2024-10-08 11:39 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022463353 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #305 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022463366 | https://www.formstack.com/admin/download/file/17022463367
2024-10-08 11:40 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2442 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022472165
2024-10-08 11:42 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022478674 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #305 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022478687 | https://www.formstack.com/admin/download/file/17022478688
2024-10-08 11:42 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2443 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022478724
2024-10-08 11:43 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2444 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022485344
2024-10-08 11:45 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2445 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022497397
2024-10-08 11:46 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2446 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022505622
2024-10-08 11:46 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022507803 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #306 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022507816 | https://www.formstack.com/admin/download/file/17022507817
2024-10-08 11:47 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2447 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022512376
2024-10-08 11:48 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2448 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022520148
2024-10-08 11:49 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2449 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022526806
2024-10-08 11:50 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-08 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2450 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022533413
2024-10-08 11:51 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1111 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022534842
2024-10-08 11:57 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022576517 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #306 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022576530 | https://www.formstack.com/admin/download/file/17022576531
2024-10-08 11:59 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1112 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022590800
2024-10-08 12:00 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022596836 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #307 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022596853 | https://www.formstack.com/admin/download/file/17022596854
2024-10-08 12:01 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1113 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022602507
2024-10-08 12:06 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022633378 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #307 - Laundry Closet¦¦(*corrected file attachments from previous submission) | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022633391 | https://www.formstack.com/admin/download/file/17022633392
2024-10-08 12:08 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022649534 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #307 - Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022649547
2024-10-08 12:12 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022672280 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #308 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022672293 | https://www.formstack.com/admin/download/file/17022672294
2024-10-08 12:14 | Mark | Thibault | 14467 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1201 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022685291
2024-10-08 12:15 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022692589 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #308 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022692615 | https://www.formstack.com/admin/download/file/17022692616
2024-10-08 12:16 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1202 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022697471
2024-10-08 12:18 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1203 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022709413
2024-10-08 12:18 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022712846 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #309 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022712859 | https://www.formstack.com/admin/download/file/17022712860
2024-10-08 12:21 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022728725 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #309 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022728749 | https://www.formstack.com/admin/download/file/17022728750
2024-10-08 12:25 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022751746 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #310 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022751759 | https://www.formstack.com/admin/download/file/17022751760
2024-10-08 12:27 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022766478 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #310 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022766491 | https://www.formstack.com/admin/download/file/17022766492
2024-10-08 12:39 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1204 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022841784
2024-10-08 12:41 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1205 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022854416
2024-10-08 12:41 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022854444 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #311 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022854457 | https://www.formstack.com/admin/download/file/17022854458
2024-10-08 12:44 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022868135 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #311 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022868148 | https://www.formstack.com/admin/download/file/17022868149
2024-10-08 12:44 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1206 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022869078
2024-10-08 12:46 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1207 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022880946
2024-10-08 12:50 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1208 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022904909
2024-10-08 12:50 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022905285 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #401 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022905298 | https://www.formstack.com/admin/download/file/17022905299
2024-10-08 12:52 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1209 Codman Way |  | Westborough | MA | 1581 | Kitchen | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022917903
2024-10-08 12:52 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022918866 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #401 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022918879 | https://www.formstack.com/admin/download/file/17022918880
2024-10-08 12:54 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1210 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whrilpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022930011
2024-10-08 12:55 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022937416 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #402 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022937429 | https://www.formstack.com/admin/download/file/17022937430
2024-10-08 12:58 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17022952175 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #402 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17022952188 | https://www.formstack.com/admin/download/file/17022952189
2024-10-08 13:01 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1211 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022972478
2024-10-08 13:03 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1212 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022984494
2024-10-08 13:05 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1213 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17022996531
2024-10-08 13:07 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1301 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023007790
2024-10-08 13:10 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1302 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023020918
2024-10-08 13:12 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1303 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023033104
2024-10-08 13:14 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1304 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023046398
2024-10-08 13:17 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1305 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023063698
2024-10-08 13:18 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023069154 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #403 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023069167 | https://www.formstack.com/admin/download/file/17023069168
2024-10-08 13:20 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1306 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023079725
2024-10-08 13:21 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023088381 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | GE Appliances | JKS3000SN1SS |  | Apartment Building | Unit #403 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023088394 | https://www.formstack.com/admin/download/file/17023088395
2024-10-08 13:22 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1307 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023093065
2024-10-08 13:24 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1308 Codman Way |  | Westborough | MA | 1581 | Kitchen | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023104701
2024-10-08 13:25 | Matthew | Dennen | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 5083886169 | Owner/President |  | Attached to file | Breaker | n/a | 50 | 30 | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17023112004 | 2024-07-31 | 2024-07-02 | [5 empty] | When oven ranges have the loads going through, the AFCI breakers are tripping | GE | On attached file |  | Multi unit renovated residential | Kitchen | No | Yes | No | No | https://www.formstack.com/admin/download/file/17023112016 | https://www.formstack.com/admin/download/file/17023112017
2024-10-08 13:27 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023123631 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #404 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023123656 | https://www.formstack.com/admin/download/file/17023123658
2024-10-08 13:27 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1309 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023128951
2024-10-08 13:29 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023138746 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #404 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023138759 | https://www.formstack.com/admin/download/file/17023138760
2024-10-08 13:29 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1310 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023139983
2024-10-08 13:31 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1311 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023152309
2024-10-08 13:33 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1312 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023163616
2024-10-08 13:35 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1401 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023176673
2024-10-08 13:37 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1402 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023188859
2024-10-08 13:39 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1403 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023200130
2024-10-08 13:41 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1404 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023214367
2024-10-08 13:43 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1405 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023226661
2024-10-08 13:45 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1406 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023238104
2024-10-08 13:47 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1407 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023251077
2024-10-08 13:49 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023258593 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #405 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023258606 | https://www.formstack.com/admin/download/file/17023258607
2024-10-08 13:50 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1408 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023264812
2024-10-08 13:51 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023272408 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #405 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023272421 | https://www.formstack.com/admin/download/file/17023272422
2024-10-08 13:51 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1409 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023276626
2024-10-08 13:53 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1410 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023288238
2024-10-08 13:55 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1411 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023300787
2024-10-08 13:57 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-01 | 2024-10-04 | 1412 Codman Way |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE975H0H24 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17023312836
2024-10-08 14:19 | Donal | McNulty | 21286 | 51 main St |  | Norwell | MA | 2061 | 617-293-4525 | Owner/President |  | AG83B00L H00BY3 50Q-R | Breaker | GFCI breaker | 20 |  | 2 Pole | Siemens | Commercial | https://www.formstack.com/admin/download/file/17023443305 | 2024-10-07 | 2024-02-23 | 72 Burbank St |  | Boston | MA | 2115 | ADA wall ovens trip required GFCI circuit breaker in apartment units 202, 302, 503. | General Electric | VV118720Q | N/A | Kitchen of apartment, ADA unit | These are located in the kitchen of three ADA (Group 2) new construction rental apartment units. | No | No | Yes | No | https://www.formstack.com/admin/download/file/17023443319 | https://www.formstack.com/admin/download/file/17023443320
2024-10-08 14:21 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023459837 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #406 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023459856 | https://www.formstack.com/admin/download/file/17023459858
2024-10-08 14:24 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023475202 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | GE Appliances | JKS3000SN1SS |  | Apartment Building | Unit #406 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023475215 | https://www.formstack.com/admin/download/file/17023475216
2024-10-08 14:26 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023491440 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #407 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023491453 | https://www.formstack.com/admin/download/file/17023491454
2024-10-08 14:29 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023505507 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #407 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023505520 | https://www.formstack.com/admin/download/file/17023505521
2024-10-08 14:31 | Donal | McNulty | 21286 | 51 MainSt |  | Norwell | MA | 2061 | 617-293-4525 | Owner/President |  | AG83B00L H00BY3 50Q-R | Breaker | GFCI breaker | 50 |  | 2 Pole | Siemens | Commercial | https://www.formstack.com/admin/download/file/17023521758 | 2024-10-04 | 2024-02-23 | 72 Burbank St |  | Boston | MA | 2115 | GFCI breaker trips in 24x apartment units when stove/range is turned on (within 30 seconds to 1 minute).¦¦affects units B01, B02, 101, 102, 201, 203, 204, 205, 301, 303, 304, 305, 401, 402, 403, 404, 405, 501, 502, 504, 601, 602, 603, 604 | General Electric | JB258RT5SS | N/A | Apartment | kitchen. only the appliance is affected. this occurs in 24 apartments in the building as noted above. | No | No | Yes | No | https://www.formstack.com/admin/download/file/17023521772 | https://www.formstack.com/admin/download/file/17023521773
2024-10-08 14:32 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023528891 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #407 - Kitchen¦¦(*correction of last entry) | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023528904 | https://www.formstack.com/admin/download/file/17023528905
2024-10-08 14:35 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023548174 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #408 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023548187 | https://www.formstack.com/admin/download/file/17023548188
2024-10-08 14:37 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023560236 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #408 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023560249 | https://www.formstack.com/admin/download/file/17023560250
2024-10-08 14:40 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023577811 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #409 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023577824 | https://www.formstack.com/admin/download/file/17023577825
2024-10-08 14:42 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023592297 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #409 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023592321 | https://www.formstack.com/admin/download/file/17023592323
2024-10-08 14:47 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023621779 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #410 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023621792 | https://www.formstack.com/admin/download/file/17023621793
2024-10-08 14:49 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023637763 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #410 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023637776 | https://www.formstack.com/admin/download/file/17023637777
2024-10-08 14:58 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023688753 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #411 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023688770 | https://www.formstack.com/admin/download/file/17023688771
2024-10-08 15:00 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023703250 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #411 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023703263 | https://www.formstack.com/admin/download/file/17023703264
2024-10-08 15:06 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023753356 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #501 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023753371 | https://www.formstack.com/admin/download/file/17023753372
2024-10-08 15:08 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023768966 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #501 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023768981 | https://www.formstack.com/admin/download/file/17023768982
2024-10-08 15:14 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023809410 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #502 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023809423 | https://www.formstack.com/admin/download/file/17023809424
2024-10-08 15:16 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17023826082 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #502 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17023826100 | https://www.formstack.com/admin/download/file/17023826101
2024-10-08 15:44 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024010068 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #503 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024010087 | https://www.formstack.com/admin/download/file/17024010088
2024-10-08 15:47 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB50 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024025600 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #503 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024025613 | https://www.formstack.com/admin/download/file/17024025614
2024-10-08 16:00 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial |  | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #504 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024106339 | https://www.formstack.com/admin/download/file/17024106340
2024-10-08 16:02 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB50 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024118878 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #504 - Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17024118891
2024-10-08 16:20 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024224417 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #505 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024224430 | https://www.formstack.com/admin/download/file/17024224431
2024-10-08 16:22 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024236739 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #505 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024236752 | https://www.formstack.com/admin/download/file/17024236753
2024-10-08 16:25 | Lucas | Lowney | 22857 | 35 Hill Drive | Douglas Pike 1st Floor Rear | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024257195 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #506 - Laundry Closed | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024257208 | https://www.formstack.com/admin/download/file/17024257209
2024-10-08 16:28 | Lucas | Lowney | 22857 | 35 Hill Drive | Douglas Pike 1st Floor Rear | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024273302 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #506 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024273315 | https://www.formstack.com/admin/download/file/17024273316
2024-10-08 16:31 | Lucas | Lowney | 22857 | 35 Hill Drive | Douglas Pike 1st Floor Rear | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024291780 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #507 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024291793 | https://www.formstack.com/admin/download/file/17024291794
2024-10-08 16:40 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024342773 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #507 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024342786 | https://www.formstack.com/admin/download/file/17024342787
2024-10-08 16:44 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024362665 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #508 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024362678 | https://www.formstack.com/admin/download/file/17024362679
2024-10-08 16:46 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024374893 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #508 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024374906 | https://www.formstack.com/admin/download/file/17024374907
2024-10-08 17:06 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024488813 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #509 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024488826 | https://www.formstack.com/admin/download/file/17024488827
2024-10-08 17:09 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024500734 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #509 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024500747 | https://www.formstack.com/admin/download/file/17024500748
2024-10-08 17:19 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024554370 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #510 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024554383 | https://www.formstack.com/admin/download/file/17024554384
2024-10-08 17:22 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024567217 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #510 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024567230 | https://www.formstack.com/admin/download/file/17024567231
2024-10-08 17:29 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024604387 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #511 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024604400 | https://www.formstack.com/admin/download/file/17024604401
2024-10-08 17:32 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17024616108 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #511 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17024616121 | https://www.formstack.com/admin/download/file/17024616122
2024-10-09 11:00 | Joseph | Spinale | 38463 | 28 Turner Dr |  | North Reading | MA | 1864 | 6178772227 | President |  | HOM240GFIC | Breaker | NO | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-07 | 2024-10-03 | 34 Powder House Blvd |  | Somerville | MA |  | Breaker will not hold. Breaker trips immediately once turned on. Checked all wiring including the cord to insure the neutral and ground were separated and everything is correct. Replaced the breaker and still does not hold. | Bosh | HIS8655U | NO | 2 FAMILY HOME | ONLY THE RANGE ON THIS BRANCH CIRCUIT | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/17027500126
2024-10-09 11:02 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17027513379 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #601 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17027513394 | https://www.formstack.com/admin/download/file/17027513395
2024-10-09 11:05 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17027528272 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #601 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17027528285 | https://www.formstack.com/admin/download/file/17027528286
2024-10-09 11:12 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17027572977 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #602 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17027572990 | https://www.formstack.com/admin/download/file/17027572991
2024-10-09 11:21 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17027629807 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #602 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17027629820 | https://www.formstack.com/admin/download/file/17027629821
2024-10-09 12:04 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17027906786 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #604 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17027906799 | https://www.formstack.com/admin/download/file/17027906800
2024-10-09 12:07 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17027930007 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #604 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17027930020 | https://www.formstack.com/admin/download/file/17027930021
2024-10-09 12:11 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17027952803 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #605 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17027952821 | https://www.formstack.com/admin/download/file/17027952822
2024-10-09 12:14 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17027970723 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #605 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17027970741 | https://www.formstack.com/admin/download/file/17027970742
2024-10-09 12:18 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17028001342 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #606 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17028001359 | https://www.formstack.com/admin/download/file/17028001360
2024-10-09 12:21 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17028015918 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #606 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17028015931 | https://www.formstack.com/admin/download/file/17028015932
2024-10-09 12:24 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17028046056 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #607 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17028046069 | https://www.formstack.com/admin/download/file/17028046070
2024-10-09 12:27 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17028066667 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #607 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17028066685 | https://www.formstack.com/admin/download/file/17028066686
2024-10-09 12:29 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17028078708 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #607 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17028078721 | https://www.formstack.com/admin/download/file/17028078722
2024-10-09 12:32 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17028105275 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #608 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17028105288 | https://www.formstack.com/admin/download/file/17028105289
2024-10-09 12:34 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17028117545 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #608 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17028117558 | https://www.formstack.com/admin/download/file/17028117559
2024-10-09 12:42 | [11 empty] | North Shore Safety Ltd./CAT NO.: PGFS-56107/ SERIAL NO.: 090324 768 | Relay/Contactor | permanent GFCI protection | 60 |  | 3 Pole | Industrial | Commercial | https://www.formstack.com/admin/download/file/17028163178 | 2024-10-07 | 2024-09-06 | [5 empty] | The blower motor for the oven, controlled by a VFD, was causing unwanted GFCI trips to voltage leakage to ground. A Rational technician verified this issue and concluded that the oven cannot operate properly with a GFCI in place. | Rational | CC1ERRA.0000219 |  | commercial bakery | kitchen area | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17028163190 | https://www.formstack.com/admin/download/file/17028163191
2024-10-09 13:27 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2300 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028448788
2024-10-09 13:30 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2302 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028465493
2024-10-09 13:31 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2303 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028474856
2024-10-09 13:33 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2304 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028484106
2024-10-09 13:34 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2305 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028492966
2024-10-09 13:47 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2306 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028568867
2024-10-09 13:49 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2307 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028579718
2024-10-09 13:50 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2308 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028589236
2024-10-09 13:52 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2309 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028597598
2024-10-09 13:53 | Montana | Darisse | 2999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2310 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028607714
2024-10-09 13:54 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2312 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028615036
2024-10-09 13:56 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2314 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028626455
2024-10-09 13:58 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2315 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028635135
2024-10-09 13:59 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2316 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028644220
2024-10-09 14:01 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2317 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028654575
2024-10-09 14:02 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2318 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028662687
2024-10-09 14:03 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2319 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028670795
2024-10-09 14:04 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2320 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17028677903
2024-10-09 16:08 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17029455297 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #603 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17029455310 | https://www.formstack.com/admin/download/file/17029455311
2024-10-09 16:10 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17029468310 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #603 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17029468331 | https://www.formstack.com/admin/download/file/17029468333
2024-10-09 16:15 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17029493780 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #609 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17029493797 | https://www.formstack.com/admin/download/file/17029493798
2024-10-09 16:18 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17029513860 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU24202SS |  | Apartment Building | Unit #609 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17029513873 | https://www.formstack.com/admin/download/file/17029513874
2024-10-09 16:23 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17029546027 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #610 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17029546042 | https://www.formstack.com/admin/download/file/17029546043
2024-10-09 16:28 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17029574934 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #610 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17029574947 | https://www.formstack.com/admin/download/file/17029574948
2024-10-09 16:47 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB230 | Breaker | Thermal Mag | 30 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17029685640 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Whirlpool | WED560LHW2 |  | Apartment Building | Unit #611 - Laundry Closet | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17029685653 | https://www.formstack.com/admin/download/file/17029685654
2024-10-09 16:52 | Lucas | Lowney | 22857 | 35 Hill Drive |  | Johnston | RI | 2919 | 508-455-8547 | President |  | GFTCB250 | Breaker | Thermal Mag | 50 |  | 2 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17029714518 | 2024-08-13 | 2023-09-05 | 21 West 2nd St |  | Boston | MA | 2127 | All 2-pole GFCI Breakers are tripping simultaneously between 11pm-2am once a month since building starting to become occupied by residents over the last 1.5 years. | Blomberg | BERU30422SS |  | Apartment Building | Unit #611 - Kitchen | Yes | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17029714536 | https://www.formstack.com/admin/download/file/17029714537
2024-10-10 10:11 | Chris | Polny | 11660 | 325 Hopping Brook |  | Holliston | MA | 1746 | 7742178986 | VP Electrical Operations |  | Leviton LB250-G | Breaker | NA | 50 |  | 2 Pole | Leviton | Residence |  | 2024-10-09 | 2024-10-09 | 21Arraphoe Dr |  | Bellingham | MA | 2019 | Installed breaker and tested existing oven. While oven was heating breaker tripped. Installed¦standard breaker and ran oven for 30 mins. Re-intsalled GFCI breaker and tripped. Verified EGC¦of circuit and range | Hot point Range | Unknown |  | Single Family | Only Range in kitchen affected, nothing else | No | No | No | No |  | https://www.formstack.com/admin/download/file/17032401898
2024-10-10 12:30 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | Owner |  | Square D Homeline | Breaker | n/a | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-08 | 2024-03-08 | 114 DOWNS ROAD |  | GREAT BARRINGTON | MA | 1230 | Breaker does not hold, kept tripping. | WOLF | SO3050PM/S/P |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17033154123
2024-10-10 12:55 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-10 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2321 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17033293402
2024-10-10 12:57 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-10 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2322 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17033300828
2024-10-10 12:58 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-10 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2323 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17033309630
2024-10-10 13:00 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-10 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2324 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17033315744
2024-10-10 13:01 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-10 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2326 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17033322945
2024-10-10 13:02 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-10 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2328 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17033330324
2024-10-10 13:06 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-10 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2329 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17033355553
2024-10-10 13:08 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-10 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2330 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17033362549
2024-10-10 13:35 | Tony | Marroquin | 14426 | 57 Chamberlain St |  | Hokinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB230 | Breaker | N/A | 30 |  | 2 Pole | Eaton | Residence |  | 2024-08-26 | 2024-07-15 | [5 empty] | Dryer tripping with normal use. | Electrolux | ELFE7637AT0 |  | Single Family | Laundry Room | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17033520682
2024-10-10 13:39 | Tony | Marroquin | 14426 | 57 Chamberlain St |  | Hokinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-26 | 2024-07-15 | [5 empty] | Stove range tripping during normal use. | JennAir | JDRP5 48HL |  | Single Family | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17033545908
2024-10-10 13:40 | Tony | Marroquin | 14426 | 57 Chamberlain St |  | Hokinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-26 | 2024-07-15 | [5 empty] | Stove range tripping during normal use. | JennAir | JDRP5 48HL |  | Single Family | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17033549560
2024-10-10 17:11 | Michael | Giombetti | 13678 | 401 SOUTH STREET | Marlboro | MARLBOROUGH | MA | 1752 | 5084813299 | President |  | Eaton BR BRN250GF | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17034802468 | 2024-10-09 | 2024-10-04 | 17 Davis Road Unit C7 |  | Acton | MA | 1720 | Breaker randomly trips while using the stove | Whirlpool | WFC315SOJW4 | None | Apartment / Kitchen | Kitchen stove | No | No | No | No | https://www.formstack.com/admin/download/file/17034802482 | https://www.formstack.com/admin/download/file/17034802483
2024-10-11 13:41 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-11 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2331 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17039554960
2024-10-11 13:43 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-11 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2332 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17039565718
2024-10-11 13:45 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-11 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2333 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17039575503
2024-10-14 07:57 | Robert | Davidson | 17373 | 8 South St |  | Taunton | MA | 2780 | 7742539280 | Owner |  | BRN250GFCS | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-10-02 | 2024-10-03 | 693 main st |  | Hingham | MA | 2018 | Breaker trips when home owner uses oven | AGA | AEL481IN | None | Single family house | Kitchen range | No | No | No | No |  | https://www.formstack.com/admin/download/file/17047710275
2024-10-14 11:11 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2334 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17048718328
2024-10-14 11:13 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2335 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17048727592
2024-10-14 11:14 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2336 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17048735628
2024-10-14 11:15 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2338 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17048742089
2024-10-14 13:34 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2340 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17049681297
2024-10-14 13:37 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2341 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17049701475
2024-10-14 13:39 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2342 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17049709191
2024-10-14 13:40 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2344 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17049716189
2024-10-14 13:41 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2345 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17049723959
2024-10-14 13:42 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2346 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17049731378
2024-10-14 13:43 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2347 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17049737098
2024-10-14 13:44 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2348 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17049744584
2024-10-14 13:45 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2349 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17049753228
2024-10-14 13:46 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2350 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17049760817
2024-10-15 10:10 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-15 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2200 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17054144550
2024-10-15 10:11 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-15 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2202 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17054152522
2024-10-15 10:12 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-15 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2203 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17054160376
2024-10-15 10:13 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-15 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2204 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17054166561
2024-10-15 10:35 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-15 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2205 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17054298093
2024-10-15 10:36 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-15 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2206 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17054306168
2024-10-15 10:38 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-15 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2207 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17054316623
2024-10-15 10:39 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . |  |  | 2 Pole | Siemens | Residence |  | 2024-10-15 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2208 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17054322072
2024-10-15 10:40 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-15 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2209 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17054328105
2024-10-15 11:36 | Sean | Griffin | 14426 | 8 Pleasant Street Suite A2 |  | Natick | MA | 1760 | 7745719815 | Project Manager |  | Eaton BRN240GF | Breaker | Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2024-10-10 | 2024-09-20 | 22 Oxbow Road |  | Raynham | MA | 2767 | Breaker trips each time the range is turned on. | General Electric | GRF500PVSS |  | Residential | Range in kitchen trips breaker each time it is turned on | No | No | No | No |  | https://www.formstack.com/admin/download/file/17054716727
2024-10-15 11:40 | Sean | Griffin | 14426 | 8 Pleasant Street Suite A2 |  | Natick | MA | 1760 | 7745719815 | Project Manager |  | Eaton BRN240GF | Breaker | Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2024-10-15 | 2024-07-26 | 24 Oxbow Road |  | Raynham | MA | 2767 | Range trips breaker each time it is turned on | General Electric | JB655SKSS |  | Townhome | Range trips breaker each time it is turned on | No | No | No | No |  | https://www.formstack.com/admin/download/file/17054748256
2024-10-15 11:45 | Sean | Griffin | 14426 | 8 Pleasant Street Suite A2 |  | Natick | MA | 1760 | 7745719815 | Project Manager |  | BRN240GF | Breaker | Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2024-10-10 | 2024-09-26 | 26 Oxbow Road |  | Raynham | MA | 2767 | Range trips breaker | General Electric | GRF500PVSS |  | Townhome | Range trips breaker each time it is turned on | No | No | No | No |  | https://www.formstack.com/admin/download/file/17054790485
2024-10-16 07:03 | Daniel | Tremblay | 57161 | 187 Center Depot Road |  | Charlton | MA | 1507 | 6179092378 | owner |  | GE/THQL2130GFT | Breaker | GFCI | 30 |  | 2 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/17059651551 | 2024-10-04 | 2024-10-04 | 1010 Waltham Street Suite 600 apartment 487 Harvard |  | Lexington | MA | 2421 | The incident occurred upon delivery of the dryer appliance. The breaker holds and is fine with no load. The second the unit is plugged in the breaker trips instantly. All testing on breaker, appliance, wiring, and outlet has been done. | Whirlpool | WET4024HW0 |  | Laundry Room | The only location affected by the breaker tripping is in the laundry room. This issue is only with and dryer. | Yes | Yes | Yes | No | https://www.formstack.com/admin/download/file/17059651564 | https://www.formstack.com/admin/download/file/17059651565
2024-10-16 08:14 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2212 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059835657
2024-10-16 08:15 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2214 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059839790
2024-10-16 08:16 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2215 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059843252
2024-10-16 08:22 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2216 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059862667
2024-10-16 08:23 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2217 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059868378
2024-10-16 08:27 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2218 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059882977
2024-10-16 08:30 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2219 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059889969
2024-10-16 08:31 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2220 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059894035
2024-10-16 08:32 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2221 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059897610
2024-10-16 08:33 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2222 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059902346
2024-10-16 08:34 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2223 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059905859
2024-10-16 08:35 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2224 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059910032
2024-10-16 08:37 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2226 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059916187
2024-10-16 08:38 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2228 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059919569
2024-10-16 08:39 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2229 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059923076
2024-10-16 08:40 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2230 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059927510
2024-10-16 08:41 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2231 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059931580
2024-10-16 08:48 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2232 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059960635
2024-10-16 08:49 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2233 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059964919
2024-10-16 08:50 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2234 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059968247
2024-10-16 08:51 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2235 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059971622
2024-10-16 08:52 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2236 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059975498
2024-10-16 08:53 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2238 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059980044
2024-10-16 08:54 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2240 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059983629
2024-10-16 08:56 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2241 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059991074
2024-10-16 08:58 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2242 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17059997357
2024-10-16 08:59 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2243 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060003448
2024-10-16 09:00 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2244 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060007382
2024-10-16 09:01 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2245 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060011523
2024-10-16 09:02 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2246 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060015760
2024-10-16 09:04 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2247 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060020857
2024-10-16 09:07 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2248 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060035150
2024-10-16 09:10 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2249 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060047681
2024-10-16 09:11 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2250 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060053177
2024-10-16 09:13 | Christine | Miller | 60582 | 138 suffield st |  | Agawam | MA | 1001 | 3048014382 | Electrician |  | Homgfi240 | Breaker | 2pole | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-15 | 2024-10-10 | [5 empty] | Breaker tripped when stove was in use | General Electric | Eer3001k01ss | None | Single family | None | No | No | No | No | https://www.formstack.com/admin/download/file/17060060574 | https://www.formstack.com/admin/download/file/17060060575
2024-10-16 09:17 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2100 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060077905
2024-10-16 09:18 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2102 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060083531
2024-10-16 09:57 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2103 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060281533
2024-10-16 09:59 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2107 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060292459
2024-10-16 10:01 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2108 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060303766
2024-10-16 10:03 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2109 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060311310
2024-10-16 10:04 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2110 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060318257
2024-10-16 10:05 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2112 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060324751
2024-10-16 10:07 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2114 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060335108
2024-10-16 10:08 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2115 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060341180
2024-10-16 10:09 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2116 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060346754
2024-10-16 10:11 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2117 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060354222
2024-10-16 10:12 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2118 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060362735
2024-10-16 11:13 | John | Sousa | 12911 | 6 Russell RD |  | Lexington | MA | 2420 | 6178687734 | Electrician |  | GFTCB250 | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2024-10-02 | 2024-10-01 | 38 Wigglesworth Street Malden |  | Malden | MA | 2148 | When turning on top burners or oven circuit trips randomly | GE Range | jb6555dk9vww |  | Kitchen | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17060737566
2024-10-16 11:14 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2119 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060737849
2024-10-16 11:24 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2120 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060803688
2024-10-16 11:25 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2121 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060811848
2024-10-16 11:27 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2122 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060820393
2024-10-16 11:28 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2123 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060827423
2024-10-16 11:29 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2124 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060834372
2024-10-16 11:30 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2126 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060842139
2024-10-16 11:32 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2128 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060850006
2024-10-16 11:33 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2129 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060857484
2024-10-16 11:34 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2130 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060865129
2024-10-16 11:35 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2131 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060875215
2024-10-16 11:37 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2132 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060883472
2024-10-16 11:38 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2133 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060890354
2024-10-16 11:39 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2134 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060897982
2024-10-16 11:41 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2135 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060907051
2024-10-16 11:42 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2136 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060913883
2024-10-16 11:43 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2138 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060921824
2024-10-16 11:44 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2140 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060929127
2024-10-16 11:46 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2141 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060940243
2024-10-16 11:48 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2142 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060949340
2024-10-16 11:49 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2143 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060960165
2024-10-16 11:50 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2144 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060968059
2024-10-16 11:52 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2145 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060976651
2024-10-16 11:53 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2146 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060984048
2024-10-16 11:54 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2147 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17060991384
2024-10-16 11:55 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2148 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17061001130
2024-10-16 11:57 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2149 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17061013586
2024-10-16 11:59 | Montana | Darisse | 8999 | 1325 Washington Street |  | Weymouth | MA | 2189 | 6035082496 | Site Administrative Assistant |  | Siemens QF250A | Breaker | . | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-16 | 2024-06-14 | [5 empty] | While warming oven | Whirlpool | WEE515SOLS2 |  | Apartment | Unit 2150 | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17061024637
2024-10-17 11:19 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 6034906301 | President |  | Schneider/HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-10 | 2024-10-11 | 6209 Peters Farm Way |  | Westborough | MA | 1581 | When warming the oven | Whirlpool | WFE550S0LZ3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17067403813
2024-10-17 11:24 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | Schneider | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-10 | 2024-10-11 | 2 Winslow Lane Unit # 304 |  | Grafton | MA | 1536 | When warming oven | Whirlpool | WFE775H0H25 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17067437964
2024-10-17 11:28 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | SchneiderHOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-14 | 2024-10-15 | 280 Martins Landing Unit # 408 |  | North Reading | MA | 1864 | When warming oven | Whirlpool | WFE550S0LZ3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17067473113
2024-10-17 11:31 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | SchneiderHOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-09 | 2024-10-10 | 4 Stratton Drive Unit # 303 |  | Woburn | MA | 1801 | When warming oven | Whirlpool | WFE550S0LZ3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17067518912
2024-10-17 11:34 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | SchneiderHOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-09 | 2024-10-10 | 3109 Peters FarmWay |  | Westborough | MA | 1581 | When warming oven | Whirlpool | WFE550S0LZ3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17067556615
2024-10-17 11:38 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | SchneiderHOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-03 | 2024-10-04 | 2 Winslow Lane Unit # 104 |  | Grafton | MA | 1536 | When warming the oven | Whirlpool | WFE550S0LZ3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17067591568
2024-10-17 11:40 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President |  | SchneiderHOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-13 | 2024-10-14 | 260 Martins Landing Unit # 210 |  | North Reading | MA | 1864 | When warming the oven | Whirlpool | WFE550S0LZ3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17067629461
2024-10-17 14:11 | Tony | Marroquin | 14426 | 22 Whalen Rd |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2024-10-15 | 2024-02-04 | 58 Chamberlain st |  | Hopkinton | MA | 1748 | Built in wall oven trips with normal use. | Kitchen Aid | KOSE500ESS | none | single family home | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17068636399
2024-10-17 14:17 | Tony | Marroquin | 14426 | 22 Whalen Rd |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager |  | Eaton | Breaker | N/A | 30 | None | 2 Pole | Eaton | Residence |  | 2024-10-15 | 2024-09-25 | 58 Chamberlain st |  | Hopkinton | MA | 1748 | Dryer trips with normal use. | Whirlpool | WED6605MW | None | Single Family Home | Laundry Room | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17068720551
2024-10-21 11:44 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-21 | 2024-06-21 | Village green 1 |  | East longmeadow | MA | 1028 | Stove would trip after 5 minutes of use. | Amana | W10175656 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17084367437
2024-10-21 11:53 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D Homeline AD-910 | Breaker | Square D Homeline AD-9109 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-15 | 2024-06-15 | Village green 14 |  | East longmeadow | MA | 1028 | Stove tripped after 5 minutes of use. | Hotpoint | 317B6641P001 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17084448376
2024-10-21 12:46 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7869 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline Ad-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-21 | 2024-06-21 | Village green 8 |  | East Longmeadow | MA | 1028 | Stove would trip after 1 minute of use. | Amana | W10175656 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17084826450
2024-10-21 12:52 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-28 | 2024-08-28 | Village green 20 |  | East Longmeadow | MA | 1028 | Stove tripped after 7 minutes of use. | Hotpoint | 317B9044P010 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17084865640
2024-10-21 12:59 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-26 | 2024-08-26 | Village green 17 |  | East Longmeadow | MA | 1028 | Stove tripped after 2 minutes of use. | Amana | W10175656 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17084910063
2024-10-21 13:04 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-26 | 2024-08-26 | Village green 25 |  | East Longmeadow | MA | 1028 | Stove tripped after 2 minutes of use. | Amana | W10175656 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17084944858
2024-10-21 13:26 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-23 | 2024-08-23 | 19 village green |  | East Longmeadow | MA | 1028 | Stove tripped after 2 minutes of use. | Amana | W10406469 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085091575
2024-10-21 13:33 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-22 | 2024-08-22 | 18 village green |  | East Longmeadow | MA | 1028 | Stove tripped after 5 minutes of use. | Hotpoint | 317B6641P001 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085138819
2024-10-21 13:38 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-14 | 2024-08-14 | 15 village green |  | East Longmeadow | MA | 1028 | Stove tripped after 1 minute of use. | Amana | W10406469 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085170361
2024-10-21 13:43 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-13 | 2024-08-13 | 16 village green |  | East Longmeadow | MA | 1028 | Stove tripped after 1 minute of use. | Amana | W10406469 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085208672
2024-10-21 13:48 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-09 | 2024-08-09 | 26 village green |  | East Longmeadow | MA | 1028 | Stove tripped after 1 minute of use. | Hotpoint | 223C3022P006 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085238151
2024-10-21 13:53 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-08 | 2024-08-08 | 30 village green |  | East Longmeadow | MA | 1028 | Stove tripped after 1 minute of use. | Amana | W10406469 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085273123
2024-10-21 14:05 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-07 | 2024-08-07 | 31 village green |  | East Longmeadow | MA | 1028 | Stove tripped after 2 minutes of use. | Hotpoint | 223C3022P006 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085352906
2024-10-21 14:11 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-06 | 2024-08-06 | 32 village green |  | East Longmeadow | MA | 1028 | Stove tripped after 4 minutes of use. | Amana | W10175656 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085392186
2024-10-21 14:19 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-05 | 2024-08-05 | 29 village green |  | East Longmeadow | MA | 1101 | Stove tripped after 1 minute of use. | Amana | W10406473 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085442527
2024-10-21 14:23 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-02 | 2024-08-02 | 36 village green |  | East Longmeadow | MA | 1028 | Stove tripped after 8 minutes of use. | Hotpoint | 223C3022P006 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085472548
2024-10-21 14:33 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-01 | 2024-08-01 | 34 village green |  | East Longmeadow | MA | 1028 | Stove tripped after 5 minutes of use. | Amana | W10406469 | None | Dwellings | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085536596
2024-10-21 14:37 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-31 | 2024-07-31 | 33 village green |  | East Longmeadow | MA | 1028 | Stove tripped after 5 minutes of use. | Hotpoint | 223C3022P006 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085569907
2024-10-21 14:42 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-26 | 2024-07-26 | 28 village green |  | East Longmeadow | MA | 1028 | Stove tripped after 5 minutes of use. | Hotpoint | 317B6641P001 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085601133
2024-10-21 14:52 | MLSchmitt electric | MLSchmitt electric | 13369 | 371 Taylor st |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician |  | Square D homeline AD-901 | Breaker | Square D homeline AD-901 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-25 | 2024-07-25 | 23 village green |  | East Longmeadow | MA | 1028 | Stove tripped after 4 minutes of use. | Amana | W10406469 | None | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17085672477
2024-10-21 16:33 | THOMAS | ARGENTO | 21738 | 260 MASSACHUSETTS ave |  | BOXBORO | MA | 1719 | 9782632971 | OWNER |  | HOM250GFICP | Breaker | 2 POLE |  |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-14 | 2024-10-14 | 44 OLD COACH RD |  | SUDBURY | MA | 1776 | GFCI BREAKER WILL NOT HOLD AT ALL | THERMADOR | ME302YP/02 |  | KITCHEN | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17086371569
2024-10-21 16:47 | THOMAS | ARGENTO | 21738 | 260 MASSACHUSETTS ave |  | BOXBORO | MA | 1719 | 978-263-2971 | OWNER |  | HOM240GFI | Breaker | 2 POLE |  |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-14 | 2024-10-14 | 44 OLD COACH RD |  | SUDBURY | MA | 1776 | BREAKER WOULD NOT HOLD | THERMADOR | CIT365YB |  | SINGLE FAMILY HOME | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17086463225
2024-10-22 13:53 | Brandon | Daniels | 1971 | 895 Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Electrician |  | Eaton | Breaker | breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-10-04 | 2024-10-04 | 3 Boston Way |  | Newburyport | MA | 1950 | Stove continually tripping breaker | GE | JB645EK9ES |  | Apartment | Kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/17091969063
2024-10-22 15:56 | Kevin | Washek | 29418 | 28 PINEWOOD DR |  | FRAMINGHAM | MA | 1701 | 5082544444 | presidant |  | E51075 | Breaker | breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-14 | 2023-09-28 | 28 PINEWOOD DR |  |  |  |  | range consistently trips breaker | whirlpool | wee510s0fs2 |  | residential kitchen | oven consistently trips gfci breaker | No | No | No | No |  | https://www.formstack.com/admin/download/file/17092777258
2024-10-22 16:06 | CHRISTOPHER | CLAPP | 15946 | PO BOX 213 |  | Hanover | MA | 2339 | 6175928508 | Master Electrician |  | Eaton CFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-10-20 | 2024-03-05 | 50 Hazel Ave |  | Scituate | MA | 2066 | Customer called about their wall oven GFCI breaker tripping several times in the last few months. | GE | ZTD90DPSN2SS | N/A | Kitchen Wall Oven | Kitchen Wall Oven | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/17092846350
2024-10-23 07:24 | Seth | Mione | 21064 | 5 Heritage way |  | Gloucester | MA | 1930 | 9782832299 | Foreman |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095434744 | 2024-10-23 | 2024-10-22 | [5 empty] | Stove trips once oven is on for 10 seconds. | G E | J B256D M3WW |  | Apartment | Kitchen 108 | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17095434760 | https://www.formstack.com/admin/download/file/17095434763
2024-10-23 07:27 | Seth | Mione | 21064 | 5 Heritage way |  | Gloucester | MA | 1930 | 9782832299 | Foreman |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095442625 | 2024-10-23 | 2024-10-22 | [5 empty] | Stove trips once oven is on for 10 seconds. | G E | J B256D M3WW |  | Apartment | Kitchen 108 | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17095442637 | https://www.formstack.com/admin/download/file/17095442638
2024-10-23 07:41 | Seth | Mione | 21064 | 71 Middle street |  | Gloucester | MA | 1930 | 9782832299 | Foreman |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095479688 | 2024-10-23 | 2024-10-22 | [5 empty] | Range trips after oven is on for 10 seconds. | Range | J B256D M3WW |  | Apartment | Kitchen 108 | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17095479700 | https://www.formstack.com/admin/download/file/17095479701
2024-10-23 07:45 | Seth | Mione | 21064 | 71 Middle street |  | Gloucester | MA | 1930 | 9782832299 | Foreman |  | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095488576 | 2024-10-23 | 2024-10-22 | [5 empty] | Range trips after oven is on for 10 seconds. | Range | J B256D M3WW |  | Apartment | Kitchen 108 | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17095488588 | https://www.formstack.com/admin/download/file/17095488589
2024-10-23 08:10 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | breaker | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095562563 | 2024-10-23 | 2024-10-22 | [5 empty] | trips while oven warming | GE | JB256D |  | APARTMENT | KITCHEN 109 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095562575 | https://www.formstack.com/admin/download/file/17095562576
2024-10-23 08:15 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095578405 | 2024-10-23 | 2024-10-22 | [5 empty] | RANGE TRIPS WHILE WARMING | GE | JB256DM3WW |  | APARTMENT | KITCHEN 110 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095578417 | https://www.formstack.com/admin/download/file/17095578418
2024-10-23 08:20 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095593350 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | RANGE TRIPS WHILE WARMING | GE | JB2565DM3WW |  | APARTMENT | KITCHEN 111 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095593365 | https://www.formstack.com/admin/download/file/17095593366
2024-10-23 08:24 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095605668 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | RANGE TRIPS WITH BURNERS ON THEN OVEN STARTING | GE | JB256DM3WW |  | APT. | KITCHEN 112 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095605681 | https://www.formstack.com/admin/download/file/17095605682
2024-10-23 08:27 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095615619 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | WHILE OVEN IS WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 113 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095615632 | https://www.formstack.com/admin/download/file/17095615633
2024-10-23 08:30 | seth | mione | 20164 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095626148 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | RANGE TRIPS WHILE OVEN IS WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 114 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095626161 | https://www.formstack.com/admin/download/file/17095626162
2024-10-23 08:34 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GBTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095639114 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | RANGE TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 115 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095639127 | https://www.formstack.com/admin/download/file/17095639128
2024-10-23 08:38 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095653535 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | RANGE TRIPS WHENOVEN WARMS | GE | JB256DM3WW |  | APT. | KITCHEN 116 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095653551 | https://www.formstack.com/admin/download/file/17095653554
2024-10-23 08:43 | seth | mione | 20164 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095673158 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | RANGE TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 117 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095673171 | https://www.formstack.com/admin/download/file/17095673172
2024-10-23 08:45 | seth | mione | 20164 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095682965 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 118 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095682978 | https://www.formstack.com/admin/download/file/17095682979
2024-10-23 08:48 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095693112 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 119 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095693135 | https://www.formstack.com/admin/download/file/17095693136
2024-10-23 09:00 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095742574 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE OVEN IS WARMING | GE | J256DM3WW |  | APT. | KITCHEN 201 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095742587 | https://www.formstack.com/admin/download/file/17095742588
2024-10-23 09:05 | seth | mione | 20164 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence |  | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | RANGE TRIPS WHILE OVEN WARMING | GE | JRP20WJ4WW |  | APT. | KITCHEN 203 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095763550 | https://www.formstack.com/admin/download/file/17095763551
2024-10-23 09:08 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095776585 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JRP20WJ4WW |  | APT. | KITCHEN 205 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095776609 | https://www.formstack.com/admin/download/file/17095776611
2024-10-23 09:12 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095793876 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 207 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095793889 | https://www.formstack.com/admin/download/file/17095793890
2024-10-23 09:15 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095805038 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 208 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095805051 | https://www.formstack.com/admin/download/file/17095805052
2024-10-23 09:17 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095818093 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS AFTER 2 MIN | GE | JB256DM3WW |  | APT. | KITCHEN 209 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095818125 | https://www.formstack.com/admin/download/file/17095818126
2024-10-23 09:29 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095873161 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 210 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095873174 | https://www.formstack.com/admin/download/file/17095873175
2024-10-23 09:32 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095888492 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 211 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095888515 | https://www.formstack.com/admin/download/file/17095888516
2024-10-23 09:35 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095900454 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 212 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095900467 | https://www.formstack.com/admin/download/file/17095900468
2024-10-23 09:38 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095916330 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING AND TOP BURNER IS ON | GE | JB256DM3WW |  | APT. | KITCHEN 213 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095916344 | https://www.formstack.com/admin/download/file/17095916345
2024-10-23 09:42 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095936231 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 214 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095936244 | https://www.formstack.com/admin/download/file/17095936245
2024-10-23 09:45 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095955513 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHEN TWO BURNERS ARE ON AND OVEN WARMS | GE | JB256DM3WW |  | APT. | KITCHEN 215 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095955529 | https://www.formstack.com/admin/download/file/17095955530
2024-10-23 09:48 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095968774 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 216 | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17095968787 | https://www.formstack.com/admin/download/file/17095968788
2024-10-23 09:51 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17095985190 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPA WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 217 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17095985210 | https://www.formstack.com/admin/download/file/17095985211
2024-10-23 09:58 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17096020944 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 218 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17096020957 | https://www.formstack.com/admin/download/file/17096020958
2024-10-23 10:03 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17096044740 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 219 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17096044753 | https://www.formstack.com/admin/download/file/17096044754
2024-10-23 10:12 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17096092436 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 301 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17096092453 | https://www.formstack.com/admin/download/file/17096092454
2024-10-23 10:19 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17096134627 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JRP20WJ4WW |  | APT. | KITCHEN 303 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17096134640 | https://www.formstack.com/admin/download/file/17096134641
2024-10-23 10:22 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB230 | Breaker | BREAKER | 30 |  | 2 Pole | Eaton | Residence |  | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | BURNERS ARE TRIPPING AFTER RUNNING FOR A MIN. | SUMMIT | CR4SS24 |  | APT. | KITCHEN 303 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17096156040 | https://www.formstack.com/admin/download/file/17096156041
2024-10-23 11:58 | MATT | PARENTEAU | 56869 | 134 FLANDERS RD |  | WESTBOROUGH | MA | 1570 | 5083419933 | BUILDER |  | EATON BRN240GF | Breaker | NO | 40 |  | 2 Pole | Eaton | Residence |  | 2024-10-22 | 2024-10-14 | 8 PLIMPTON FARM RD |  | MILLIS | MA | 2054 | Appliance trips breaker despite no working load. | JENNAIR | JDRP436HL | NONE | SINGLE FAMILY | KITCHEN APPLIANCE TRIPS | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17096753376
2024-10-23 12:03 | MATT | PARENTEAU | 56869 | 134 FLANDERS RD |  | WESTBOROUGH | MA | 1581 | 5083419933 | BUILDER |  | EATON BRN240GF | Breaker | NO | 40 |  | 2 Pole | Eaton | Residence |  | 2024-10-22 | 2024-10-14 | 4 PLIMPTON FARM RD |  | MILLIS | MA | 2054 | APPLIANCE TRIPS UNDER NO WORKING LOAD | JENNAIR | JJW3430LL | NONE | SINGLE FAMILY | KITCHEN-APPLIANCE TRIPS | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17096789812
2024-10-23 12:45 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097051543 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JRP20WJ4WW |  | APT. | KITCHEN 205 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17097051556 | https://www.formstack.com/admin/download/file/17097051557
2024-10-23 12:50 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GTCB230 | Breaker | BREAKER | 30 |  | 2 Pole | Eaton | Residence |  | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE BURNERS ARE WARMING. | SUMMIT | CR4SS24 |  | APT. | KITCHEN 305 | Yes | No | No | Yes | https://www.formstack.com/admin/download/file/17097085815 | https://www.formstack.com/admin/download/file/17097085820
2024-10-23 12:54 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097107704 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | TRIPS WHILE WARMING | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17097107717 | https://www.formstack.com/admin/download/file/17097107718
2024-10-23 13:00 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097148598 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 308 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17097148611 | https://www.formstack.com/admin/download/file/17097148612
2024-10-23 13:03 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097165328 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 309 | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17097165341 | https://www.formstack.com/admin/download/file/17097165342
2024-10-23 13:06 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097182710 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 310 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17097182723 | https://www.formstack.com/admin/download/file/17097182724
2024-10-23 13:10 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097208347 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE OVEN IS WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 311 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17097208360 | https://www.formstack.com/admin/download/file/17097208361
2024-10-23 13:22 | seth | mione | 20164 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097286659 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 312 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17097286672 | https://www.formstack.com/admin/download/file/17097286673
2024-10-23 13:27 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097316726 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 313 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17097316749 | https://www.formstack.com/admin/download/file/17097316752
2024-10-23 13:30 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097333627 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE OVEN IS WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 314 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17097333640 | https://www.formstack.com/admin/download/file/17097333641
2024-10-23 13:32 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097348816 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHEN WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 315 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17097348829 | https://www.formstack.com/admin/download/file/17097348830
2024-10-23 13:35 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097364851 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHEN WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 316 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17097364864 | https://www.formstack.com/admin/download/file/17097364865
2024-10-23 13:37 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097380133 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 317 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17097380146 | https://www.formstack.com/admin/download/file/17097380148
2024-10-23 13:39 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097395800 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 318 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17097395813 | https://www.formstack.com/admin/download/file/17097395814
2024-10-23 13:45 | MATT | PARENTEAU | 56869 | 134 FLANDERS RD |  | WESTBOROUGH | MA | 1581 | 5083419933 | BUILDER |  | EATON/BRN240GF | Breaker | NO | 40 |  | 2 Pole | Eaton | Residence |  | 2024-10-22 | 2024-10-14 | 9 PLIMPTON FARM RD |  | MILLIS | MA | 2054 | BREAKER TRIPS UNDER NO WORKING LOAD ON APPLIANCE | JENNAIR | JJW3430LL | NO | SINGLE FAMILY | KITCHEN | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17097432395
2024-10-23 13:46 | seth | mione | 21064 | 71 MIDDLE STREET |  | GLOUCESTER | MA | 1930 | 9782832299 | FOREMAN |  | GFTCB250 | Breaker | BREAKER | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17097439612 | 2024-10-23 | 2024-10-22 | 71 MIDDLE STREET |  |  |  |  | TRIPS WHILE WARMING | GE | JB256DM3WW |  | APT. | KITCHEN 319 | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17097439625 | https://www.formstack.com/admin/download/file/17097439626
2024-10-24 06:07 | Michael | Perkins | 14342 | p.o. box 142, main st, Main st |  | millis | MA | 2054 | 508.326.0705 | President/ electrical contractor |  | QF250A | Breaker | n/a | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-24 | 2024-10-22 | 36 Cypress rd |  | natick | MA | 1760 | breaker tripping when you plug in the appliance | Bosch | HIS8655U/06 | 0 | single family | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17100815854
2024-10-25 10:10 | Tony | Marroquin | 14426 | 33 Whalen Rd |  | Hokinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB230 | Breaker | N/A | 30 |  | 2 Pole | Eaton | Residence |  | 2024-10-04 | 2024-10-28 | [5 empty] | Dryer tripping with normal use. | Samsung | DVE52A5500V |  | Single Family | Laundry Room | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17108164955
2024-10-25 13:47 | Christine | Miller | 60582 | 74 West Main Street |  | Cummington | MA | 1026 | 4134858510 | Electrician |  | Qo240cp | Breaker | 2 pole | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17109376887 | 2024-10-25 | 2024-10-25 | [5 empty] | Oven tripped immediately | G E | Jb860sj4ss | None | Single family | None | No | No | No | No | https://www.formstack.com/admin/download/file/17109376900 | https://www.formstack.com/admin/download/file/17109376901
2024-10-25 14:21 | Moises | Docanto | 23130 | 4980 N main st Apt 408 |  | Fall River | MA | 2720 | 6178490920 | OWNER |  | GFTCB240 | Breaker | N/A | 40 | N/A | 2 Pole | Eaton | Residence |  | 2024-10-08 | 2024-09-30 | 28 Rosa's Lane |  | Ma | MA | 2066 | Once we install the GFCI Breaker it started tripping once customer use the oven. | BOSCH | HBLP451 | NO | Single Family | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17109564815
2024-10-25 16:16 | Sean | Griffin | 14426 | 8 Pleasant Street Suite A2 |  | Natick | MA | 1760 | 7745719815 | Project Manager |  | BRN240GF | Breaker | Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2024-10-25 | 2024-10-25 | 4 Oxbow Road |  | Raynham | MA | 2767 | breaker trips when oven is turned on | General Electric | JS760SPSS | None | Townhome | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17110209758
2024-10-26 11:32 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor |  | Seimens 30 amp gfi | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2024-10-25 | 2024-10-24 | 65 Moore Lane |  | Wayland | MA | 1778 | Installed a 30 gfi breaker on a new cooktop. Breaker would continue to trip. | Thermador | CITR36YWB |  | Single family | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17112351250
2024-10-26 11:43 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor |  | QF240A | Breaker | Breaker | 40 |  | 2 Pole | Siemens | Residence |  | 2024-10-25 | 2024-10-24 | 56 Moore Lane |  | Wayland | MA | 1778 | Installed a 40 amp gfci breaker on a new wall oven. The breaker continued to trip. | Cafe | CTD70PDNSI |  | Single Family | Kitchen. | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17112390107
2024-10-26 11:51 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1778 | 978-337-6541 | castlecp@hotmail.com |  | QF120A | Breaker | Breaker | 20 |  | 1 Pole | Siemens | Residence |  | 2024-10-25 | 2024-10-24 | 56 Moore Lane |  | Wayland | MA | 1778 | Installed a 20 amp dual function, on a new Microwave. The breaker continues to trip. | Beko | MWDR24100SS |  | Single family | Kitchen. | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17112422069
2024-10-28 14:59 | Cal | Harvey | 14426 | 8 Pleasant St | Unit B | Natick | MA | 1760 | 7816974950 | Project Assistant |  | GFTCB230 | Breaker | BR | 30 |  | 2 Pole | Eaton | Residence |  | 2024-10-28 | 2024-10-14 | 28 Oxbow Road |  | Raynham | MA | 2767 | Dryer causing breaker to trip | General Electric | GFD55ESSNWW |  | Townhome | Laundry Room | No | No | No | No |  | https://www.formstack.com/admin/download/file/17120815784
2024-10-28 20:08 | Alexander | Stelmah | 22142 | 9 Sunset Ave |  | North Reading | MA | 1864 | 617 416 8054 | Electrician |  | LB120-DFR | Breaker | Breaker | 20 |  | 1 Pole | Leviton | Residence |  | 2024-10-28 | 2024-10-25 | 36 Ballardvale Rd |  | Andover | MA | 1810 | Installed 20Amp dual function on the SUB ZERO fridge. The breaker continues to trip | SUB ZERO | CL4850UFDID/S/P |  | Single family | kitchen | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/17122458318
2024-10-29 08:26 | MLSchmittelectric | MLSchmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-17 | 2024-06-17 | 2 Village green |  | East Longmeadow | MA | 1028 | Stove trips within five minutes of use. | Amana | W10175656 |  | Residential | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124104675
2024-10-29 08:34 | MLSchmittelectric | MLSchmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-24 | 2024-06-24 | 3 Village green |  | East Longmeadow | MA | 1028 | Stove trips within five minutes of use. | Amana | W10175656 |  | Residential | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124133324
2024-10-29 08:43 | MLShmittelectric | MLSmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-25 | 2024-06-25 | 4 Village Green |  | East Longmeadow | MA | 1028 | Stove trips within five minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124168528
2024-10-29 09:09 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-03 | 2024-07-03 | 5 Village Green |  | East Longmeadow | MA | 1028 | Stove trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124281417
2024-10-29 09:10 | MLShmittelectric | MLSmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-25 | 2024-06-25 | 4 Village Green |  | East Longmeadow | MA | 1028 | Stove trips within five minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124282807
2024-10-29 09:14 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-02 | 2024-07-02 | 6 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124306165
2024-10-29 09:21 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-08 | 2024-07-08 | 7 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124338094
2024-10-29 09:26 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-01 | 2024-07-01 | 9 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124364623
2024-10-29 09:33 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electric |  | Square D homelineAD-910 | Breaker | Square DAD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-09 | 2024-07-09 | 10 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124396713
2024-10-29 09:41 | Mlaschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-10 | 2024-07-10 | 11 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124437153
2024-10-29 09:48 | Mlaschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-10 | 2024-07-10 | 11 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124473203
2024-10-29 09:52 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-11 | 2024-07-11 | 12 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124498534
2024-10-29 09:58 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-12 | 2024-07-12 | 13 Village Green |  | East longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124531742
2024-10-29 10:02 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-08-23 | 2024-08-23 | 19 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124554303
2024-10-29 10:17 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-18 | 2024-06-18 | 21 Village Green |  | East Longmeadow | MA | 1101 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124638261
2024-10-29 10:21 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electric |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-19 | 2024-06-19 | 22 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124662915
2024-10-29 10:29 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-15 | 2024-07-15 | 24 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124706096
2024-10-29 10:29 | Brian | Palazzi | 38622 | 366 Dwight Rd |  | Springfield | MA | 01108-3434 | 4133489307 | Service Manager |  | Leviton / LB240-G | Breaker | 40-amp 120/240 V GFCI | 40 |  | 2 Pole | Leviton | Residence |  | 2024-09-13 | 2024-09-13 | 57 Danek Drive (Ely Apartments) |  | Westfield | MA | 1085 | we tried (2) breakers to be sure that the breaker is not the problem.¦¦The burner is turned on and within 1 minute the breaker trips | Peerless- Premier Appliance CO | 26006 |  | Westfield Housing Authority Residential Space | Oven outlet only. | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124708684
2024-10-29 10:34 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-20 | 2024-06-20 | 27 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124735974
2024-10-29 10:39 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-24 | 2024-06-24 | 35 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17124766554
2024-10-29 11:54 | Mlschmittelectric | Mlschmittelectric | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 4137337868 | Master Electrician |  | Square D homeline AD-910 | Breaker | Square D homeline AD-910 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-24 | 2024-06-24 | 35 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17125252527
2024-10-29 19:24 | Domenic | Vitone | 33225 | 86 Underwood Ave |  | West Newton | MA | 2465 | 6178387070 | ELECTRICAL COMTRACTOR |  | EATON/GFTCB230 | Breaker | GFCI | 30 |  | 2 Pole | Eaton | Residence |  | 2024-10-15 | 2024-10-07 | 186 Waban Ave |  | Newton | MA | 2468 | breaker trip during cooking | Thermador Cooktop | PO301W/04 | 0 | kitchen | kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17128033228 | https://www.formstack.com/admin/download/file/17128033229
2024-10-29 20:56 | Domenic | Vitone | 33225 | 86 Underwood Ave |  | West Newton | MA | 2465 | 6178387070 | Electrical contractor |  | EATON /GFTCB230 | Breaker | GFCI | 30 |  | 2 Pole | Eaton | Residence |  | 2024-10-18 | 2024-10-10 | 186 Oliver RD |  | Newton | MA | 2468 | breaker tripped during cooking | Thermador | CIT36YWBB | 0 | single family home | kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17128373913 | https://www.formstack.com/admin/download/file/17128373914
2024-10-30 10:23 | Tony | Marroquin | 14426 | 22 Whalen Rd |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB250 | Breaker | none | 50 |  | 2 Pole | Eaton | Residence |  | 2024-10-30 | 2024-09-03 | 50 Chamberlain st |  | Hopkinton | MA | 1748 | Oven trips with normal use. | JennAir | JJW3430LL | none | Single Family | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17130337219
2024-10-30 10:33 | Tony | Marroquin | 14426 | 22 Whalen Rd |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager |  | GFTCB240 | Breaker | none | 40 |  | 2 Pole | Eaton | Residence |  | 2024-10-30 | 2024-09-03 | 50 Chamberlain st |  | Hopkinton | MA | 1748 | breaker trips immediately | JennAir | JIC4536KS | none | Single Family | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17130396726
2024-10-31 08:55 | Paul | Macrina | 15503 | 104 Adams Street |  | Medfield | MA | 2052 | 508-359-7954 | Owner |  | GFTCB250 | Breaker | . |  |  | 2 Pole | Eaton | Commercial |  | 2024-09-15 | 2024-08-10 | 130 Warren Street |  | Brookline | MA | 2445 | While the homeowner is using the oven to cook, the breaker will trip on the middle of use. | Wolf | DF60650CG/S/P | None | residential kitchen | residential kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17135223972
2024-10-31 13:06 | William | Jennings | 10516 | 15 Nourse Street |  | Arlington | MA | 2474 | 781-389-4719 | Electrician |  | BRN230GF | Breaker | NA | 30 |  | 2 Pole | Eaton | Residence |  | 2024-07-08 | 2024-07-08 | [5 empty] | GFCI breaker trips immediately after dryer whip is plugged into outlet | Whirlpool | WET4024HWC |  | 2 family | Basement laundry area | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17136604036
2024-10-31 13:10 | William | Jennings | 10516 | 15 Nourse Street |  | Alrington | MA | 2474 | 7813894719 | Electrician |  | BRN230GF | Breaker | NA | 30 |  | 2 Pole | Eaton | Residence |  | 2024-07-08 | 2024-07-08 | [5 empty] | Breaker trips immediately after range whip is plugged into outlet. | Samsung | NE63*651*5* |  | 2 family | Basement laundry area | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17136629356
2024-10-31 21:04 | Greg | Kehlhem | 11544 | 3 saddle hill road |  | Medway | MA | 2053 | 774-993-9697 | Owner |  | Siemens QF250A | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17138847515 | 2024-10-30 | 2024-10-30 | 121 Brandywine |  | Franklin | MA | 2038 | Wolf cooktop will not hold on a gfci breaker. Tried a different brand for the panel and still trips. Ran on standard breaker for multiple hours but still tripped gfci breaker after. | Wolf | CI365T/S | None | Single family | Kitchen induction cooktop | No | No | No | No | https://www.formstack.com/admin/download/file/17138847529 | https://www.formstack.com/admin/download/file/17138847530
2024-11-01 08:21 | Michael | Hester | 56880 | 70 Pleasant St | #49 | Oxford | MA | 1537 | 5083358328 | Master Electrician/Project Manager |  | Siemens QF250A | Breaker | none | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17139907965 | 2024-08-15 | 2024-08-15 | 291 Prospect St |  | Franklin | MA | 2038 | Stove Trips GFCI breaker on broil mode only. Stove Functions fine otherwise. Wiring and equipment installation was installed correctly as per the local wiring inspector. Stove is only about 6 years old and functioned normally on a standard Siemens QP circuit breaker. | Samsung | NE59M4320 | None | Single Family Dwelling | Kitchen | No | No | Yes | No | https://www.formstack.com/admin/download/file/17139907979 | https://www.formstack.com/admin/download/file/17139907980
2024-11-02 07:05 | Joe | Gore | 21745 | 4 Washington Terrace |  | Woburn | MA | 1801 | 7818313258 | Owner/installer | Joseph.gore@Comcast.net | Square D HOM230GFIC | Breaker | N/a | 30 | N/a | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17144084542 | 2024-10-07 | 2024-09-23 | 15 Stewart road |  | North Reading | MA | 1864 | Brand new circuit was installed including new wiring, new panel and new receptacle. Circuit breaker turns on and stays on. Dryer is plugged into the receptacle and circuit breaker stays on. Once the dryer is turned on to start a cycle, the circuit breaker immediately trips. This happens every time. The dryer operates normally on a standard Non-Gfci circuit breaker. | Whirlpool | WED5821SWO | None | Single family home | This is a 30 amp dedicated dryer circuit. There are no other rooms or circuits affected. | Yes | Yes | Yes | No | https://www.formstack.com/admin/download/file/17144084556 | https://www.formstack.com/admin/download/file/17144084557
2024-11-02 12:02 | Christine | Miller | 60582 | 59 Federal Ave |  | Agawam | MA | 1011 | 4134858510 | Electrician | christine.miller@trinity-solar.com | QO240GFI | Breaker | 2pole | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17144612839 | 2024-11-02 | 2024-11-02 | [5 empty] | Breaker tripped when we tried to operate the stove | General Electric Company | Jbp30gy1wh | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17144612852 | https://www.formstack.com/admin/download/file/17144612853
2024-11-03 10:34 | Ronald | Abel | 8845 | 19 Rumford St |  | Winchester | MA | 1890 | 781-953-8849 | President | raesi@comcast.net | Sq D Homeline HOM250GFCIP | Breaker | 0 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-29 | 2024-10-29 | [5 empty] | Installed GFCI breaker and electric range tripped instantly. | AGA Mercury 36 Induction | AMC36in |  | Single family | No rooms | No | No | No | No |  | https://www.formstack.com/admin/download/file/17146530484
2024-11-03 16:13 | Ronald | Abel | 8845 | 19 Rumford Street |  | Winchester | MA | 1890 | 781-953-8849 | Electrician | raesi@comcast.net | Square D Homeline HOM250GFCIP | Breaker | 0 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-29 | 2024-10-29 | 2 New Meadows Rd. |  | Winchester | MA | 1890 | Breaker tripped as soon as the range was turned on. | AGA Mercury 36 Induction | AMC36IN | None | Single Family | No Rooms. Range is a dedicated line. | No | No | No | No |  | https://www.formstack.com/admin/download/file/17148199646
2024-11-04 07:26 | [11 empty] | Legrand | Receptacle | None | 20 | None | 1 Pole | Legrand | Commercial |  | 2024-10-28 | 2024-10-28 | 664 Merrimack St |  | Lowell | MA | 1854 | Nuisance tripping on from the countertop GFI when the refrigerator is plugged in. | Whirlpool | WRQA59CNKZ | None | Kitchen | Kitchen, Nuisance tripping on from the countertop GFI when the refrigerator is plugged in. | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17150013437 | https://www.formstack.com/admin/download/file/17150013438
2024-11-04 10:01 | Sean | Griffin | 14426 | 8 Pleasant Street Suite A2 |  | Natick | MA | 1760 | 7745719815 | Project Manager | sean.griffin@thorndikedevelopment.com | BRN240GF | Breaker | Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2024-11-04 | 2024-11-04 | 16 Oxbow Road |  | Raynham | MA | 2767 | range trips breaker | General Electric | JS760SPSS | None | Townhome | range trips breaker | No | No | No | No |  | https://www.formstack.com/admin/download/file/17150783135
2024-11-04 13:07 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-15 | 2024-10-16 | 280 Martins Landing Unit # 303 |  | North Reading | MA | 1864 | When warming up the stove | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17152066084
2024-11-04 13:11 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schnieder | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-16 | 2024-10-17 | 2 Winslow Lan Unit # 410 |  | Grafton | MA | 1536 | When warming up the stove | Whirlpool | WFE50S0LZ3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17152094371
2024-11-04 13:20 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-17 | 2024-10-18 | 2 Winslow Lane Unit # 203 |  | Grafton | MA | 1536 | When warming up the stove | Whirlpool | WFES3530RS0 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17152156891
2024-11-04 13:38 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-21 | 2024-10-22 | 260 Martins Landing Unit # 104 |  | North Reading | MA | 1864 | When warming up the stove | Whirlpool | WFE51550J53 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17152285653
2024-11-04 13:41 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-20 | 2024-10-21 | 6110 Peters Farm Way |  | Westborough | MA | 1581 | When warming up the stove | Whirlpool | WFE550S0LZ3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17152303056
2024-11-04 13:44 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-20 | 2024-10-21 | 2 Winslow Lane Unit # 108 |  | Grafton | MA | 1536 | When warming up the stove | Whirlpool | WFE51550J53 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17152325560
2024-11-04 14:22 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-21 | 2024-10-22 | 6111 Peters Farm Way |  | Westborough | MA | 1581 | When warming up the stove | Whirlpool | WFE525S0JZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17152599119
2024-11-04 14:25 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-21 | 2024-10-22 | 6108 Peters Farm Way |  | Westborough | MA | 1581 | When warming up the stove | Whirlpool | WFE535S0LS3 |  | Condon | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17152618215
2024-11-04 14:27 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-17 | 2024-10-18 | 4 Stratton Drive Unit # 104 |  | Woburn | MA | 1801 | When warming up the stove | Whirlpool | W0EC3030LS00 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17152638769
2024-11-04 14:42 | Jonathan | Shepard | 21277 | 177 Chestnut st |  | Hudson | MA | 1749 | 7742492435 | Owner | jmselectric09@gmail.com | Qpf Gfci 5MA 2P 240V 50A 10KA | Breaker | breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-09 | 2024-02-09 | 35 wetherbee Ave |  | Lowell | MA | 1852 | Breaker trips a few minutes after the stove is running. | Frigidaire | GCFI3060BF | No | Single family. | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17152743648
2024-11-04 16:33 | JAMES | M WALSH | 9032 | 307 York St |  | Canton | MA | 2021 | 5083263528 | electrician | jwalsh@elconelectricco.com | SQD | Breaker | none | 50 |  | 2 Pole | Eaton | Residence |  | 2024-08-07 | 2024-08-01 | 989 Memorial Dr unit 601 |  | Cambridge | MA |  | Induction stove would run for 30 min and then GFI would trip out | Induction stove | Bosh |  | multi | Kitchen, induction stove | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/17153509621
2024-11-05 09:32 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-17 | 2024-10-18 | 401 Emery Lane Unit # 412 |  | Sudbury | MA | 1776 | When warming up the stove | Whirlpool | KMHC319ESS06 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17156432652
2024-11-05 10:38 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-29 | 2024-10-30 | 2 Winslow Lane Unit # 404 |  | Grafton | MA | 1536 | When warming up the stove | Whirlpool | WFE775H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17156810867
2024-11-05 10:41 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-27 | 2024-10-28 | 280 Martins Landing Unit # 403 |  | North Reading | MA | 1864 | When warming up the stove | Whirlpool | WFE775HOHZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17156827581
2024-11-05 10:46 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-27 | 2024-10-28 | 2 Winslow Lane Unit # 406 |  | Grafton | MA | 1536 | When warming up the stove | Whirlpool | WFE525S0JS4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17156859913
2024-11-05 10:49 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-31 | 2024-11-01 | 6204 Peters farm Way |  | Westborough | MA | 1581 | When warming up the stove | Whirlpool | WFE550S0LZ3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17156879372
2024-11-05 10:52 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-06 | 2024-11-07 | 2 Winslow Lane Unit # 302 |  | Grafton | MA | 1536 | When warming up stove | Whirlpool | WFE775H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17156897484
2024-11-05 11:05 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | President | PHannon@HannonElectricInc.com | GFTCB240 | Breaker | n/a | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17156984867 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | nuisance tripping | GE | JB2560 M4WW |  | senior living | Kitchen range | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17156984880 | https://www.formstack.com/admin/download/file/17156984881
2024-11-05 12:46 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | President | phannon@hannonelectricinc.com | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17157684068 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | nuisance tripping | GE | JB 2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17157684085 | https://www.formstack.com/admin/download/file/17157684086
2024-11-05 13:14 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17157868076 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17157868089 | https://www.formstack.com/admin/download/file/17157868090
2024-11-05 13:29 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17157961957 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17157961970 | https://www.formstack.com/admin/download/file/17157961971
2024-11-05 13:34 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17157996919 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17157996932 | https://www.formstack.com/admin/download/file/17157996933
2024-11-05 14:08 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158215605 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158215618 | https://www.formstack.com/admin/download/file/17158215619
2024-11-05 14:12 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158245985 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158245998 | https://www.formstack.com/admin/download/file/17158245999
2024-11-05 14:21 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158300029 | 2024-11-02 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158300042 | https://www.formstack.com/admin/download/file/17158300043
2024-11-05 14:26 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158330437 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158330450 | https://www.formstack.com/admin/download/file/17158330451
2024-11-05 14:31 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082589955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158367376 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158367402 | https://www.formstack.com/admin/download/file/17158367404
2024-11-05 14:35 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158395356 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158395371 | https://www.formstack.com/admin/download/file/17158395372
2024-11-05 14:40 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158425408 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158425421 | https://www.formstack.com/admin/download/file/17158425422
2024-11-05 14:45 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158455307 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158455320 | https://www.formstack.com/admin/download/file/17158455321
2024-11-05 14:49 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158486787 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158486800 | https://www.formstack.com/admin/download/file/17158486801
2024-11-05 14:54 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158518754 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158518768 | https://www.formstack.com/admin/download/file/17158518769
2024-11-05 14:59 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158548905 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158548918 | https://www.formstack.com/admin/download/file/17158548919
2024-11-05 15:03 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158575883 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158575896 | https://www.formstack.com/admin/download/file/17158575897
2024-11-05 15:09 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158614365 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158614378 | https://www.formstack.com/admin/download/file/17158614379
2024-11-05 15:14 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158647395 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158647408 | https://www.formstack.com/admin/download/file/17158647409
2024-11-05 15:20 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158686178 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158686191 | https://www.formstack.com/admin/download/file/17158686192
2024-11-05 15:25 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17158717899 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17158717919 | https://www.formstack.com/admin/download/file/17158717922
2024-11-05 19:08 | John | Peterson | 39801 | 90 center st |  | bellingham | AL | 2019 | 5089221662 | electrician | pete40399@yahoo.com | eaton | Breaker | gfi | 40 |  | 2 Pole | Eaton | Residence |  | 2024-10-30 | 2024-10-30 | 9 walker st |  | hopkinton | MA | 1748 | gfi breaker trip as soon as you turn on over | cafe | ces700p2m3s1 |  | kitchen | stove in kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17159844430
2024-11-06 08:44 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17161591010 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17161591023 | https://www.formstack.com/admin/download/file/17161591024
2024-11-06 08:55 | Andrew | Woodford | 11549 | 73 Winchester St |  | Baldwinville | MA | 1436 | 9787308870 | President | Woodfordelectric@gmail.com | Square D | Breaker | QO250GFI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-06 | 2024-11-06 | 36 Edgell St |  | GARDNER | MA | 1440 | GFI trips when new oven is turned on | Bosch | HIIP057U |  | Kitchen | Kitchen range receptacle | No | No | No | No |  | https://www.formstack.com/admin/download/file/17161635017
2024-11-06 11:01 | Dave | DiBiase | 40387 | 45 Winchendon rd |  | Baldwinville | MA | 1436 | 9787308870 | Electrician | Woodfordelectric@gmail.com | SQ D hom250gfi | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-11-05 | 2024-10-29 | 91 Linwood St |  | GARDNER | MA | 1440 | Oven trips breaker when turned on | GE | J BP35D D1BB | none | single family | Kitchen range receptacle only | No | No | No | No |  | https://www.formstack.com/admin/download/file/17162289877
2024-11-06 12:00 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17162706431 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17162706447 | https://www.formstack.com/admin/download/file/17162706448
2024-11-06 12:05 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17162729701 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17162729714 | https://www.formstack.com/admin/download/file/17162729715
2024-11-06 12:08 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17162752987 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17162753000 | https://www.formstack.com/admin/download/file/17162753001
2024-11-06 12:17 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17162802976 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17162802989 | https://www.formstack.com/admin/download/file/17162802990
2024-11-06 12:21 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17162824434 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17162824447 | https://www.formstack.com/admin/download/file/17162824448
2024-11-06 12:25 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17162847847 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17162847860 | https://www.formstack.com/admin/download/file/17162847861
2024-11-06 12:29 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17162872441 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17162872458 | https://www.formstack.com/admin/download/file/17162872460
2024-11-06 12:36 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17162912429 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17162912445 | https://www.formstack.com/admin/download/file/17162912447
2024-11-06 12:54 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163034237 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITHCNE RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163034250 | https://www.formstack.com/admin/download/file/17163034251
2024-11-06 12:58 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N?A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163058697 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163058710 | https://www.formstack.com/admin/download/file/17163058711
2024-11-06 13:02 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163086147 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163086160 | https://www.formstack.com/admin/download/file/17163086161
2024-11-06 13:06 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163110757 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163110770 | https://www.formstack.com/admin/download/file/17163110771
2024-11-06 13:13 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163153197 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUJISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163153210 | https://www.formstack.com/admin/download/file/17163153211
2024-11-06 13:18 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163179784 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163179797 | https://www.formstack.com/admin/download/file/17163179798
2024-11-06 13:45 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163341633 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163341646 | https://www.formstack.com/admin/download/file/17163341647
2024-11-06 13:52 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163390158 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163390171 | https://www.formstack.com/admin/download/file/17163390172
2024-11-06 13:57 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163421935 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163421948 | https://www.formstack.com/admin/download/file/17163421949
2024-11-06 14:03 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163463103 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163463116 | https://www.formstack.com/admin/download/file/17163463117
2024-11-06 14:07 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163489318 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163489331 | https://www.formstack.com/admin/download/file/17163489332
2024-11-06 14:12 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163513940 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163513953 | https://www.formstack.com/admin/download/file/17163513954
2024-11-06 14:16 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163539669 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17163539688
2024-11-06 14:21 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163567928 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163567941 | https://www.formstack.com/admin/download/file/17163567942
2024-11-06 14:25 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17163596547 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17163596560 | https://www.formstack.com/admin/download/file/17163596561
2024-11-06 14:55 | Cal | Harvey | 14426 | 8 Pleasant St | Unit B | Natick | MA | 1760 | 7816974950 | Project Assistant | cal.harvey@thorndikedevelopment.com | BRN250GF | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2024-11-05 | 2024-10-29 | 14 Oxbow Rd |  | Raynham | MA | 2767 | Range causing breaker trip | GE | JS760SPSS |  | Townhome | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17163802672
2024-11-07 11:05 | JAMES | M WALSH | 9032 | 11 Perry DR Foxboro MA |  | Foxboro | MA | 2035 | 508-326-3528 | Electrician | jwalsh@elconelectricco.com | SQD 502P 50amp 2 pole | Breaker | None | 50 |  | 2 Pole | ABB | Residence |  | 2024-09-12 | 2024-09-03 | 989 Memorial Dr unit 601 |  | Cambridge | MA | 2138 | Miele KM7740FR Induction cook top will work for a 30min or so and then trip out. we tried a standard 2 pole 50amp breaker and it works with no tripping | Mieli | KM7740FR |  | Kitchen | Kitchen Induction cooktop | No | No | No | No |  | https://www.formstack.com/admin/download/file/17167658706
2024-11-07 15:03 | Tony | Marroquin | 14426 | 54 Chamberlain |  | Hopkinton | MA | 1748 | 4015726319 | Construction Manager | amarroquin@tollbrothers.com | GFTCB250 | Breaker | Other | 50 |  | 2 Pole | Eaton | Residence |  | 2024-09-04 | 2024-08-01 | 54 Chamberlain st |  | Hopkinton | MA | 1748 | oven trips with normal use | JennAir | JJW3430LL |  | Single Family | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17169115809
2024-11-07 15:17 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169203705 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169203718 | https://www.formstack.com/admin/download/file/17169203719
2024-11-07 15:22 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169231754 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | SANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169231767 | https://www.formstack.com/admin/download/file/17169231768
2024-11-07 15:26 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169259796 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169259821 | https://www.formstack.com/admin/download/file/17169259823
2024-11-07 15:30 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PREISDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169286114 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169286136 | https://www.formstack.com/admin/download/file/17169286138
2024-11-07 15:33 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169309567 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169309580 | https://www.formstack.com/admin/download/file/17169309581
2024-11-07 15:37 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169332801 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169332814 | https://www.formstack.com/admin/download/file/17169332815
2024-11-07 15:41 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169356256 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169356269 | https://www.formstack.com/admin/download/file/17169356270
2024-11-07 15:45 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169380314 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169380327 | https://www.formstack.com/admin/download/file/17169380328
2024-11-07 15:49 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169409663 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169409676 | https://www.formstack.com/admin/download/file/17169409677
2024-11-07 15:54 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169436568 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | HE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169436581 | https://www.formstack.com/admin/download/file/17169436582
2024-11-07 15:58 | Patrick | Hannon | 23226 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169464144 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169464157 | https://www.formstack.com/admin/download/file/17169464158
2024-11-07 16:02 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169485841 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169485854 | https://www.formstack.com/admin/download/file/17169485855
2024-11-07 16:05 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169512750 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | Yes | No | Yes | https://www.formstack.com/admin/download/file/17169512769 | https://www.formstack.com/admin/download/file/17169512770
2024-11-07 16:09 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 82859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169537051 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169537064 | https://www.formstack.com/admin/download/file/17169537065
2024-11-07 16:13 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRINCINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169561432 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169561445 | https://www.formstack.com/admin/download/file/17169561446
2024-11-07 16:17 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169587186 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169587199 | https://www.formstack.com/admin/download/file/17169587200
2024-11-07 16:21 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169612248 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169612261 | https://www.formstack.com/admin/download/file/17169612262
2024-11-07 16:25 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@qHANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169635673 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KITCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169635688 | https://www.formstack.com/admin/download/file/17169635690
2024-11-07 16:28 | Patrick | Hannon | 23229 | 117 Eastman St |  | South Easton | MA | 2375 | 5082859955 | PRESIDENT | PHANNON@HANNONELECTRICINC.COM | GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17169655809 | 2024-11-01 | 2024-09-02 | 21 Newton St |  | Waltham | MA | 2453 | NUISANCE TRIPPING | GE | JB2560M4WW |  | SENIOR LIVING | KIYCHEN RANGE | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17169655822 | https://www.formstack.com/admin/download/file/17169655823
2024-11-08 09:24 | Cal | Harvey | 14426 | 8 Pleasant St | Unit B | Natick | MA | 1760 | 7816974950 | Project Assistant | cal.harvey@thorndikedevelopment.com | BRN250GF | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2024-11-08 | 2024-11-01 | 6 Oxbow Road |  | Raynham | MA | 2767 | Range causing breaker to trip | GE | GRF500PVSS |  | Townhome | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17172290444
2024-11-08 09:31 | Cal | Harvey | 14426 | 8 Pleasant St | Unit B | Natick | MA | 1760 | 7816974950 | Project Assistant | cal.harvey@thorndikedevelopment.com | BRN240GF | Breaker | BR | 40 |  | 2 Pole | Eaton | Residence |  | 2024-11-08 | 2024-11-01 | 8 Oxbow Road |  | Raynham | MA | 2767 | Range causing breaker to trip | GE | GRF500PVSS |  | Townhome | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17172322957
2024-11-08 09:34 | Cal | Harvey | 14426 | 8 Pleasant St | Unit B | Natick | MA | 1760 | 7816974950 | Project Assistant | cal.harvey@thorndikedevelopment.com | BRN240GF | Breaker | BR | 40 |  | 2 Pole | Eaton | Residence |  | 2024-11-08 | 2024-11-01 | 20 Oxbow Road |  | Raynham | MA | 2767 | Range causing breaker to trip | GE | PHS903YPFS |  | Townhome | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17172336079
2024-11-11 15:59 | Kelly | Manning | 53163 | 106 NW Main |  | Douglas | MA | 1516 | 5087377951 | Homeowner | kgazz99@gmail.com | Eaton BRN250GF | Breaker | N/A | 50 | N/A | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17188110200 | 2024-11-05 | 2024-11-04 | 106 NW Main St |  | Douglas | MA | 1516 | Intermittent trip overnight while appliance was not in use. | GE | JB650DF2BB | None | Single family home | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17188110214 | https://www.formstack.com/admin/download/file/17188110215
2024-11-11 20:50 | Corey | Hood | 8228 | 108 | Bird's Hill Ave | Needham | MA | 2492 | 781-915-7358 | Owner | coreyhoodelectric@gmail.com | GFTCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-10-31 | 2024-10-31 | [5 empty] | New Double wall oven, trips when reaching 200 degrees, tried multiple breakers | Thermador | PO302W/04 |  | Single Family Home | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17189272528
2024-11-12 14:17 | Michael | Giombetti | 13678 | 401 SOUTH STREET | Marlboro | MARLBOROUGH | MA | 1752 | 5084813299 | President | Mike@giombettielectric.com | Eaton BRN240GF | Breaker | NA | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17193936906 | 2024-11-09 | 2024-11-11 | 65 Sheffield Terrace |  | Marlboro | MA | 1752 | Breaker will trip while using the oven only | Whirlpool | WSIS5030RZ0 | None | Single family kitchen | Kitchen stove | No | No | No | No | https://www.formstack.com/admin/download/file/17193936941 | https://www.formstack.com/admin/download/file/17193936945
2024-11-13 06:53 | ANDREW | CHURCH | 22219 | 735 CONANT STREET |  | BRIDGEWATER | MA | 2324 | 7819851029 | ELECTRICIAN | andy02190@yahoo.com | SQD HOMLINE | Breaker | n/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-06 | 2024-11-04 |  |  | 28 colonel hunt drive | MA | 2351 | breaker trips after short time of the appliance being on. | frigidaire | fcc13627ab, 1f20296752 | n/a | kitchen | cooktop | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17197104009
2024-11-13 07:06 | ANDREW | CHURCH | 22219 | 735 CONANT STREET |  | BRIDGEWATER | MA | 2324 | 7819851029 | ELECTRICIAN | andy02190@yahoo.com | SQD HOMLINE | Breaker | n/a | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-06 | 2024-11-04 | 28 colonel hunt drive |  | abington | MA | 2351 | breaker trips shortly after appliance is turned on. | FRIGIDAIRE | GCWD3067AFC | N/A | KITCHEN | DOUBLE OVEN | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17197134865
2024-11-13 08:28 | Daniel | Greenberg | 22971 | 32 Norfolk Ave. |  | South Easton | MA | 2375 | 7812647746 | Site Supervisor / CSL Holder | Dgreenberg@stonebridgehomesinc.com | HOM240GFIC | Breaker | N/A | 40 | N/A | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17197371815 | 2024-11-11 | 2024-11-11 | 52 Metacomet Rd. |  | W. Bridgewater | MA | 2379 | Whenever the oven runs, the breaker trips. We are homebuilders and see this happen on almost every range we install. | Frigidaire | GCRE3060BFC | NONE | Single Family Home | Kitchen is the only room affected as it is a dedicated circuit. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17197371829 | https://www.formstack.com/admin/download/file/17197371830
2024-11-13 16:15 | Conrad | Mercer | 52774 | 46 Quisset Rd |  | Centerville | MA | 2632 | 5082210895 | Lead/Service/Finish | conrad.macelectric@icloud.com | Q230GF | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2024-11-10 | 2024-10-15 | 31 Grist Mill Ln |  |  | MA | 2673 | Was fine then starts random tripping with no sertain combination of cycle, load size, setting, etc. All connections checked and good. Insulation meter test no appliance with Fluke meter cleared frame/ground to all phases. | Electrolux Home Products inc | ELFE7637ATO | none | single family dwelling | Laundry Dryer | No | No | No | No | https://www.formstack.com/admin/download/file/17200209202 | https://www.formstack.com/admin/download/file/17200209203
2024-11-13 18:06 | BERNARD | LITCHFIELD | 14334 | 172 South Sandisfield Road |  | New Marlborough, MA | MA | 1230 | 4134291575 | owner electrical contractor | litchfieldgang99@gmail.com | square D QO250 GFCI CIRCUIT BREAKER | Breaker | NONE | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-10 | 2023-12-08 | 16 HIGHLAND DRIVE |  | GT BARRINGTON | MA | 01230-1346 | CIRCUIT BREAKER TRIPS RANDOMLY DURING APPLIANCE OPERATION AND HAS OCCURED SINCE INSTALLATION | THERMADOR | CIT 367YGS | NONE | SINGLE FAMILY RESIDENCE | KITCHEN COOKTOP ONLY | No | No | No | No |  | https://www.formstack.com/admin/download/file/17200823842
2024-11-13 18:21 | BERNARD | LITCHFIELD | 14334 | 172 South Sandisfield Road |  | New Marlborough, MA | MA | 1230 | 4134291575 | OWNER ELECTRICAL CONTRACTOR | litchfieldgang99@gmail.com | SCHNEIDER ELECTRIC QO 250 GFCI | Breaker | NONE | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-09 | 2023-12-08 | 16 HIGHLAND DRIVE |  | GT BARRINGTON | MA | 01230-1346 | DOUBLE OVEN TRIPPED QO 240 GFCI BREAKER DURING COOKING OWNER RESET BREAKER SHORTLY AFTER STARTING APPLIANCE BREAKER AGAIN TRIPPED | THERMADOR | ME302WS/03 | NONE | SINGLE FAMILY RESIDENCE | KITCHEN DOUBLE OVEN ONLY | No | No | No | No |  | https://www.formstack.com/admin/download/file/17200891024
2024-11-14 08:45 | william | whalen | 11255 | 27sandra lane | sandra ln | WEYMOUTH | MA | 2188 | 7817066908 | owner | whalenelectric1@comcast.net | cutler hammer | Breaker | none | 50 |  | 2 Pole | Eaton | Residence |  | 2024-11-01 | 2024-10-24 | 51 sekkonet rd |  | marshfield | MA | 2020 | stove trips when using oven | ge appliances | js760sp8ss | none | kitchen | stove | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17203310937
2024-11-14 10:37 | Daniel | Greenberg | 22971 | 35 Old Farm Rd. | Norfolk Ave. | Bridgewater | MA | 2324 | 7812647746 | Site Supervisor / CSL Holder | Dgreenberg@stonebridgehomesinc.com | HOM240GFIC | Breaker | N/A | 40 | N/A | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17204306316 | 2024-11-11 | 2024-11-11 | 54 Metacomet Rd |  | W. Bridgewater | MA | 2379 | Every time the oven runs, the breaker trips. This happens to us on all of our electric ranges on all the houses we build (about 120 houses / year). | Frigidaire | GCRE3060BFC | - | Single Family Homes | Kitchen. Dedicated circuit so only kitchen range is affected. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17204306338 | https://www.formstack.com/admin/download/file/17204306341
2024-11-15 00:33 | Michael | Chin | 25128 | 27 Pawtucket Drive |  | Lowell | MA | 1854 | 9788539863 | Electrician | mjckrc@aol.com | THQL2140GFT2 | Breaker | NONE | 40 |  | 2 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/17210090147 | 2024-09-19 | 2024-11-18 | 70 Mount Walley Road |  | Waltham | MA | 2451 | Breaker trips on ground fault when oven is on | GE | CHS950P2M6S1 |  | Single Family House | Kitchen | Yes | Yes | Yes | No | https://www.formstack.com/admin/download/file/17210090160 | https://www.formstack.com/admin/download/file/17210090161
2024-11-17 13:33 | Kyle | Franco | 100044 | 44 Janice Dr |  | Goffstown | NH | 3045 | 6036608428 | Owner | Freestateelctric603@gmail.com | GE: THQL2120GFTP | Breaker | THQ | 30 |  | 2 Pole | ABB | Residence |  | 2024-11-05 | 2024-10-30 | 16 Granli Dr |  | Andover | MA |  | frequent tripping. Home owner isnt noticing any patterns | General Electric | ZTS90DPSN3SS |  | Single Family Home | Kitchen Oven | No | No | No | No | https://www.formstack.com/admin/download/file/17222890569 | https://www.formstack.com/admin/download/file/17222890570
2024-11-17 13:52 | Steve | Laurencio | 18079 | PO Box 645 |  | Bedford | MA | 1730 | 978621-7221 | Electrician | steve@desousaelectric.com | Siemens | Breaker | 0 | 50 |  | 2 Pole | Siemens | Residence |  | 2024-11-15 | 2024-11-15 | 43 Lincoln Rd. |  | Lexington | MA | 2421 | Circuit breaker tripping instantly. | Wolf | CI365C/B | NO | Single family | Kitchen induction cooktop. | No | No | No | No |  | https://www.formstack.com/admin/download/file/17222928334
2024-11-17 14:06 | Steve | Laurencio | 18079 | PO Box 645 |  | Bedford | MA | 1730 | 978 621-7221 | Electrician | steve@desousaelectric.com | Siemens | Breaker | 0 | 50 |  | 2 Pole | Siemens | Residence |  | 2024-11-15 | 2024-11-15 | 43 Lincoln Rd. |  | Lexington | MA | 2421 | Oven tripped on baking setting. | Wolf Appliance | DO3050TE/S/T | No | Single Family | Kitchen wall oven. | No | No | No | No |  | https://www.formstack.com/admin/download/file/17222954717
2024-11-17 14:25 | Steve | Laurencio | 18079 | PO BOX 645 |  | Bedford | MA | 1730 | 978 621-7221 | Electrician | steve@desousaelectric.com | SquareD Hom240GFIC | Breaker | 0 | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-10 | 2024-10-10 | 976 Main St. Unit 4 |  | Melrose | MA |  | Circuit breaker tripped when baking setting is turned Off. | Cafe | CES700P4M3W2 | No | Apartment building | Kitchen stove. | No | No | No | No |  | https://www.formstack.com/admin/download/file/17222993605
2024-11-17 19:56 | Paul | Eklund | 54252 | 210 Lisle St. |  | Braintree | MA | 2184 | 617-750-8798 | owner | pauleklundelectrical@gmail.com | siemens Q120DFP | Breaker | none | 20 |  | 1 Pole | Siemens | Residence |  | 2024-11-15 | 2024-11-13 | 15 Westover St. |  | West Roxbury | MA |  | The refrigerator keeps tripping the gfi portion of the circuit breaker | Thermador | T36FT820NS | none / dedicated circuit | Owner occupied 2 family | This is a dedicated circuit for a kitchen refridgerator. The fridge keeps tripping the circuit breaker | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17223725019
2024-11-18 12:38 | Allan | Fernandes | 55685 | 3 Isabella St |  | Quincy | MA | 2169 | 6178778181 | Electrician | alfernandes.electrical@gmail.com | Q120DFP | Breaker | none |  |  | 1 Pole | Siemens | Residence |  | 2024-11-11 | 2024-10-21 | 12 Franklin Rodgers Road |  | Hingham | MA | 2043 | unit is tripping the breaker after running for a very short amount of time. Yale appliance tested until and it is pulling 14.5 A while running. | Beko | MWDR24100SS |  | residence | kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17226596710
2024-11-18 15:18 | Christopher | Veliotis | 14765 | 13 Crabapple Dr. |  | Berkley | MA | 2779 | 508-880-0490 | Owner, Veliotis Electric LLC | cv1218@aol.com | QF250A | Breaker | No | 50 |  | 2 Pole | Siemens | Residence |  | 2024-10-31 | 2024-10-18 | 85 Pilgrim Rd. |  | Needham | MA | 2492 | Breaker services a double wall oven, after replacing the breaker with an equal 50amp. GFCI breaker of the same manufacturer the tripping would still occur. The tripping would happen aproxx. 2-3 minuets into the cooking cycle. | GE | CTD70DP2N3S1 | None | Single family | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17227623579
2024-11-18 15:25 | Christopher | Veliotis | 14765 | 13 Crabapple Dr. |  | Berkley | MA | 2779 | 508-880-0490 | Owner, Veliotis Electric LLC | cv1218@aol.com | BRN230GF | Breaker | no | 30 |  | 2 Pole | Eaton | Residence |  | 2024-11-08 | 2024-10-20 | 10 Goodwin Dr. |  | Foxboro | MA | 20235 | Single wall oven would trip GFCI breaker approx. 1-3 minuets into the cooking cycle. Changed out and replaced the breaker with a 30amp. GFCI breaker of the same manufacturer with the same results. | GE | PTS7000SN355 | no | Singe family | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17227673706
2024-11-18 19:00 | Douglas | Blume | 32056 | 124 cook rd | Po box 142 | Sheffield | MA | 1257 | 413-229-2784 | Owner | dwb123@roadrunner.com | Leviton LB250-G | Breaker | None | 50 |  | 2 Pole | Leviton | Residence |  | 2024-11-18 | 2024-11-18 | [5 empty] | Induction range trips when plugged in to 4 wire receptacle protected by breaker | Frigidaire | PCF13670AF | None | Kitchen | Induction range trips breaker | No | No | No | No |  | https://www.formstack.com/admin/download/file/17229650327
2024-11-18 19:08 | Douglas | Blume | 32056 | 124 cook rd | Po box 142 | Sheffield | MA | 1257 | 413-229-2784 | Electrician | dwb123@roadrunner.com | Leviton | Breaker | LB230-G | 30 |  | 2 Pole | Leviton | Residence |  | 2024-11-18 | 2024-11-18 | 42 bosworth rd. |  | Sandisfield | MA | 1245 | Electric drier trips gfci breaker when plugged in | Electrolux | ELFE7637ATO | None | Laundry | Electric drier trips gfci breaker when plugged in | No | No | No | No |  | https://www.formstack.com/admin/download/file/17229680078
2024-11-18 19:14 | Douglas | Blume | 32056 | 124 cook rd | Po box 142 | Sheffield | MA | 1257 | 413-229-2784 | Electrician | dwb123@roadrunner.com | Leviton LB120-DFT | Breaker | Arc fault | 20 |  | 1 Pole | Leviton | Residence |  | 2024-11-18 | 2024-11-18 | 42 bosworth rd |  | Sandisfield | MA | 1245 | Refrigerator trips breaker when plugged in | Frigidaire | GRMC2273CD02 | None | Kitchen home | Kitchen frig trips | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/17229702349
2024-11-18 21:34 | John | Novello | 12791 | 167 Winn Street |  | Woburn | MA | 1801 | 9782837348 | Electrician | john.novello@gmail.com | Eaton-Cutler Hammer-Westinghouse GFCB120 | Breaker | NA | 20 |  | 1 Pole | Eaton | Residence |  | 2024-10-15 | 2024-10-15 | [5 empty] | Tripping after washing machine is started. | Miele front load washing machine. | wwd160 wcs |  | Single family laundry closet. | 1st floor laundry closet | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17230174331
2024-11-20 12:30 | Aniano | Carvalho | 57083 | 20 grover st |  | Malden | MA | 2148 | 8572331631 | Eletrician | anianocarvalho@hotmail.com | QF240A | Breaker | No | 40 |  | 2 Pole | Siemens | Residence |  | 2024-11-19 | 2024-11-05 | 343 commercial st, Apt 502 |  | Boston | MA | 2109 | The breaker is tripping when the oven is turned on. | Wolf appliance ink | CONAPPWM |  | Apartment | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17238135155
2024-11-20 14:07 | Christopher | Veliotis | 14765 | 13 Crabapple Dr. |  | Berkley | MA | 2779 | 508-880-0490 | Owner | cv1218@aol.com | BRN230GE | Breaker | no | 30 | 0 | 2 Pole | Eaton | Residence |  | 2024-10-20 | 2024-10-01 | 95 Sperry lane |  | Attleboro | MA | 2760 | Single wall oven would trip GFCI breaker usually 1-3 minuets after appliance was turned on. Changed breaker with replacement GFCI type of the same manufacturer with the same results. | LG | WSEP4723F /00 | none | Single family | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17238711179
2024-11-20 17:22 | Matthew | Costa | 22688 | 18 Arsene way |  | Fairhaven | MA | 2719 | 508-717-9213 | owner | Mcosta@macoelectric.com | HOM250GFICP | Breaker | pig tail breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-18 | 2024-11-13 | 18 Arsene way |  |  |  |  | Electric Range on 1st floor unit, Heats up on burners however 30 seconds after oven is turned on heat element trips the breaker | whirlpool | WFES3030RS0 |  | Kitchen | Range | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17239928351
2024-11-20 17:22 | Matthew | Costa | 22688 | 18 Arsene way |  | Fairhaven | MA | 2719 | 508-717-9213 | owner | Mcosta@macoelectric.com | HOM250GFICP | Breaker | pig tail breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-18 | 2024-11-13 | 18 Arsene way |  |  |  |  | Electric Range on 1st floor unit, Heats up on burners however 30 seconds after oven is turned on heat element trips the breaker | whirlpool | WFES3030RS0 |  | Kitchen | Range | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17239929364
2024-11-20 17:30 | Matthew | Costa | 22688 | 18 Arsene way |  | Fairhaven | MA | 2719 | 5087179213 | owner | Mcosta@macoelectric.com | HOM250GFICP | Breaker | pigtail breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-13 | 2024-11-18 | 50 Spring street unit B |  | Fairhaven | MA | 2719 | second floor unit, electric cook top works fine but once the oven is turned on 30 seconds later the breaker trips | Whirlpool | WFES3030RS0 |  | Residence | Kitchen range in second floor | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17239966697
2024-11-21 13:37 | Kyle | Aussant | 22084 | 2180 Mendon Road, Ste 7 |  | Cumberland | RI | 2864 | 4013652511 | President | office@aussantelectric.net | GE/ THQL2140GFT | Breaker | GFI breaker | 40 | None | 2 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/17243937390 | 2024-11-20 | 2024-11-20 | 92 Milton Street |  | Waltham | MA | 2453 | As soon as we turn the stove on, the breaker trips immediately. When the standard breaker is put in it holds. The amperage and voltage were checked on the regular breaker and continued to hold. the continuity was also checked to make sure everything was fine, and it was. | Samsung | Model NE63A6511SS | NoneGE | Single family home | Kitchen | Yes | No | No | No | https://www.formstack.com/admin/download/file/17243937404 | https://www.formstack.com/admin/download/file/17243937405
2024-11-21 15:44 | Moises | Docanto | 23130 | 4980 N main st Apt 408 |  | Fall River | MA | 2720 | 6127 849-0920 | Owner of DOCANTO ELECTRICAL SOLUTIONS INC | info@docantoelectrical.com | GFTCB250 | Breaker | Gfci Breaker | 50 | 240v | 2 Pole | Eaton | Residence |  | 2024-11-21 | 2024-10-14 | 35 woodruff rd |  | Walpole | MA | 2081 | We install a GFCI breaker soon the double oven kicks it trips the breaker less then 40sec. | Wolf Appliance INC Wall Oven | D03050TM/S/T | NO | Single Family Home | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17244703017
2024-11-21 15:58 | Moises | Docanto | 23130 | 4980 N main st Apt 408 |  | Fall River | MA | 2720 | 617 849-0920 | Owner Of Docanto Electrical Solutions INC | Info@docantoelectrical.com | BRN250GFCS | Breaker | Gfci Breaker | 50 | 240v | 2 Pole | Eaton | Residence |  | 2024-11-21 | 2024-10-14 | 35 woodruff rd |  | Walpole | MA | 2081 | Manufacture recommended not to put cooktop on a ground fault interrupter because it will cause interruption of operation. | Wolf Appliance INC | CI36560T/S CookTOP | NO | Single Family Home | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17244784422
2024-11-22 13:55 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 508-297-7700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-20 | 2024-11-19 | 660 Main St. |  | Worcester | MA |  | Apt 603¦Over portion cannot be used without tripping breaker. Have contacted E before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM2WW | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17248813108
2024-11-22 13:58 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 508-297-7700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-20 | 2024-11-19 | 660 Main St. |  | Worcester | MA |  | Apt 503¦Serial-SJHZ915703R¦Over portion cannot be used without tripping breaker. Have contacted E before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM2WW | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17248827457
2024-11-22 14:02 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 508-297-7700 | Foreman | matthies.sean@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-20 | 2024-11-19 | 660 Main St. |  | Worcester | MA |  | Apt 403¦serial-SQHZ917894R¦Over portion cannot be used without tripping breaker. Have contacted E before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM2WW | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17248852965
2024-11-22 14:05 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 508-297-7700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-20 | 2024-11-19 | 660 Main St. |  | Worcester | MA |  | Apt 303¦Serial-HZ915697R¦Over portion cannot be used without tripping breaker. Have contacted E before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM2WW | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17248865113
2024-11-22 14:07 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton` | MA | 2076 | 508-297-7700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-20 | 2024-11-19 | 660 Main St. |  | Worcester | MA |  | Apt 203¦Serial-HZ920433R¦Over portion cannot be used without tripping breaker. Have contacted E before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17248876686
2024-11-25 08:35 | Eric | Conrad | 40723 | 23 Buttonwoods Ave |  | Haverhill | MA | 1830 | 781-844-8676 | Owner/Electrician | conradelectric23@gmail.com | Siemans/QF250A | Breaker | Double pole 50 amp GFCI | 50 |  | 2 Pole | Siemens | Residence |  | 2024-11-21 | 2024-11-20 |  |  | Brookline | MA | 2445 | Breaker would trip intermittently. | Tharmador | PRI36LBH/04 FD0407 Z-NR00040 | None. | Single family. | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17256465980
2024-11-25 08:51 | Eric | Conrad | 40723 | 23 Buttonwoods Ave |  | Haverhill | MA | 1830 | 781-844-8676 | Owner/Electrician | conradelectric23@gmail.com | Siemans/Q120DFN | Breaker | Single Pole 20 amp dual function | 20 |  | 1 Pole | Siemens | Residence |  | 2024-11-21 | 2024-11-20 |  |  | Brookline | MA | 2445 | Washer trips intermittently. | Miele | 11619650 | None | Single family | Laundry | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17256534612
2024-11-25 08:56 | Eric | Conrad | 40723 | 23 Buttonwoods Ave |  | Haverhill | MA | 1830 | 781-844-8676 | Owner/Electrician | conradelectric23@gmail.com | Siemans/Q120DFN | Breaker | Single pole 20 amp dual function | 20 |  | 1 Pole | Siemens | Residence |  | 2024-11-21 | 2024-11-20 |  |  | Brookline | MA | 2445 | Dryer trips breaker intermittently. | Miele | WXD160 11614070 | None | Single family | Laundry | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17256556700
2024-11-25 15:35 | Brett | Nasuti | 16007 | 336 King St |  | Littleton | MA | 1460 | 7745737534 | Assistant Project Manager | bnasuti@nauset.com | THQB2130 | Breaker | AFC | 30 |  | 2 Pole | ABB | Commercial |  | 2024-11-22 | 2024-08-15 | [5 empty] | AFCI Breakers are causing a nuisance trip with the Condenser Units, will not remain operational. Mini split HVAC systems will trip and power down in the middle of the night leaving residents waking up in freezing units. Have had the electricians as well as Samsung out to inspect the installation of the systems. Through process of elimination we have tested out all parts of our system leaving the Samsung representative and our electrician to determine that the issue lies with the Arch Fault Breakers. | Samsung | AJ020TXS3CH | AR07TSFABWKN, AR09TSFABWKN | Elder Living center | Entire units are without heat and or cooling capabilities. When the rooftop unit trips it causes the mini splits within the unit to power off. Each unit contains between 2-4 mini splits and when the breaker trips it causes all mini splits to power down leaving non-conditioned spaces with owners living in these spaces. | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17259161700
2024-11-25 16:17 | Axhem | Nonaj | 55501 | 960 S Franklin St |  | Holbrook | MA | 02343-2051 | 9172548926 | Electrician | ajelectrician18@gmail.com | 155535 | Breaker | None | 40 |  | 2 Pole | Leviton | Residence |  | 2024-11-25 | 2024-11-21 | 24 volunter rd |  | Hingham | MA | 2043 | As the double oven starts it trips the GFCI, with regular 40amp breaker doesn't trip | GE Cafe | CTD70DP2N1S1 |  | Residential | Kitchen double oven | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17259416325 | https://www.formstack.com/admin/download/file/17259416326
2024-11-26 15:37 | Jacob | Radzik | 52982 | 8 rose ln |  | Oxford | MA | 1540 | 7744774747 | Electrician | jake@phcprecision.com | Hom240gfic | Breaker | . | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-26 | 2024-11-22 | 123 Worthington ave |  |  | MA | 1545 | Oven is consistently tripping gfci breaker | Spectra | Jbp85c0b4cc | No | Kitchen | Kitchen range | No | No | No | No | https://www.formstack.com/admin/download/file/17264359787 | https://www.formstack.com/admin/download/file/17264359788
2024-11-26 19:45 | Michael | Ferguson | 54163 | 11 Wheeler Road |  | Billerica | MA | 1821 | 9785809064 | Journeyman | mfergs1919@gmail.com | QF250A | Breaker | NA | 50 |  | 2 Pole | Siemens | Residence |  | 2024-02-10 | 2024-02-09 | 20 Partridge circle |  | Waltham | MA | 1821 | Breaker trips when stovetop and oven ate being used | Miele | HR14223I | Dedicated | Single family | Kitchen stove | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17265496352
2024-11-27 07:41 | Stephen | Cosgrove | 39483 | 410 Pratt Street |  | Mansfield | MA | 2048 | 5089545908 | owner | sjcosgrove@msn.com | square D | Breaker | breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-20 | 2024-11-19 | 8 Countryclub lane |  | Foxboro | MA | 2035 | oven will run for 2 minutes than trip tried replacing breaker same results ¦installed standard qo240 breaker now working | fisher&paykel | ob30dpptx1fpu | no | single family home | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17266870865
2024-11-27 19:30 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-26 | 2024-11-25 | 660 Main St. |  | Worcester | MA |  | Apt 605¦¦Over portion cannot be used without tripping breaker. Have contacted E¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | ge | ras240dm3ww | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17269787495
2024-11-27 19:32 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | martthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-27 | 2024-11-26 | 660 Main St. |  | Worcester | MA |  | Apt 505¦serial HZ919952R¦Over portion cannot be used without tripping breaker. Have contacted E¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | ge | RAS240DM3WW | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17269791956
2024-11-27 19:34 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-27 | 2024-11-26 | 660 Main St. |  | Worcester | MA |  | Apt 405¦Serial HZ920592R¦¦Over portion cannot be used without tripping breaker. Have contacted E¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | ge | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17269798093
2024-11-27 19:37 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-27 | 2024-11-26 | 660 Main St. |  | Worcester | MA |  | Apt 305¦Serial-HZ920600R¦¦Over portion cannot be used without tripping breaker. Have contacted E¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | ge | RAS240DM3WW | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17269804419
2024-11-27 19:39 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-27 | 2024-11-26 | 660 Main St. |  | Worcester | MA |  | Apt 205¦Serial-HZ919173R¦¦Over portion cannot be used without tripping breaker. Have contacted E¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17269809660
2024-11-29 07:58 | Christopher | Veliotis | 14765 | 13 Crabapple Dr. |  | Berkley | MA | 2779 | 508-880-0490 | Owner | cv1218@aol.com | QF250A | Breaker | no | 50 | 0 | 2 Pole | Siemens | Residence |  | 2024-10-22 | 2024-10-10 | 78 Sylvan Drive |  | Barnstable | MA | 2601 | Wall oven would operate for approx. 2 minuets and the GFCI breaker would trip. This happened on numerous occasions. I replaced the breaker with another 50amp. GFCI breaker and same manufacturer only to have the same results. All aspects of the circuit conductors were checked including the equipment grounding conductor. | Whirlpool | WOED5030LB01 | None | Single family dwelling | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17273440530
2024-12-01 10:37 | thomas | gallagher | 16482 | 16 west street |  | northborough | MA | 1532 | 508-330-0872 | electrical contractor | gallagherelectric@verizon.net | gftcb250cs | Breaker | ? | 50 |  | 2 Pole | Eaton | Residence |  | 2024-11-15 | 2024-11-01 | 4 blacksmith drive |  | sudbury | MA | 1776 | gfci trips when stove is used | bosch | his8055u/05 | no | residential dwelling | kitchen range | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17278339285 | https://www.formstack.com/admin/download/file/17278339286
2024-12-01 12:46 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor | castlecp@hotmail.com | BRN250GFCI | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-11-24 | 2024-11-24 | 35 Old Beaver Brook Rd. |  | Acton | MA | 1720 | Installed a new 2 pole 50 amp GFCI breaker on a new wall oven. It Continuously trips. | GE | PTD7000SN5SS |  | Condo | Kitchen. | No | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17278568747
2024-12-02 06:57 | Joshua | Bedard | 2641 | 286 S Elm St |  | Manchester | NH | 3103 | 9788157160 | General Foreman | jdbedard12@yahoo.com | Siemens QF250A | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2024-11-18 | 2024-11-18 | 56 Carmel Rd. |  | Andover | MA | 1810 | When the circuit is under load the circuit breaker trips. Example is when a induction burner is turned on. | Bertazzoni | Pro486igfepxt | none | single family kitchen range | Kitchen range only | No | No | No | No |  | https://www.formstack.com/admin/download/file/17280837553
2024-12-02 10:07 | Tony | Marroquin | 14426 | 26 Whalen Rd |  | Hopkinton | MA | 1748 | 9787997274 | Construction Manager | amarroquin@tollbrothers.com | GFTCB250 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2024-11-21 | 2024-03-12 | [5 empty] | Oven tripping during normal use. | KitchenAid | KOSE500ESS |  | Single Family | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17281502572
2024-12-02 14:02 | Gerald | Hebert | 18303 | 55 6TH road |  | Woburn | MA | 1801 | 5082699493 | Director of operations | gerry.hebert@bostonsolar.us | Eaton BRN250GF | Breaker | NONE | 50 |  | 2 Pole | Eaton | Residence |  | 2024-09-09 | 2024-09-09 | 2Exeter Way |  | Andover | MA | 1810 | After installing a new service and changed the conductor to the electrical panel to a 4 conductor, we then changed the conductor to a 4 wire to the existing range and installed a GFCI breaker. once installed, the breaker immediately tripped on ground fault. | GE | JBS60RF3SS | NONE | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17283080619
2024-12-02 14:50 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-01 | 2024-12-02 | 280 Martins Landing Unit # 409 |  | North Reading | MA | 1864 | When warming up oven | Whirlpool | WFE550S0LZ3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17283423977
2024-12-02 14:57 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-06 | 2024-10-07 | 15 Archer Drive |  | Woburn | MA | 1801 | When warming up oven | Whirlpool | WFE515S0JZ3 |  | Townhouse | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17283475069
2024-12-02 15:06 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-19 | 2024-11-20 | 250 Martins Landing Unit # 201 |  | North Reading | MA | 1864 | When warming up oven | Whirpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17283540438
2024-12-02 15:11 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-01 | 2024-12-02 | 260 Martins Landing Unit # 409 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE775HOHZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17283579292
2024-12-02 15:16 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-20 | 2024-11-21 | 2 Winslow Lane Unit # 308 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17283612533
2024-12-02 15:20 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-19 | 2024-11-20 | 2 Stratton Drive Unit # 204 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | K0EC530PSS00 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17283635548
2024-12-02 15:22 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-25 | 2024-11-26 | 6308 Peters Farm Way |  | Westborough | MA | 1581 | When warming up oven | Whirlpool | WFE51550JS4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17283652478
2024-12-02 19:00 | Christopher | Trites | 40129 | 7 Kosciusko St |  | Woburn | MA | 01801-3863 | 7815898967 | Master Electrician | christrites.kes@gmail.com | Eaton GFTCB250 | Breaker | GFCI Circuit Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-11-21 | 2024-11-14 | 83 lincoln road |  | Lincoln | MA | 1773 | New electric range. Breaker trips randomly during cooking processes | Fisher Paykel | OR36SCI6X1 | none | Kitchen | New Kitchen Electric Range | No | No | No | No |  | https://www.formstack.com/admin/download/file/17284813638
2024-12-03 12:07 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-10 | 2024-10-11 | 4 Stratton Drive Unit # 305 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | K0EC30PPS00 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17287997177
2024-12-03 12:10 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-06 | 2024-10-07 | 2 Stratton Drive Unit # 206 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE515S0JS3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288015774
2024-12-03 12:13 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-11 | 2024-11-12 | 260 Martins Landing Unit # 204 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE515S0JS3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288035490
2024-12-03 12:16 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-10 | 2024-11-11 | 280 Martins Landing Unit # 503 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288054364
2024-12-03 12:18 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-10 | 2024-11-11 | 6405 Peters Farm Way |  | Westborough | MA | 1581 | When warming up the oven | Whirlpool | WFE550S0LZ3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288072067
2024-12-03 12:21 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-11 | 2024-11-12 | 2 Stratton Drive Unit # 404 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288088123
2024-12-03 12:23 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-14 | 2024-11-15 | 2 Stratton Drive Unit # 306 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288105509
2024-12-03 12:26 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-19 | 2024-11-20 | 2 Winslow Lane Unit # 111 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288128427
2024-12-03 12:28 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-19 | 2024-11-20 | 2 Winslow Lane Unit # 408 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | WFE51550JSE |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288143895
2024-12-03 12:33 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-17 | 2024-10-18 | 4 Stratton Drive Unit # 405 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288173021
2024-12-03 12:35 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-18 | 2024-10-19 | 4 Stratton Drive Unit # 406 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288194655
2024-12-03 12:37 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 6213 Peters Farm Way |  | Westborough | MA | 1581 | When warming up the oven | Whirlpool | WFE550S0LZ3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288216108
2024-12-03 12:40 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 6401 Peters Farm Way |  | Westborough | MA | 1581 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288230848
2024-12-03 12:42 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-21 | 2024-11-22 | 4 Stratton Drive Unit # 207 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288246663
2024-12-03 13:41 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 101 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288645374
2024-12-03 13:43 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 102 |  | Wobur | MA | 1801 | When warming up the oven | hirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288658490
2024-12-03 13:45 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 105 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288673665
2024-12-03 13:48 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 106 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288692077
2024-12-03 13:50 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 107 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288703607
2024-12-03 13:52 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 108 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288715163
2024-12-03 13:54 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 109 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288725194
2024-12-03 13:56 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 201 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288736781
2024-12-03 14:23 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 202 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288920471
2024-12-03 14:26 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 203 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288939605
2024-12-03 14:28 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 204 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288954943
2024-12-03 14:30 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 206 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288970719
2024-12-03 14:32 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 208 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17288986825
2024-12-03 14:34 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 209 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17289002918
2024-12-03 14:36 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 302 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE51550JSE |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17289019651
2024-12-03 14:39 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 304 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE51550JSE |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17289041397
2024-12-03 14:41 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 306 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE51550JSE |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17289055604
2024-12-03 14:43 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A |  | 5 | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 307 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE51550JSE |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17289076317
2024-12-03 14:45 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 308 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE51550JSE |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17289091271
2024-12-03 14:47 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 309 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE51550JSE |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17289106470
2024-12-03 14:49 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 401 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE51550JSE |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17289121377
2024-12-03 14:51 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 402 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE51550JSE |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17289137848
2024-12-03 14:53 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 403 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE51550JSE |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17289153435
2024-12-03 14:55 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 404 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE51550JSE |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17289168151
2024-12-03 14:57 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 408 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE51550JSE |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17289182636
2024-12-03 14:59 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-24 | 2024-11-25 | 4 Stratton Drive Unit # 409 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE51550JSE |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17289196624
2024-12-04 21:37 | David | Eldridge | 36787 | 15 Woodside Ter |  | Woburn | MA | 1801 | 9783603319 | Owner | dsparky1228@aol.com | GE / THoL2140GFT2P | Breaker | Breaker | 40 | 40 | 2 Pole | ABB | Residence |  | 2024-11-26 | 2024-11-26 | 15 Woodside Ter |  | Woburn | MA | 1801 | Put the rang on Bake @ 350 it per heated no problem after 10 minutes or so it tripped the GFCI¦Pulled the range out of its spot unplug the unit opened up the unit and charge wiring to the cord . Pulled the plug out of the wall and checked that out and that was good put everything back together and repeated same results. Put a regular 2pole breaker in the panel . | Frigidaire | GCF13060BF | None | House | Kitchen Range | No | No | No | No |  | https://www.formstack.com/admin/download/file/17296245761
2024-12-04 22:55 | David | Eldridge | 36787 | 15 Woodside Ter |  | Woburn | MA | 1801 | 978-360-3319 | Owner | dsparky1228@aol.com | GE/thil2140gft2p | Breaker | Breaker | 40 | 40 | 2 Pole | ABB | Residence |  | 2024-11-26 | 2024-11-26 | 705 lowell st |  | Lynnfield | MA |  | Preheated the range on bake @350 preheated no problem after about 10 minutes or so it tripped the GFCI breaker . Pulled the range out of its spot unplugged the unit opened up the unit to check the wiring @ the cord end and that was good pulled the plug out of the wall and checked that and that was good put everything back together and repeated same results. Installed a regular 2 pole breaker in the panel. | Frigidaire | Gcf13060BF | None | House | Kitchen Range | No | No | No | No |  | https://www.formstack.com/admin/download/file/17296442762
2024-12-05 09:14 | christopher | anastasi | 13178 | 33 rock rd |  | tyngsboro | MA | 1879 | 9789447088 | electrician | canastasi@cpsgens.com | THQL2130GFTP | Breaker | breaker | 30 |  | 2 Pole | ABB | Residence |  | 2024-11-25 | 2024-12-25 | 2 bittersweet lane |  | andover | MA | 1810 | 50 year old dryer keeps tripping gfci breaker | whirlpool | tbd1 |  | single family home | clothes dryer trips when installed on gfci breaker | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/17297748768
2024-12-05 10:58 | Scott | Jarry | 2727 | 79 granby rd |  | South hadley | MA | 1075 | 4136935159 | Electrician | snkbja@gmail.com | Square D Homeline 4884006004 | Breaker | 2-pole breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-28 | 2024-06-17 | [5 empty] | Baking cookies and after 20 minutes breaker tripped. Amp probed each line leg and reading was 10amps on each. Checked stove to make sure jumper was removed and it was. Checked receptacle and all was good. Reinstalled 2-pole 40amp breaker to assure the GFCI wouldn't be the factor if tripped. Before changing breaker we had the oven on for over 30 minutes with no incident. | Amana | AER5830VAB1 | None | Kitchen | The oven would trip after about 20 mins of baking. It tripped 4 times in one day while baking. | No | No | No | No |  | https://www.formstack.com/admin/download/file/17298287069
2024-12-05 14:31 | Brett | Nasuti | 16007 | 336 King St |  | Littleton | MA | 1460 | 7745737534 | Assistant Project Manager | bnasuti@nauset.com | THQB2130 | Breaker | AFC | 30 |  | 2 Pole | ABB | Commercial |  | 2024-11-22 | 2024-08-15 | [5 empty] | GFCI Breakers causing a nuisance trip with the refrigerators. Causes fridge to power down at random. | General Electric | GNE25JYKHFFS |  | 50 plus community | Kitchens, at the refrigerators, in all units continuously cause breakers to nuisance trip | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17299589782
2024-12-06 09:16 | Christine | Miller | 60582 | 16 pine street |  | Adams | MA | 1220 | 413-485-8510 | Electrician | christine.miller@trinity-solar.com | Hom240gfi | Breaker | 2 pole | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17302895484 | 2024-12-06 | 2024-11-08 | [5 empty] | Breaker tripped when oven was in use | Maytag | Mer5750bab | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17302895497 | https://www.formstack.com/admin/download/file/17302895498
2024-12-06 14:06 | Philip | Mendonca | 10757 | 6R Mount Vernon St. |  | Arlington | MA | 2476 | 6178885434 | Electrician | philipselectric@gmail.com | Siemens ITE Q230GF | Breaker | no | 50 |  | 2 Pole | Siemens | Residence |  | 2024-12-04 | 2024-12-04 | 29 Academy St |  | Arlington | MA | 2476 | tripping after working for 10 minutes | Frigidaire | fcf13083as |  | kitchen | kitchen stove | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17304513527
2024-12-06 15:26 | Alexander | Bielunis | 8653 | 8 Sequoia Dr |  | Holyoke | MA | 1040 | 4135622988 | Master Electrician/ MGR | ageelectricllc@gmail.com | Sq D | Breaker | 0 | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-06 | 2024-12-06 | 11 Montague Rd |  | Shutesbury | MA | 1072 | Range Trips Breaker | Bosch | 00634738 H11P056U | 0 | Residential Kitchen | Kitchen Range | No | No | No | No |  | https://www.formstack.com/admin/download/file/17304954550
2024-12-06 15:57 | Andrew | Harland | 21030 | Harland Electric | PO Box 94 | Littleton, MA | MA | 1460 | 9784868154 | President | andy@harlandelectric.com | Square D Homeline HOM250GFI | Breaker | Homeline | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-04 | 2024-11-04 | 116 Willow St |  | Acton | MA | 1720 | Installed new 50A 4 wire range circuit. GFCI breaker tripped when oven preheated. Removed GFCI breaker, installed 2 pole breaker, ran oven at 325 for 20 minutes to bake off any moisture, reinstalled GFCI breaker. GFCI breaker continued to trip, oven could not be used. | Frigidaire | FFEH3054USE |  | Single Family | Kitchen range circuit | No | No | No | No | https://www.formstack.com/admin/download/file/17305124271 | https://www.formstack.com/admin/download/file/17305124272
2024-12-09 09:46 | Jonathan | Dykstra | 52998 | 115 Upper Gore Rd |  | Webster | MA | 1570 | 508-581-0289 | Electrician | jon@coreelectricalservices.com | Schneider Electric | Breaker | N/A | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-06 | 2024-12-05 | 401 Summer St |  | Westwood | MA | 2090 | Trips after a sort time of use or no use at all. Double checked all wiring. Manufacture states the cooktop is not recommended to be on a GFCI | Wolf | CI30460C/B | None | Single family | Electrical induction cooktop in kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17312224731
2024-12-10 11:47 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | Owner | JOHN@HENRYSELECTRICINC.COM | Square ""D"" / QO250 | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-05 | 2024-12-05 | 62 MAPLE HILL ROAD |  | WEST STOCKBRIDGE | MA | 1266 | Breaker does not hold, kept tripping. | BOSCH | HIS8655U |  | SINGLE FAMILY | KITCHEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/17319074633
2024-12-10 12:01 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | OWNER | JOHN@HENRYSELECTRICINC.COM | EATON / BR240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence |  | 2024-11-18 | 2024-11-18 | 129 HAYES HILL ROAD |  | MILL RIVER | MA | 1244 | Breaker does not hold, kept tripping. | FRIGIDAIRE | GCFI3060BF |  | SINGLE FAMILY | KITCHEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/17319194116
2024-12-10 14:50 | joe | silverio | 17118 | 78 G parker st |  | acton | MA | 1720 | 9788514900 | electrician | fourstarlighting@gmail.com | eaton | Breaker | breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-12-10 | 2024-11-14 | 78 G parker st |  | acton | MA | 1720 | once electric stove got to temperature would trip the GFI breaker | GE | ras200dm2ww | dedicated | apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17321075147
2024-12-10 21:20 | Michael | Ferguson | 54163 | 11 Wheeler Road |  | Billerica | MA | 1821 | 9785809064 | Journeyman | mfergs1919@gmail.com | Qf250a | Breaker | NA | 50 |  | 2 Pole | Siemens | Residence |  | 2024-11-16 | 2024-11-13 | 105 Sherman St |  | Belmont | MA | 2478 | Trips when oven preheats. | Cafe | CHS900P4MW2 | Dedicated | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17322843260
2024-12-11 06:53 | Seamus | O'Doherty | 16761 | 453 Clapboardtree Street |  | Westwood | MA | 2090 | 6177199603 | Electrician owner | kerryelectricco@gmail.com | Siemens QF250A | Breaker | circuit breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2024-12-09 | 2024-12-02 | 66 Yale st |  | winchester | MA | 1890 | As soon as stove is turned on circuit breaker trips | Bosch | HIS8655U | no | single residence | Kitchen stove | No | No | Yes | No | https://www.formstack.com/admin/download/file/17323791915 | https://www.formstack.com/admin/download/file/17323791916
2024-12-11 09:15 | Daniel | DelSignore | 50772 | 50 Rosewood dr. |  | seekonk | MA | 2771 | 5084005123 | electrical foreman | ddelelectric@gmail.com | Frigidaire Gallery 30-in | Breaker | Eaton | 50 |  | 2 Pole | Eaton | Residence |  | 2024-12-10 | 2024-11-10 | [5 empty] | Range trips when oven reaches a certain temp.¦Replaced with another 50a gfci breaker and still trips¦.¦Ground strap was removed on install of cord by me | Frigidaire | GCFI3060BF |  | Single family home | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17324195533
2024-12-11 12:01 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 508-297-7700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-10 | 2024-12-09 | 660 Main St. |  | Worcester | MA |  | Apt 609¦¦Over portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17325090290
2024-12-11 12:03 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | hom240gfic | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-10 | 2024-12-09 | 660 Main St. |  | Worcester | MA |  | Apt 509¦¦Over portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17325102913
2024-12-11 12:05 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 508-297-7700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-10 | 2024-12-09 | 660 Main St. |  | Worcester | MA |  | Apt 409¦¦Over portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17325113692
2024-12-11 12:07 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-10 | 2024-12-09 | 660 Main St. |  | Worcester | MA |  | Apt 309¦¦Over portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17325126307
2024-12-11 12:08 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-10 | 2024-12-09 | 660 Main St. |  | Worcester` | MA |  | Apt 209¦¦Over portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17325134756
2024-12-11 12:11 | Jeffrey | Derouen | 8601 | EAV Solutions LLC | 260A Main Street | Buzzards Bay | MA | 2532 | 5082457155 | Owner | jeff@eavsolutions.com | Siemens 50Q-R | Breaker | GFI | 50 |  | 1 Pole | Siemens | Residence |  | 2024-12-06 | 2024-12-06 | 32 Main Street |  | Hyannis | MA | 2601 | New stove does not work with GFI protected breaker ¦Breaker will not hold | GE | GRF500PV1SS |  | Kitchen | Stove does not work properly with GFI breaker | No | No | No | No |  | https://www.formstack.com/admin/download/file/17325147595
2024-12-11 18:03 | David | Ricciardelli | 35640 | 21 Columbus Ave |  | Saugus MA 01906 | MA | 1906 | 7812488827 | Electrician | ricciardelli@hotmail.com | QF230AP | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2024-12-06 | 2024-12-06 | 9 Cleveland Road |  | Peabody | MA | 1906 | Breaker trips immediately, even when unit isn't running. | LG | WKEX200HWA |  | Laundry | Dryer, stackable unit in the laundry room. | No | No | No | No |  | https://www.formstack.com/admin/download/file/17327339396
2024-12-12 11:14 | Nick | McElroy | 670 | 381 Old Falmouth Rd. | Suite #32 | MARSTONS MILLS | MA | 2648 | 5085664489 | President | Nick@capecodelectrician.com | HOM250GFICP | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-10 | 2024-12-09 | 61 Winterhoff Trail |  | Brewster | MA | 2631 | Breaker will not hold | Wolf | ci365c/b | no | Kitchen cooktop | kitchen cooktop | No | No | No | No |  | https://www.formstack.com/admin/download/file/17330178800
2024-12-12 15:35 | Steven | Rooney | 13678 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service department | Steven@Giombettielectric.com | qf250a | Breaker | ITE | 50 |  | 2 Pole | Siemens | Residence |  | 2024-12-03 | 2024-12-03 | 103 Frye Street Marlboro |  | Marlborough | MA | 1752 | trips instantly | Amana | AER5830van 0 |  | 2nd floor Kitchen stove | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17331902149
2024-12-12 15:42 | Steven | Rooney | 13678 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service Manger | Steven@Giombettielectric.com | Siemans | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2024-12-03 | 2024-12-03 | 103 Frye Street Marlboro |  | Marlborough | MA | 1752 | tripped instantly | Kitchen Aid | KERC500YBZL3 | na | 1st floor Kitchen | stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/17331937552
2024-12-12 15:47 | Steven | Rooney | 136789 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service Manger | Steven@Giombettielectric.com | q230gf | Breaker | na | 30 |  | 2 Pole | Siemens | Residence |  | 2024-12-03 | 2024-12-03 | 103 Frye Street Marlboro |  | Marlborough | MA | 1752 | tripped Instantly | Whirlpool | CEM2745FQ1 | na | Dryer | laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/17331970886
2024-12-12 15:56 | Matthew | Doremus | 2123 | 244 Cedar St. #3 |  | Somerville | MA | 2145 | 781-738-6180 | President | matt@symmetry-electric.com | BRN240GF | Breaker | n/a | 40 |  | 2 Pole | Eaton | Residence |  | 2024-11-08 | 2024-10-23 | 84 Crowninshield Rd |  | Brookline | MA |  | Oven powered on for 10 days. First 3 operations at regular bake had no nuissance tripping. Upon convection bake setting, GFCI instantly tripped. Continued to trip each time with convection bake setting | Thermador | PODS302B/02 |  | single family | kitchen | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17332022752 | https://www.formstack.com/admin/download/file/17332022753
2024-12-12 16:02 | Steven | Rooney | 13678 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service Manager | Steven@Giombettielectric.com | HOM250gfi | Breaker | na | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-10-16 | 2024-08-25 | 323 Hudson Rd |  | Stow | MA | 1752 | breaker would randomly trip | Maytag | MER8800FZ5 | none | kitchen | stove does not work | No | No | No | No |  | https://www.formstack.com/admin/download/file/17332057025
2024-12-13 09:16 | David | Pelletier | 57841 | 20 Pease Ave. |  | Monson | MA | 1057 | 413-544-8445 | Electrician | david.n1tqp@gmail.com | Hom230gfci | Breaker | Breaker | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-13 | 2024-12-13 | 11 Maplewood Dr. |  |  | MA | 1095 | Breaker trip as soon as you turned on the dryer. | Alliance | Ade3srgs177tw02 |  | Home | Laundry room in the basement. | No | No | No | No |  | https://www.formstack.com/admin/download/file/17334709859
2024-12-13 14:11 | William | Sanchez | 56731 | 527 Great Rd |  | Littleton | MA | 1460 | 9784860600 | Electrician | nwest@nashobaair.com | Sq D Homeline | Breaker | NONE | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17336214535 | 2024-12-09 | 2024-12-09 | 28 Skinners Rd |  | Groton | MA | 1450 | Customer replaced his oven three times because he thought the problem was the oven until an electrician let him know the GFCi tripping is a known problem. | Maytag | MFES6030RZ |  | Single family home | Oven in kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17336214548 | https://www.formstack.com/admin/download/file/17336214549
2024-12-13 18:13 | [11 empty] | MER8700DS1 | Cordset | Stove | 50 |  | 2 Pole | Leviton | Residence |  | 2024-12-04 | 2024-12-04 | 60 Elliott Street |  | Braintree | MA | 2184 | Ran a new 4 wire for the whirlpool stove. Installed a 4 wire receptacle and 2 pole GFCI breaker. After we turned on the breaker it immediately tripped. Once the stove was unplugged the GFCI breaker held. | Whirlpool | MER8700DS1 |  | Kitchen | Stove in the kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17337333908
2024-12-15 12:47 | Lucas | Ingellis | 23758 | 655 shelburne falls rd |  | conway | MA | 1341 | 413-559-1312 | owner | l.ingelliselectric@gmail.com | General electirc | Breaker | n/a | 50 | n/a | 2 Pole | ABB | Residence |  | 2024-11-27 | 2024-12-18 | 104 johnson rd |  | chicopee | MA | 1013 | stove was installed, breaker tripped tries troubleshooting found breaker kept tripping called AHJ and explained situation swapped out for a new breaker and issue was fixed | fridgeidaire | FCF13083AS | no | residental | the stove | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17342201350
2024-12-16 11:12 | Kevin | McKeown | 38083 | 52 Stanbro Street |  | Boston | MA | 2136 | 6178286000 | electrician | kmck7392@gmail.com | Siemans | Breaker | 2 pole 50amp | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17345442573 | 2024-12-06 | 2024-12-07 | 20 Neal St |  | Walpole | MA | 2081 | Turn oven on to 350 runs for about 15/20 mins then breaker trips | Wolf oven | DF60650CG/S/P | none | single family | Kitchen dual fuel Wolf range | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17345442592
2024-12-16 19:47 | BERNARD | LITCHFIELD | 14334 | 172 SOUTH SANDISFIELD ROAD |  | NEW MARLBOROUGH | MA | 1230 | 413 229 2606 | OWNER | litchfieldgang99@gmail.com | SCHNEIDER ELECT SQUARE D | Breaker | NONE | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-12 | 2024-11-12 | 145 CASTLE HILL AVE. |  | GREAT BARRINGTON | MA | 1230 | UPON ENERGIZING APPLIANCE THERE WAS AN INSTANT TRIP OF BREAKER FURTHER TEST OF CIRCUIT SHOWED NO ABNORMAL CONDITIONS EXISTED THIS OCCURED 4 ADDITIONAL TIMES. | WOLF | CI36560T/S | NONE | SINGLE FAMILY | KITCHEN WOLF INDUCTION COOKTOP | No | No | No | No |  | https://www.formstack.com/admin/download/file/17348259452
2024-12-16 21:42 | Mark | Roussel | 21100 | 33 old forge Ln |  | Sudbury | MA | 1776 | 9784438888 | Electrician | Baseball78@verizon.net | GE Model # THQL2150GFT2P | Breaker | Breaker | 50 |  | 2 Pole | ABB | Residence |  | 2024-12-13 | 2024-12-13 | 52 Gleason Rd |  | Lexington | MA | 2420 | The range trips consistently 5-20 minutes after oven being turned on | Frigidaire - Electrolux Range | GCFI306OBFC | nothing | single family house | the only thing affected is this 1 range | No | No | Yes | No | https://www.formstack.com/admin/download/file/17348585511 | https://www.formstack.com/admin/download/file/17348585512
2024-12-17 19:49 | Tiago | Felisbino | 57436 | 8 Riverbank ter |  | Billerica | MA | 1821 | 6175299170 | Electrician | felisbino.tiago@gmail.com | Siemens-QF250A | Breaker | 2 pole | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17355189951 | 2024-12-17 | 2024-12-17 | 3 Ordway Rd |  | Wellesley Hills |  |  | This Range (Thermador), Assembled in Europe, has Neutrals. The ground wires are not separated in the wiring diagram | Thermador | PRI36LBHU |  | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17355189964 | https://www.formstack.com/admin/download/file/17355189965
2024-12-17 20:16 | Tiago | Felisbino | 57436 | 8 Riverbank ter |  | Billerica | MA | 1821 | 617-529-9170 | Electrician | felisbino.tiago@gmail.com | Siemens-Q230AP | Breaker | Microwave/Oven | 30 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17355268861 | 2024-12-17 | 2024-12-17 | 3 Ordway Rd |  | Wellesley Hills | MA | 2481 | GFCI breaker is not compatible due to the wiring diagram having neutral and ground wiring together | Thermador | PODMCW31W |  | Single Family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17355268876 | https://www.formstack.com/admin/download/file/17355268879
2024-12-17 20:31 | Tiago | Felisbino | 57436 | 8 Riverbank ter |  | Billerica | MA | 1821 | 617-529-9170 | Electrician | Felisbino.tiago@gmail.com | Siemens-QF250A | Breaker | Oven | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17355307642 | 2024-12-17 | 2024-12-17 | 3 Ordway Rd |  | Wellesley | MA | 1821 | The GFCI breaker is not compatible with the appliance due to the wiring diagram having neutral and ground together | Thermador | PODMCW31W |  | Single Family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17355307655 | https://www.formstack.com/admin/download/file/17355307656
2024-12-18 07:30 | Steve | Daniels | 16467 | 895Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Master electrician | office@danielsel.com | Square D | Breaker | Homeline |  |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-17 | 2024-12-17 | 2 School House Road |  | Gloucester | MA | 1930 | Stove continually trips breaker | Stove | JB445EK4ES |  | Apartment | Stove continually tripping | No | No | No | No |  | https://www.formstack.com/admin/download/file/17356417246
2024-12-18 12:16 | Steve | Daniels | 16467 | 895 Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Master electrician | office@danielsel.com | Siemens | Breaker | NA |  |  | 2 Pole | Siemens | Residence |  | 2024-12-17 | 2024-12-17 | 29 Victor St- Unit 24 |  | Haverhill | MA | 1832 | Constantly tripping stove breaker | GE | JB256D M4BB |  | Kitchen | Kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/17357879229
2024-12-18 12:39 | Brandon | Daniels | 59827 | 895 Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | electrician | office@danielsel.com | Siemens | Breaker | NA |  |  | 2 Pole | Siemens | Residence |  | 2024-12-09 | 2024-12-09 | 28 Victor St UNit 21 |  | Haverhill | MA | 1832 | stove constantly tripping | GE | JB258DM1BB |  | Kitchen | kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/17358006198
2024-12-18 15:10 | Stephen | Daniels | 16467 | 895 Salem Street 2A |  | Groveland | MA | 1834 | 9783731393 | Electrician | office@danielsel.com | Siemens/ QPF 50 amp breaker | Breaker | GFI | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17358887269 | 2024-11-06 | 2024-12-09 | 23 victor street unit 13 |  | haverhill | MA | 1832 | frequent tripping for range | GE appliances | J B256D M3BB |  | apartment | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17358887282
2024-12-19 12:20 | GUSTAVO | SIMOES | 23674 | 12 WELLES WAY |  | CHILMARK | MA | 2535 | 7745634988 | OWNER | gustavo@gsselectricmv.com | LB240-G | Breaker | Regular 2-pole breaker | 40 | 40 | 2 Pole | Leviton | Residence | https://www.formstack.com/admin/download/file/17363408065 | 2024-12-18 | 2024-12-18 | 96 Washque ave |  | Edgartown | MA | 2539 | Circuit is for a dedicated Cooking Range, range doesn't require a neutral, once you turn on the GFCI overcurrent device, it trips immediately. | Wolf | IR30450/S/T | N/A | Single family dwelling | Kitchen. | No | No | No | No | https://www.formstack.com/admin/download/file/17363408079 | https://www.formstack.com/admin/download/file/17363408080
2024-12-22 22:23 | Corey | Hood | 8228 | 103 Lawton Road |  | Needham | MA | 2492 | 7819157358 | Owner | coreyhoodelectric@gmail.com | GFTCB250 | Breaker | plug on | 40 |  | 2 Pole | Eaton | Residence |  | 2024-12-20 | 2024-12-20 | [5 empty] | Ovens trips when starting to heat everytime | thermador | PO302W/05 | NONE | Single Family | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17373450522
2024-12-24 08:50 | Carl | Perkins | 11876 | 79 Cooley St, |  | AGAWAM | MA | 1001 | 4132043063 | Service electrician | no72gto@yahoo.com | Home230gfi | Breaker | Breaker | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-23 | 2024-12-23 | 297 Hermitage Dr. |  | Springfield | MA | 1119 | Dryer kept tripping breaker. | Whirlpool | Wed6200SW1 | None | Dwelling | Dryer shuts off | No | No | Yes | No | https://www.formstack.com/admin/download/file/17378063950 | https://www.formstack.com/admin/download/file/17378063951
2024-12-24 08:55 | Carl | Perkins | 11876 | 79 Cooley St |  | AGAWAM | MA | 1001 | 4132043063 | Service electrician | no72gto@yahoo.com | Home250gfi | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-23 | 2024-12-23 | 297 Hermitage Dr. |  | Springfield | MA | 1119 | Stove kept tripping GFI. | Frigidaire | Fef362mxesc | None | Dwelling | Kitchen stove stopped working. | No | No | Yes | No | https://www.formstack.com/admin/download/file/17378074420 | https://www.formstack.com/admin/download/file/17378074421
2024-12-25 12:11 | Robert | Burkett | 14236 | 193 L Street |  | Boston | MA | 2127 | 6173892257 | owner | burkettelectric@gmail.com | BF230 | Breaker | NA | 30 |  | 2 Pole | Siemens | Commercial |  | 2024-11-21 | 2024-11-21 | 155 Seaport Blvd |  | Boston | MA | 2210 | Breaker trips after machine heats water¦Happening everytime.¦Manufacturer of equipment sent out a tech and confirmed nothing wrong with machine | Bunn | IMIX-5, HWB 120/208-240 LED (DD) |  | kitchen | equipment outlet | No | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17379760158 | https://www.formstack.com/admin/download/file/17379760159
2024-12-25 12:21 | Robert | Burkett | 14236 | 193 L Street |  | Boston | MA | 2127 | 6173892257 | manager | burkettelectric@gmail.com | BF230 | Breaker | NA | 30 |  | 2 Pole | Siemens | Commercial | https://www.formstack.com/admin/download/file/17379768109 | 2024-12-19 | 2024-12-19 | 296 Cambridge St |  | Boston | MA | 2114 | Equipment electronics is conflicting with the GFCI¦ | Turbochef Technologies | Encore2 |  | Commercial | Equipment outlet | No | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17379768122 | https://www.formstack.com/admin/download/file/17379768123
2024-12-27 13:22 | MLSCHMITTELECTRIC | MLSCHMITTELECTRIC | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 413 733-7868 | Electrician | georgeb@mlschmittelectric.com | Square D Homeline AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-21 | 2024-06-21 | 37 Village green |  | East Longmeadow | MA | 1028 | Range trips breaker within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17385040650
2024-12-31 09:54 | MLSCHMITTELECTRIC | MLSCHMITTELECTRIC | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | (413) 733-7868 | Electrician | georgeb@mlschmittelectric.com | Square D Homeline AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-26 | 2024-06-26 | 38 Village Green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17394588492
2024-12-31 15:21 | Alexander | Bielunis | 8653 | 8 Sequoia Drive |  | Holyoke | MA | 1040 | 4132043762 | Master Electrician | ageelectricllc@gmail.com | CH250GFT | Breaker | none | 50 |  | 2 Pole | Eaton | Residence |  | 2024-12-16 | 2024-12-16 | 14 Ashley Circle |  | Amherst | MA | 1002 | Breaker Trips as soon as the Oven is turned on | GE | JTD3000SN3SS | NONE | Kitchen | Kitchen Oven | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17395708548
2024-12-31 17:36 | richard | bagni | 16024 | 83 alexander rd |  | billerica | MA | 1821 | 9788088992 | electrician | jnuzzo@murrayhills.com | square D | Breaker | breaker | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17396062577 | 2024-09-16 | 2024-09-02 | 19 ferullo drive |  | woburn | MA | 1801 | breaker trips as soon as you turn on oven | thermador | mem301ws/07 |  | single family dwelling | kitchen oven only | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17396062590 | https://www.formstack.com/admin/download/file/17396062591
2024-12-31 17:48 | RICHARD | BAGNI | 16024 | 83 alexander rd |  | billerica | MA | 1821 | 9788088992 | ELECTRICIAN | jnuzzo@murrayhills.com | SQUARE D | Breaker | BREAKER | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17396086551 | 2024-07-15 | 2024-07-01 | 30 FERULLO DRIVE |  | WOBURN | MA | 1801 | BREAKER POPS AS SOON AS YOU TURN OVEN ON | THERMADOR | MEM301WS/07 |  | SINGLE FAMILY DWELLING | KITCHEN | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17396086564 | https://www.formstack.com/admin/download/file/17396086565
2024-12-31 17:49 | RICHARD | BAGNI | 16024 | 83 alexander rd |  | billerica | MA | 1821 | 9788088992 | ELECTRICIAN | jnuzzo@murrayhills.com | SQUARE D | Breaker | BREAKER | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17396088397 | 2024-07-15 | 2024-07-01 | 30 FERULLO DRIVE |  | WOBURN | MA | 1801 | BREAKER POPS AS SOON AS YOU TURN OVEN ON | THERMADOR | MEM301WS/07 |  | SINGLE FAMILY DWELLING | KITCHEN | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17396088410 | https://www.formstack.com/admin/download/file/17396088411
2024-12-31 18:10 | RICHARD | BAGNI | 16024 | 83 alexander rd |  | billerica | MA | 1821 | 9788088992 | ELECTRICIAN | jnuzzo@murrayhills.com | SQUARE D | Breaker | BREAKER | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17396128943 | 2024-05-06 | 2024-04-22 | 10 SCOTT AVE |  | BURLINGTON | MA | 1803 | OVEN BREAKER TRIPS AS SOON AS YOU TURN IT ON | THERMADOR | MEM301WS/07 |  | SINGLE FAMILY DWELLING | KITCHEN | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17396128956 | https://www.formstack.com/admin/download/file/17396128957
2025-01-02 08:37 | Ryan | LaBrache | 22042 | 1 Summer Street |  | Watertown | MA | 2472 | 617-538-4851 | owner | ryan@lampasonabloomer.com | BRN230GF | Breaker | na | 30 |  | 2 Pole | Eaton | Residence |  | 2024-12-30 | 2024-10-07 | 8 Harvard Dr. |  | Milford | MA | 1757 | Breaker would trip instantly when starting dryer | GE | GTD33EASK0WW |  | single family | Laundry Room | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/17399213806
2025-01-02 12:55 | Italo | Azevedo | 55518 | 29 Beach st |  | Milford | MA | 1757 | 5083089826 | Journeyman | italo@imaelectric.com | Eaton BR | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2024-10-11 | 2024-10-11 | 28 Cheryl dr |  | Sharon | MA | 2067 | stove not compatible with GFCI breaker | WOLF | IR30450/S/T | NO | KITCHEN | KITCHEN STOVE | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17400609741
2025-01-02 13:07 | Stephen | Cosgrove | 39483 | 410 Pratt Street |  | Mansfield | MA | 2048 | 5089545908 | owner | sjcosgrove@msn.com | Eaton/brn230gf | Breaker | breaker | 30 |  | 2 Pole | Eaton | Residence |  | 2024-12-20 | 2024-12-19 | 194 Highland Avenue |  | Attleboro | MA | 2703 | breaker tripping when unit gets plugged in tried new breaker same thing replace with standard breaker no problems | samsung Clothes dryer | dv42h5200ew/a3 | no | laundryroom dryer | dryer | No | No | No | No |  | https://www.formstack.com/admin/download/file/17400672930
2025-01-03 13:52 | Brandon | Daniels | 59827 | 895 Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Electrician | office@danielsel.com | Siemens | Breaker | 50 |  |  | 2 Pole | Siemens | Residence |  | 2025-01-02 | 2025-01-02 | 28 Victor St unit 23 |  | Haverhill | MA | 1832 | Oven continually tripping the breaker | GE | JB256D M4BB |  | Apartment | Stove circuit tripping | No | No | No | No |  | https://www.formstack.com/admin/download/file/17405213514
2025-01-05 06:19 | Scott | Macdougall | 21193 | 79 | Westover Parkway | Norwood | MA | 2062 | 7742791423 | Owner | semacdougall2003@hotmail.com | Siemens | Breaker | Gfci breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17409304027 | 2024-10-07 | 2024-10-01 | 79, Westover Parkway |  | Norwood | MA | 2062 | Stove keeps tripping breaker. We tried 3 Siemens 2 pole 50 amp breakers and all of them tripped within a day. We then installed a 2 pole 50 amp regulator breaker and it has been fine | GE | GRF600AV1SS |  | Single family | Kitchen | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/17409304040
2025-01-07 09:47 | Joseph | Garnhum | 23401 | 18 Oak Ridge Ave | apt 2 | Salem | NH | 3079 | 6172858248 | Owner/Operator | GARNHUMES@GMAIL.COM | ITE Q230GF | Breaker | N/A | 30 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17417630771 | 2024-12-30 | 2024-12-30 | 8 Handel Road |  | Billerica | MA | 1821 | Plugged dryer in and breaker trips instantly. | GE | GUD27ESSM1WW | NONE | RESIDENTIAL HOME | BATHROOM DRYER RECEPTACLE CIRCUIT | No | Yes | Yes | No | https://www.formstack.com/admin/download/file/17417630785 | https://www.formstack.com/admin/download/file/17417630786
2025-01-07 11:40 | Daniels | Electric | 16467 | 895 Salem Street 2A |  | Groveland | MA | 1834 | 9783731393 | Electrician | office@danielsel.com | JB645EK9ES | Receptacle | Range | 50 |  | 2 Pole | Eaton | Residence |  | 2024-11-06 | 2025-01-06 | 3 Boston Way Unit 106 |  | Newburyport | MA | 1950 | Nuisance tripping breaker to stove ¦ | GE | JB645EK9ES |  | Apartment | Range tripping frequently | No | No | No | No | https://www.formstack.com/admin/download/file/17418298239 | https://www.formstack.com/admin/download/file/17418298240
2025-01-07 12:33 | MLSCHMITTELECTRIC | MLSCHMITTELECTRIC | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 413-733-7868 | Master Electrician | georgeb@mlschmittelectric.com | Square D Homeline AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-27 | 2024-06-27 | 39 Village green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17418633759
2025-01-07 12:55 | MLSCHMITTELECTRIC | MLSCHMITTELECTRIC | 13369 | 371 Taylor street |  | Springfield | MA | 1101 | 413-733-7868 | Master electrician | georgeb@mlschmittelectric.com | Square D Homeline AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-06-28 | 2024-06-28 | 40 Village green |  | East Longmeadow | MA | 1028 | Range trips within minutes of use. | Amana | W10175656 |  | Dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17418766935
2025-01-08 09:26 | Francis | Baudanza | 20326 | 102 South Rd |  | Bedford | MA | 1730 | 781-275-6662 | President/owner | baudanza@erols.com | Leviton LB250-GF | Breaker | GFCI | 50 |  | 2 Pole | Leviton | Residence |  | 2025-01-06 | 2024-12-17 | [5 empty] | Range trips the breaker as soon as it is plugged in. Connections to the range are correct, neutral and grounds are separated. | Bosch | HIS8655U |  | kitchen | kitchen range only | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17422754568
2025-01-08 14:23 | chris | anastasi | 21442 | 33 rock rd |  | Tyngsboro | MA | 1879 | 9789447088 | electrician | canastasi@cpsgens.com | qf250a | Breaker | breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2025-01-07 | 2025-01-06 | 755 Great Rd |  | Stow | MA | 1775 | breaker trips only when oven is plugged in | GE | jb655dk1cc |  | single family home | kitchen range | No | No | No | No |  | https://www.formstack.com/admin/download/file/17424969055
2025-01-08 23:19 | Mark | Roussel | 21100 | 33 Old Forge Lane |  | Sudbury | MA | 1776 | 978 443 8888 | Electrician | Baseball78@verizon.net | Leviton Model # M42-GFTR2-04W | Receptacle | Receptical | 20 | 20 | 1 Pole | Leviton | Commercial | https://www.formstack.com/admin/download/file/17427425267 | 2024-12-30 | 2024-12-30 | 167 Broad St |  | Hudson | MA | 1749 | After the installation of a brand new compressor the gfci constantly trips¦¦I have tried plugging the unit into other gfci outlets in the area with the same result | Mega Top Refrigerator | MSF8308GR | nothing | Commercial Kitchen | no other rooms are affected | No | No | Yes | No | https://www.formstack.com/admin/download/file/17427425281 | https://www.formstack.com/admin/download/file/17427425282
2025-01-09 11:27 | David | Niemi | 20725 | 8 Dunton Rd. |  | Wilmington | MA | 1887 | 6174176112 | Electrician | smoky989@comcast.net | BRN230GFCS | Breaker | ? | 30 |  | 2 Pole | Eaton | Residence |  | 2024-11-06 | 2024-11-06 | 61 Richfield Rd. |  | Arlington | MA |  | Breaker tripped regularly for a couple months. | Electrolux | ELFE7637ATO | None | single family | Laundry | No | No | No | No |  | https://www.formstack.com/admin/download/file/17429216451
2025-01-09 12:02 | Bryan | Dollard | 23498 | 472 West Broadway 101B | Suite 4 | boston | MA | 2127 | 7812667291 | president | bryan@bayelectricalcorp.com | thql2150gftzp | Breaker | na | 50 |  | 2 Pole | Eaton | Residence |  | 2024-12-23 | 2024-09-11 | 69 Bailey st #208 |  | dorchester | MA | 2124 | Stove keeps tripping after a few min. Put on regular breaker and turned on for an hour . Ran of gfci for few weeks but then started tripping again | LG | LREL63215 | NO | APT | STOVE IN KITCHEN UNIT 208 | No | No | No | No |  | https://www.formstack.com/admin/download/file/17429428322
2025-01-09 13:15 | Steven | Rooney | 50969 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service Manager | Steven@Giombettielectric.com | ITE QF240A | Breaker | n/a | 40 |  | 2 Pole | Siemens | Residence |  | 2025-01-08 | 2025-01-08 | 117 Dudley Road |  | Berlin | MA | 6037 | wire new stove circuit and plug. GFI breaker tripped after 10 minutes. check all connections. Remove breaker, install regular breaker. Works fine. | LG | LTEL733F/00 |  | Condo / duplex | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17429852595
2025-01-09 17:07 | William | Tolan | 52207 | 5 Torrey Road |  | Sutton | MA | 1590 | 5086880395 | Electrician | wtolan.electrician@gmail.com | Eaton BRN250GFCS | Breaker | Circuit breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2025-01-09 | 2025-01-09 | 6 Village rock Ln unit 14 |  | Natick | MA | 1760 | GFCI TRIPS INSTANTANEOUSLY WHEN RANGE IS PLUGGED IN. | Frigidaire | FFEH3051VSA | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17431241759 | https://www.formstack.com/admin/download/file/17431241762
2025-01-10 08:39 | Cristie | Silva | 59592 | 1 CHARLES ST S |  | Boston | MA | 2116 | 9782598176 | Eletrician | info@alexagc.com | THQL2120GFTP | Breaker | GE BREAKER | 20 |  | 2 Pole | ABB | Residence |  | 2025-01-01 | 2025-01-01 | 1 CHARLES ST S |  |  | MA | 2116 | Appliance not compatible with GFCI BREAKERS | WOLF | CSO3050PM/S/P |  | Apartment | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17433279211 | https://www.formstack.com/admin/download/file/17433279212
2025-01-10 09:07 | Cristie | Silva | 59592 | 1 CHARLES ST S | Unit 11D | Boston | MA | 2116 | 9782598176 | Eletrician | info@alexagc.com | THQL2130GFTP | Breaker | GFCI Breaker | 30 | Wire amperage 40A (8/3 Romex) | 2 Pole | ABB | Residence |  | 2025-01-10 | 2025-01-01 | [5 empty] | Appliance not compatible with GFCI breakers | WOLF | CI243TF/S |  | Apartment | Kitchen | No | No | Yes | No | https://www.formstack.com/admin/download/file/17433401352 | https://www.formstack.com/admin/download/file/17433401353
2025-01-10 13:06 | CHRISTOPHER | CLAPP | 15946 | PO BOX 213 |  | Hanover | MA | 2339 | 6175928508 | owner | clappa23@yahoo.com | BR230GFCI | Breaker | Breaker | 30 |  | 2 Pole | Eaton | Residence |  | 2025-01-10 | 2024-07-04 | 102 Downer Ave |  | Hingham | MA | 2043 | Single wall oven is intermittently tripping GFCI | VIKING | VSOE130SS03 | 0 | Kitchen | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/17434693100
2025-01-10 16:28 | Yovani | Hernandez | 12931 | 29 agatha st |  | Revere | MA | 2151 | 6172307537 | Electrician | Yovaelectrician@gmail.com | Gfci breaker | Breaker | No | 50 |  | 2 Pole | Siemens | Residence |  | 2024-11-14 | 2024-11-14 | 32 walnut hill rd |  | Brookline | MA | 2467 | When install in gfci breaker the gfci trips read the instructions and then manufacture doesn't require a gfci | Cook top | Chs950p2m6s1 | No | Kychen | Stove only in the kitchen dedicated circuit | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17435738026
2025-01-13 11:47 | Chris | Polny | 11660 | 325 Hopping Brook |  | Holliston | MA | 1746 | 7742178986 | VP Electrical Operations | christopherpolny@rodenhiser.com | Eaton GFTCB240 | Breaker | N/A | 40 |  | 2 Pole | Eaton | Residence |  | 2025-01-09 | 2021-06-01 | 1 Daybreak |  | Wayland | MA | 1778 | It trips when cooktop and oven are used simultaneously even after 30 minute burnout. | Kitchen Aid | KSIB900ESS2 |  | Dwelling | Only effects range | No | No | No | No |  | https://www.formstack.com/admin/download/file/17443502683
2025-01-13 15:34 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor | Castlecp@hotmail.com | QF240A | Breaker | Breaker | 40 |  | 2 Pole | Siemens | Residence |  | 2024-12-19 | 2024-12-19 | Olds Carriage Path |  | Groton | MA | 1450 | Installed a new 2pole 40 amp gfci breaker on a new wall oven. It continuously trips. | KitchenAid | KOEC530PBS00 |  | Single family | Kitchen | No | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17445023048
2025-01-14 07:55 | Macnair | Roza | 53508 | 30 Spring Circle |  | Shrewsbury | MA | 1545 | 774-721-6619 | Electrician | MJR@MJRELECTRICINC.COM | THQL1120DF | Breaker | GFCI/ Combination AFCI Breaker | 20 |  | 1 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/17447792104 | 2025-01-03 | 2024-12-16 | 580 Washington St. APT 5-C |  | Boston | MA | 2111 | The GFCI combination GE (ABB) breaker is tripping randomly, regardless of whether an appliance is in use or not. | Signature Kitchen Suite | sqsmd2401s |  | Kitchen | This is the microwave oven, install on the kitchen island. | No | No | No | No | https://www.formstack.com/admin/download/file/17447792117 | https://www.formstack.com/admin/download/file/17447792118
2025-01-14 07:58 | Macnair | Roza | 53508 | 30 Spring Circle |  | Shrewsbury | MA | 1545 | 774-721-6619 | Electrician | MJR@MJRELECTRICINC.COM | THQL1120DF | Breaker | GFCI/ Combination AFCI Breaker | 20 |  | 1 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/17447798863 | 2025-01-03 | 2024-12-16 | 580 Washington St. APT 5-C |  | Boston | MA | 2111 | The GFCI combination GE (ABB) breaker is tripping randomly, regardless of whether an appliance is in use or not. | Signature Kitchen Suite | sqsmd2401s |  | Kitchen | This is the microwave oven, install on the kitchen island. | No | No | No | No | https://www.formstack.com/admin/download/file/17447798876 | https://www.formstack.com/admin/download/file/17447798877
2025-01-14 08:12 | Macnair | Roza | 53508 | 30 Spring Circle, Shrewsbury, MA, 01545 |  | Shrewsbury | MA | 1545 | 7747216619 | Electrician | MJR@MJRELECTRICINC.COM | THQL1120DF | Breaker | GFCI COMBINATION AFCI | 20 |  | 1 Pole | ABB | Residence | https://www.formstack.com/admin/download/file/17447861454 | 2025-01-03 | 2024-12-16 | 580 Washington St. APT 5-C |  | Boston | MA | 2111 | The gas range and the hood fan are in the same circuit and its causing the GFCI combination GE (ABB) breaker to trip randomly, regardless of whether the appliance is in use or not. | yale | PCHBL630SS | Bosh Gas Range HGI8056UC | KITCHEN | kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17447861468 | https://www.formstack.com/admin/download/file/17447861469
2025-01-15 08:25 | Jon | McDonald | 23427 | 19 Deseret Dr |  | Buzzards Bay | MA | 2532 | 7742695521 | Electrician | jon@longfellowdb.com | AD-287 | Breaker | CH | 30 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17453321761 | 2025-01-08 | 2025-01-08 | 385 Saltworks rd |  | Eastham | MA | 2642 | 2 pole 30A GFCI Breaker instantly tripping when trying to turn on induction cooktop | Thermador | CIT36YWB | None | House | Kitchen | No | No | Yes | No | https://www.formstack.com/admin/download/file/17453321775 | https://www.formstack.com/admin/download/file/17453321776
2025-01-15 09:20 | joseph | silverio | 17118 | 32 franklin street |  | lowell | MA | 1854 | 9788514900 | Electrician | fourstarlighting@gmail.com | Siemens QF250A 50 amp GFCI breaker | Breaker | n/a | 50 |  | 2 Pole | Siemens | Residence |  | 2025-01-08 | 2024-12-18 | unit 68 G parker street |  | acton | MA | 1718 | burners on stove in use, preheat on oven turned on and breaker trips | GE | RAS200DM2WW | n/a | apartment | kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/17453578317
2025-01-15 15:14 | Robert | Demole | 37106 | 12 susan dr |  | Billerica | MA | 1821 | 7818447080 | Owner | rfdemole@verizon.net | Square d | Breaker | Square d | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-14 | 2025-01-14 | 39 rindge ave |  | Lexington | MA | 1731 | Bosch 50 amp electric stove trips on gfci only when install a standard circuit breaker everything is fine.the appliance company sent out a technician and he tested everything but said this happens on this model. | Bosch | Shpm78z55n |  | Residencial | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17455917833
2025-01-15 21:13 | Corey | Hood | 8228 | 113 Lawton Road |  | Needham | MA | 2492 | 7819157358 | Owner | coreyhoodelectric@gmail.com | GFTCB250 | Breaker | Plug On | 40 |  | 2 Pole | Eaton | Residence |  | 2025-01-03 | 2025-01-03 | [5 empty] | Breaker trips on preheat every time. | Thermador | PO302W/04 |  | Single Family Home | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17457565932
2025-01-15 21:15 | Corey | Hood | 8228 | 123 Lawton Road |  | Needham | MA | 2492 | 7819157358 | Owner | coreyhoodelectric@gmail.com | GFTCB250 | Breaker | Plug On | 40 |  | 2 Pole | Eaton | Residence |  | 2025-01-10 | 2025-01-10 | [5 empty] | Breaker trips every time when preheating | Thermador | PO302W/05 |  | Single Family Home | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17457572762
2025-01-17 07:51 | Charles | Perfetuo | 17426 | P.O. Box 709 |  | Norwell | MA | 2061 | 781-659-7826 | Owner | chipco@comcast.net | Square D homeline/HOM230GFI | Breaker | none | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-15 | 2024-12-09 | 1 Fieldstone Farm |  | Duxbury | MA | 2332 | The circuit is fine until the dryer cord is plugged into the receptacle. Once plugged in it trips immediately. | Samsung | DV42H5200EP/A3 |  | Laundry | Laundry room dryer | No | No | No | No |  | https://www.formstack.com/admin/download/file/17464176537
2025-01-18 11:32 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor | castlecp@hotmail.com | QF240A | Breaker | Breaker | 40 |  | 2 Pole | Siemens | Residence |  | 2025-01-16 | 2025-01-16 | 11 Guswood Rd. |  | Acton | MA | 1720 | Installed a new 2 pole 40 amp gfci breaker on a new wall oven. It continuously trips. | Thermador | MC30WP |  | Single family. | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17468996810
2025-01-20 15:19 | Eric | Decesar | 23418 | PO Box 1757 |  | Plymouth | MA | 2362 | 5087472330 | Electrician | Services@decesarelectric.com | LEV LB240 G 2P | Breaker | Breaker | 40 |  | 2 Pole | Leviton | Residence |  | 2024-12-14 | 2024-07-03 | 15 High St. Unit 104 |  | Norwell | MA | 2061 | Range was causing GFCI trip intermittently while using. Dedicated circuit was evaluated multiple times. GFCI Breaker was swapped multiple times. | General Electric | GRF600AV1SS | NO | Apartment | Range | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17475224515
2025-01-20 15:25 | Eric | Decesar | 23418 | PO Box 1757 |  | Plymouth | MA | 2362 | 5087472330 | Electrician | Services@decesarelectric.com | LEV LB240 G 2P | Breaker | Breaker | 40 |  | 2 Pole | Leviton | Residence |  | 2024-12-14 | 2024-07-03 | 15 High St. Unit 104 |  | Norwell | MA | 2061 | Range was causing GFCI trip intermittently while using. Dedicated circuit was evaluated multiple times. GFCI Breaker was swapped multiple times. | General Electric | GRF600AV1SS | NO | Apartment | Range | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17475254769
2025-01-20 15:32 | Eric | Decesr | 23418 | PO Box 1757 |  | Plymouth | MA | 2362 | 5087472330 | Electrician | Services@decesarelectric.com | LEV LB240 G 2P | Breaker | Breaker | 40 |  | 2 Pole | Leviton | Residence |  | 2025-01-08 | 2024-07-03 | 15 High St. Unit 211 |  | Norwell | MA | 2061 | Range was causing GFCI trip intermittently while using. Dedicated circuit was evaluated multiple times. GFCI Breaker was swapped multiple times. | General Electric | GRF600AV1SS | NO | Apartment | Range | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17475283625
2025-01-21 07:18 | Eric | Decesar | 23418 | PO Box 1757 |  | Plymouth | MA | 2362 | 5087472330 | Electrician | Decesarelec@hotmail.com | LEV LB240 G 2P | Breaker | Breaker | 40 |  | 2 Pole | Leviton | Residence |  | 2025-01-13 | 2024-07-03 | 15 High St. Unit 201 |  | Norwell | MA | 2061 | Range was causing GFCI trip intermittently while using. Dedicated circuit was evaluated multiple times. GFCI Breaker was swapped multiple times. | General Electric | GRF600AV1SS |  | Apartment | Range | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17477589445
2025-01-21 07:26 | Eric | Decesar | 23418 | PO Box 1757 |  | Plymouth | MA | 2362 | 5089229116 | Electrician | Services@decesarelectric.com | LEV LB240 G 2P | Breaker | Breaker | 40 |  | 2 Pole | Leviton | Residence |  | 2024-12-12 | 2024-10-21 | 15 High St. Unit 803 |  | Norwell | MA | 2061 | Range was causing GFCI trip intermittently while using. Dedicated circuit was evaluated multiple times. GFCI Breaker was swapped multiple times. | General Electric | GRF600AV1SS | NO | Apartment | Range | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17477606719
2025-01-21 07:30 | Eric | Decesar | 23418 | PO Box 1757 |  | Plymouth | MA | 2362 | 5087472330 | Electrician | Services@decesarelectric.com | LEV LB240 G 2P | Breaker | Breaker | 40 |  | 2 Pole | Leviton | Residence |  | 2024-12-12 | 2025-09-13 | 15 High St. Uniit 609 |  | Norwell | MA | 2061 | Range was causing GFCI trip intermittently while using. Dedicated circuit was evaluated multiple times. GFCI Breaker was swapped multiple times. | General Electric | GRF600AV1SS | NO | Apartment | Range | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17477614366
2025-01-21 12:15 | Adriano | De Mello | 56932 | 14 Bramble Hill Rd |  | Methuen | MA | 1844 | 978-221.0743 | Electrician | admello1969@gmail.com | Q120DF | Breaker | AFCI/GFCI | 20 |  | 1 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17478978657 | 2025-01-10 | 2025-01-08 | 17 Bethesda Lane |  | Reading | MA | 1867 | Breaker trips all the time, replace a couple to make sure the problem was not the breaker, on the manufactures manual, it's stated that:¦A ground fault circuit interrupter (GFCI) is ""NOT"" recommended and may cause interruption of operation | Sub-Zero | DEC2450FI/R |  | Kitchen | Home run circuit for freezer | No | No | No | No |  | https://www.formstack.com/admin/download/file/17478978670
2025-01-21 21:26 | Greg | Kehlhem | 11544 | 3 saddle hill road |  | Medway | MA | 2053 | 7749939697 | Owner electrician | kehlhemelectric@gmail.com | Qf250A | Breaker | None | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17481704480 | 2025-01-16 | 2025-01-16 | 2 Bumker |  | Medfield | MA | 2052 | New induction range. New circuit. Ran range for 2 hours on standard 2pole 50 then put the gfci breaker back in to try again but still tripped the gfci. Tried a different gfci breaker and still tripped. | Bosch | HIS8655u /07 | Move | Kitchen | Kitchen Range | No | No | No | No | https://www.formstack.com/admin/download/file/17481704494 | https://www.formstack.com/admin/download/file/17481704495
2025-01-22 08:27 | David | DeGrazia | 17119 | Po Box 299 |  | E. Freetown MA 02717 | MA | 2717 | 5085420174 | Master Electrican | yellekd1956@comcast.net | Eaton | Breaker | breaker | 30 |  | 1 Pole | Eaton | Residence |  | 2024-12-01 | 2024-11-01 | 110 Plain Street (A) |  | Middleboro | MA | 2346 | breaker trips unwanted | Electrolux | FCWS3027ABD | NA | kitchen | range is located in kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17482862752
2025-01-22 08:34 | David | DeGrazia | 17119 | Po Box 299 |  | E. Freetown MA 02717 | MA | 2717 | 5085420179 | Master Electrican | yellekd1956@comast.net | Eaton | Breaker | breaker | 40 |  | 1 Pole | Eaton | Residence |  | 2024-12-01 | 2024-11-01 | 110 Plain Street (A) |  | Middleboro | MA | 2346 | breakers tripping unwanted | Electrolux | FCWS3027ABD | na | kitchen | gfci trips on range | No | No | No | No |  | https://www.formstack.com/admin/download/file/17482882548
2025-01-22 08:38 | David | DeGrazia | 17119 | Po Box 299 |  | E. Freetown MA 02717 | MA | 2717 | 5085420179 | Master Electrican | yellekd1956@comcast.net | Eaton | Breaker | breaker | 30 |  | 1 Pole | Eaton | Residence |  | 2024-12-01 | 2024-11-01 | 110 Plain Street (B) |  | Middleboro | MA | 2346 | gfci tripping unwanted | Electrolux | FCWS3027ABD | na | kitchen | range trips unwated | No | No | No | No |  | https://www.formstack.com/admin/download/file/17482896312
2025-01-22 08:42 | David | DeGrazia | 17119 | Po Box 299 |  | E. Freetown MA 02717 | MA | 2717 | 5085420179 | Master Electrican | yellekd1956@comcast.net | Eaton | Breaker | breaker | 40 |  | 1 Pole | Eaton | Residence |  | 2024-12-01 | 2024-11-01 | 110 Plain Street (B) |  | Middleboro | MA | 2346 | range unwanted tripping | Electrolux | FCWS3027ABD | na | kitchen | range unwanted tripping | No | No | No | No |  | https://www.formstack.com/admin/download/file/17482908654
2025-01-22 09:24 | Robert | Kimberley | 10984 | 51 Town Hill Rd. |  | WEST OTIS | MA | 01245-9736 | 413-441-0212 | Electrician | RRKIM71@GMAIL.COM | QO230GFI | Breaker | plug-on | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-18 | 2024-12-16 | 74 Main Rd |  | Tyringham | MA | 1264 | It worked for 2 days, then overnight it would trip. It trips when not in use. | Thermador Induction cooktop | CIT36YWBB | NONE | Kitchen | Kitchen cooktop | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17483065449
2025-01-22 10:07 | Wayne | Dawson | 11876 | 2 middle st |  | Hadley | MA | 1035 | 4132043063 | Electrician | no72gto@yahoo.com | Homeline | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-21 | 2025-01-10 | 2 middle st |  | Hadley | MA | 1035 | Using broiler on stove and GFI trips. | Hotpoint | R8787WOYZWW | None | Dwelling | No rooms. Stove | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17483267153 | https://www.formstack.com/admin/download/file/17483267154
2025-01-22 12:40 | Carl | Perkins | 11876 | 4 Open Square Way |  | Holyoke | MA | 1040 | 4132765472 | Electrician | no72gto@Yahoo.com | Home250gfi | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17484199417 | 2025-01-22 | 2025-01-20 | 92 Barrett st |  | Northampton | MA | 1060 | Customer uses burners normally, when oven is also turned on the gfi trips. When oven is turned on by itself the gfi trips. | Amana | AER5712BAW | None | Dwelling | No room. Stove | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17484199431 | https://www.formstack.com/admin/download/file/17484199432
2025-01-23 07:57 | Gustavo | Simoes | 23674 | 12 Welles Way |  | Chilmark | MA | 2535 | 7745634988 | Electrician | gsselectricmv@gmail.com | LB240G | Breaker |  | 40 |  | 2 Pole | Leviton | Residence |  | 2025-01-21 | 2025-01-21 | 12 Smith Ln |  | Chilmark | MA | 2535 | Breaker won't hold when Wall oven is plugged in | Wolf | DO3050PM/S/P |  | Single Family dwelling | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17487919432
2025-01-23 07:58 | Gustavo | Simoes | 23674 | 12 Welles way |  | Chilmark | MA | 2535 | 7745634988 | Electrician | gsselectricmv@gmail.com | LB230G | Breaker |  | 30 |  | 2 Pole | Leviton | Residence |  | 2025-01-21 | 2025-01-21 | 12 Smith Ln |  | Chilmark | MA | 2535 | Breaker won't hold while cook top is hardwired to the circuit. | Wolf | CI30460C/B |  | Kitchen | Kitchen Range Circuit | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17487920808
2025-01-23 10:37 | Carl | Perkins | 11876 | 79 Cooley st. |  | Agawam | MA | 1001 | 4132043063 | Electrician | no72gto@Yahoo.com | Hom240GFI | Breaker | Breaker | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17488618168 | 2025-01-22 | 2025-01-20 | 360 Northfield Rd |  | Bernardston | MA | 1337 | Stove trips GFI when burner and oven is turned on. | GE | JB640DP1CC | None | Dwelling | Stove, no rooms | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17488618182 | https://www.formstack.com/admin/download/file/17488618183
2025-01-23 12:20 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | VP/OWNER | JOHN@HENRYSELECTRICINC.COM | SIEMENS/Q240 | Breaker | N/A | 40 |  | 2 Pole | Siemens | Residence |  | 2025-01-22 | 2025-01-15 | 305 WOODLAND WWAY |  | OTIS | ME | 1253 | Breaker does not hold - continually trips. | LG | LSIL633TFE/00 |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17489218222
2025-01-28 16:49 | Jeffrey | Williams | 22806 | 145 Plain St |  | Hanover | MA | 2339 | 781-831-0433 | electrician | jcw145@comcast.net | homeline 240gfi | Breaker | N/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-16 | 2024-11-13 | 34 Cliff road south |  | Scituate | MA | 2040 | trips when oven starts heating | Whirlpool wall oven | KOEC530PSS00 | none | single family | Kitchen wall oven | No | No | No | No |  | https://www.formstack.com/admin/download/file/17510972976
2025-01-28 16:59 | Jeffrey | Williams | 22806 | 145 Plain St |  | Hanover | MA | 2339 | 781-831-0433 | Electrician | jcw145@comcast.net | homeline 240gfi | Breaker | N/a | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-16 | 2024-11-13 | 34 Cliff road south |  | Scituate | MA | 2040 | trips when turns on | Whirlpool | KCIG556JSS02 | none | single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17511032068
2025-01-29 08:17 | Sean | Cranston | 17070 | 10 - 12 cleveland place | 10-12 CLEVELAND PLACE | gloucester | MA | 1930 | 9784237196 | ELECTRICIAN/OWNER | cranstonelectric@comcast.net | EATON GFCB 250 | Breaker | EATON | 50 |  | 2 Pole | Eaton | Residence |  | 2024-01-24 | 2025-01-18 | 321 HIDDEN ROAD |  | ANDOVER | ME | 1810 | KEEPS TRIPPING ON GFI BREAKER | WOLF | D03050PM/S/P | NO | KITCHEN | WALL OVEN KEEPS TRIPPING BREAKER | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17513424775
2025-01-29 08:22 | Trevor | Hebb | 16467 | 895 Salem Street |  | Groveland | MA | 1834 | 9783731393 | Electrician | office@danielsel.com | s9d 2p50 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2024-12-22 | 2025-01-22 | 2 school house road unit 3211 |  | Gloucester | MA | 1930 | Tripping while heating & self cleaning | GE | JB646RR655 |  | Apartment | Kitchen | No | No | No | No
2025-01-29 08:30 | Trevor | Hebb | 16467 | 895 Salem Street |  | Groveland | MA | 1834 | 9783731393 | Electrician | office@danielsel.com | Sauare D 2p50 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-05 | 2025-01-22 | 2 School House Rd |  | Gloucester | MA | 1930 | While heating | GE | JB645RR655 |  | Apartment | Kitchen | No | No | No | No
2025-01-29 08:30 | Sean | Cranston | 17070 | 10 - 12 cleveland place | 10-12 CLEVELAND PLACE | gloucester | MA | 1930 | 9784237196 | ELECTRICIAN/OWNER | cranstonelectric@comcast.net | EATON/ GFCB 120 , BRP120DF, BRP 120AF | Breaker | EATON | 20 |  | 1 Pole | Eaton | Residence |  | 2024-01-12 | 2025-01-12 | 32 HIDDEN ROAD |  | ANDOVER | MA | 1810 | BASEMENT REF KEEPS TRIPPING BREAKER | THERMODOR | T36BT820NS | NO | BASEMENT | NONE | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17513466307
2025-01-29 08:37 | Trevor | Hebb | 1971 | 895 Salem Street |  | Groveland | MA | 1834 | 9783731393 | Electrician | office@danielsel.com | Eaton 2p 50 GFCI | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-11-11 | 2025-01-06 | 3 Boston Way |  | Newburyport | MA | 1950 | while heating | GE | JB645ER4ES |  | Apartment | Kitchen Stove | No | No | No | No
2025-01-29 08:41 | Sean | Cranston | 17070 | 10 - 12 cleveland place | 10-12 CLEVELAND PLACE | gloucester | MA | 1930 | 9784237196 | ELECTRICIAN/OWNER | cranstonelectric@comcast.net | EATON GFCB 230 | Breaker | EATON | 30 |  | 2 Pole | Eaton | Residence |  | 2025-01-12 | 2025-01-14 | 32 HIDDEN ROAD |  | ANDOVER | MA | 1810 | DRYER WONT HOLD KEEPS TRIPPIN | GE | GFD85ESSN1WW | NO | JUST DRYER | NONE | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17513500515
2025-01-29 11:54 | Kyle | Aussant | 22084 | 4 Kazan Street |  | Cumberland | RI | 2864 | 401-636-2101 | President | office@aussantelectric.net | Seimans BLFD | Breaker | NA | 20 |  | 2 Pole | Siemens | Commercial |  | 2025-01-21 | 2025-01-13 | Springhouse Senior Living, 2nd floor kitchen/Bistro area |  | 44 Allandale Street | MA | 2130 | Oven would trip several minutes into heating process. Installed standard breaker and let oven run for 60 minutes. then reinstalled GFI breaker and retested and issue still occurred. | GE APPLIANCES | JTS3000SNSS |  | Multi unit | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17515510269 | https://www.formstack.com/admin/download/file/17514585825
2025-01-29 13:29 | Kyle | Aussant | 22084 | 4 Kazan Street |  | Cumberland | RI | 2864 | 401-636-2101 | President | office@aussantelectric.net | Seimans BLFD | Breaker | NA | 20 |  | 2 Pole | Siemens | Commercial | https://www.formstack.com/admin/download/file/17515512041 | 2025-01-21 | 2025-01-13 | Springhouse Senior Living, 2nd floor kitchen/Bistro area |  | 44 Allandale Street | MA | 2130 | Oven would trip several minutes into heating process. Installed standard breaker and let oven run for 60 minutes. then reinstalled GFI breaker and retested and issue still occurred. | GE APPLIANCES | JTS3000SNSS |  | Multi unit | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17515172331
2025-01-29 13:30 | Kyle | Aussant | 22084 | 4 Kazan Street |  | Cumberland | RI | 2864 | 401-636-2101 | President | office@aussantelectric.net | Seimans BLFD | Breaker | NA | 20 |  | 2 Pole | Siemens | Commercial | https://www.formstack.com/admin/download/file/17515514432 | 2025-01-21 | 2025-01-13 | Springhouse Senior Living, 2nd floor kitchen/Bistro area |  | 44 Allandale Street | MA | 2130 | Oven would trip several minutes into heating process. Installed standard breaker and let oven run for 60 minutes. then reinstalled GFI breaker and retested and issue still occurred. | GE APPLIANCES | JTS3000SNSS |  | Multi unit | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17515172864
2025-01-29 13:42 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-29 | 2025-01-28 | 660 Main St. |  | Worcester | MA |  | Apt 601 ¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17515247558
2025-01-29 13:44 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-29 | 2025-01-28 | 660 Main St. |  | Worcester | MA |  | Apt 501 ¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17515260338
2025-01-29 13:51 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 508-297-7700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-29 | 2025-01-28 | 660 Main St. |  | Worcester | MA |  | Apt 401 ¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17515300394
2025-01-29 14:01 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 508-297-7700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-29 | 2025-01-28 | 660 Main St. |  | Worcester | MA |  | Apt 301 ¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17515364317
2025-01-29 14:03 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 508-297-7700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-29 | 2025-01-28 | 660 Main St. |  | Worcester | MA |  | Apt 201 ¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17515374791
2025-01-30 10:33 | Wadley | louissaint | 57074 | 945 Centre Street |  | Brockton | MA | 2302 | 5083865840 | Electrician | wadleylouissaint@yahoo.com | Siemens | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17519193790 | 2025-01-27 | 2025-01-27 | 8 Ingalls |  | Woburn | MA | 1801 | When plugging in range it trips breaker. | Maytag | CRE9600CCM |  | Single family | Range keeps tripping breaker in kitchen. | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17519193803 | https://www.formstack.com/admin/download/file/17519193804
2025-01-30 10:33 | Wadley | louissaint | 57074 | 945 Centre Street |  | Brockton | MA | 2302 | 5083865840 | Electrician | wadleylouissaint@yahoo.com | Siemens | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17519195528 | 2025-01-27 | 2025-01-27 | 8 Ingalls |  | Woburn | MA | 1801 | When plugging in range it trips breaker. | Maytag | CRE9600CCM |  | Single family | Range keeps tripping breaker in kitchen. | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17519195546 | https://www.formstack.com/admin/download/file/17519195547
2025-01-30 11:10 | Wadley | louissaint | 57074 | 945 Centre Street |  | Brockton | MA | 2302 | 5083865840 | Electrician | wadleylouissaint@yahoo.com | AJ5X9000 | Breaker | N/A | 30 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17519407689 | 2025-01-27 | 2025-01-27 | 8 Ingalls st |  |  | MA | 1801 | Tripping when dryer is plugged in. | Whirlpool | M21328953 |  | Single family | Laundry room dryer keeps tripping breaker when plugged in. | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17519407702 | https://www.formstack.com/admin/download/file/17519407703
2025-01-30 11:21 | Wadley | louissaint | 57074 | 945 Centre Street |  | Brockton | MA | 2302 | 5083865840 | Electrician | wadleylouissaint@yahoo.com | L2311080524 | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17519472513 | 2025-01-27 | 2025-01-27 | 8 Ingalls |  | Woburn | MA | 1801 | Breaker keeps tripping when range is plugged in. | Maytag | CRE9600CM |  | Single family | Kitchen range on first floor. | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17519472543 | https://www.formstack.com/admin/download/file/17519472546
2025-01-30 11:39 | Wadley | louissaint | 57074 | 945 Centre Street |  | Brockton | MA | 2302 | 5083865840 | Electrician | wadleylouissaint@yahoo.com | L2311080524 | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17519579145 | 2025-01-27 | 2025-01-27 | 8 Ingalls |  | Woburn | MA | 1801 | Breaker keeps tripping when range is plugged in. | Maytag | CRE9600CM |  | Single family | Kitchen range on first floor. | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17519579158 | https://www.formstack.com/admin/download/file/17519579159
2025-01-31 10:20 | Joseph | DeCampo | 38033 | 72 Morningside dr |  | Arlington | MA | 2474 | 781-316-6980 | Owner | joedecampo@yahoo.com | Qf250A | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2025-01-31 | 2025-01-14 | [5 empty] | Brand new installation of wiring and breaker on a new stove, stove runs fine for 1 hr on standard breaker | Whirlpool | WFES3330RW0 |  | Apartment | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/17524164787
2025-01-31 10:25 | Joseph | DeCampo | 38033 | 72 Morningside dr |  | Arlington | MA | 2474 | 781-316-6980 | Owner | joedecampo@yahoo.com | QF250A | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2025-01-31 | 2025-01-14 | 86 Bacon st |  | Waltham | MA | 2451 | New installation of stove, wire and breaker. ¦Stove runs for short periods of time and trips breaker¦Works fine on standard breaker | Whirlpool | WFES3330RW0 | None | Apartment | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/17524190790
2025-01-31 10:31 | Joseph | DeCampo | 38033 | 72 Morningside dr |  | Arlington | MA | 2474 | 7813166980 | Owner | joedecampo@yahoo.com | QF250A | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2025-01-31 | 2025-01-14 | 88 Bacon st |  | Waltham | MA | 2451 | Brand new installation, new wire, breaker and appliance | Whirlpool | WFES3330RW0 | None | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17524225588
2025-01-31 17:08 | Philip | Mendonca | 10757 | 6R Mount Vernon St. |  | Arlington | MA | 2476 | 6178885434 | electrician | philipselectric@live.com | Eaton | Breaker | plug in breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2025-01-31 | 2025-01-27 | 183 Hillside Ave |  | Arlington | MA | 2476 | new stove tripping gfci breaker | Frigidaire | FCF13083AS |  | kitchen | kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/17526483680
2025-02-01 15:30 | Michael | Bell | 4520 | P.O. Box 1038 |  | Plymouth | MA | 2362 | 5082948148 | Master Electrician | vibemike@gmail.com | Eaton CH250GF | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2025-01-07 | 2025-01-07 | 3 Huntinghouse Brook Lane |  | Lakeville | MA | 2347 | The appliance is a double electric wall oven. When turning ovens on to heat up, the breaker will trip during the heating up process. This oven is controlled by a touch pad on the unit. The breaker trips with either one oven or with both ovens turned on. When switched to a standard (non GFI breaker) the oven works correctly. Appliance is not GFI compatible | Thermador | ME302YP | NONE | Single Family Dwelling | Kitchen wall oven. Dedicated circuit | No | No | No | No |  | https://www.formstack.com/admin/download/file/17528731267
2025-02-01 15:38 | Michael | Bell | 4520 | P.O. Box 1038 |  | Plymouth | MA | 2362 | 5082948148 | Master Electrician | WARRENTOWNEELECTRIC@GMAIL.COM | BR250GF | Breaker | NONE | 50 |  | 2 Pole | Eaton | Residence |  | 2024-12-05 | 2024-12-03 | 26 Surplus Street |  | Duxbury | MA | 2324 | Appliance is a Double oven with induction top slide in range unit made by Cafe. Appliance is fully touch pad controlled. Unit trips randomly when owner tries to use top or either oven. Works fine with standard circuit breaker (no GFI). On a dedicated and new circuit direct from the electric panel. Appliance is not GFI compatible. | Cafe | CCHS950P4MS1 | NONE | Single family dwelling | Kitchen range. Dedicated circuit | No | No | No | No |  | https://www.formstack.com/admin/download/file/17528749128
2025-02-02 11:29 | Nathan | Dean | 53556 | 9 Anthony Terrace |  | New Bedford | MA | 2740 | 774-930-7116 | Owner | ndeanelectric@gmail.com | Eaton BR 50 amp gfci breaker/BRN250GF | Breaker | None | 50 |  | 2 Pole | Eaton | Residence |  | 2025-01-24 | 2024-11-01 | Kitchen |  | 6 Charity Stevens | MA | 2719 | As soon as the oven heats up the gfci breaker trips instantly. | Whirlpool | WFES3030RS | No | Residential Home | Kitchen Stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/17530350731
2025-02-03 15:55 | Vito | Ferrara | 50584 | 220 Magnolia Ave, magnolia ave |  | GLOUCESTER | MA | 1930 | 9788367785 | owner | ferraraelectric1@gmail.com | qf250 | Breaker | none | 50 |  | 2 Pole | Siemens | Residence |  | 2025-02-03 | 2024-11-01 | 220 Magnolia Ave, magnolia ave |  | GLOUCESTER | MA | 1930 | cooktop runs fine range trips gfi breaker | amana | aer6303mms | none | 2 family | kitchen range | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/17535464199
2025-02-05 10:09 | Carl | Perkins | 11876 | 79 Cooley St |  | Agawam | MA | 1001 | 4132043063 | Electrician | no72gto@Yahoo.com | Hom240GFI | Breaker | Breaker | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17544556438 | 2024-10-11 | 2024-10-07 | 62 Grove Street |  | Pittsfield | MA | 1201 | Turning on oven breaker trips. Burner are ok. | GE | JB655EK4ES | None | Dwelling | No rooms | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17544556477 | https://www.formstack.com/admin/download/file/17544556481
2025-02-05 17:22 | John | Tamasi | 12321 | 6 easy St |  | Windham | NH | 3087 | 603-247-6135 | electricain | johntamasi@yahoo.com | HOM250GFIC | Breaker | GFI Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-23 | 2025-01-23 | 158 Naples Road |  | Brookline | MA | 2446 | Installed breaker 20 minutes later breaker trip. Check cable and wiring to cooktop with multi meter for any shorts or ground fault. All clear. Turn breaker back on trip again 40 minutes later. It will trip without turning on cooktop. It will continue throughout the day. Sometimes it doesn't trip for several hours. Then it will trip again. | GE | PT9060 | NO | Single Family Home | Just cooktop unit itself in kitchen. | Yes | No | No | No | https://www.formstack.com/admin/download/file/17547340196 | https://www.formstack.com/admin/download/file/17547340197
2025-02-06 10:31 | Kyle | Aussant | 22084 | 89 Central Street |  | Manville | RI | 2838 | 401-636-2101 | President | office@aussantelectric.net | THQL2150GFT2P | Breaker | NA | 50 |  | 2 Pole | ABB | Residence |  | 2025-01-27 | 2025-01-21 | 255 Norfolk St. |  | Canton | MA | 2021 | Oven would trip several minutes into heating process. Installed standard breaker and oven run for 60 minutes. Then installed GFI breaker and retested and issue still occurred. | Kenmore | 790.9541 | NA | Residential | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17549994862 | https://www.formstack.com/admin/download/file/17549994863
2025-02-06 14:43 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | OWNER/VP | JOHN@HENRYSELECTRICINC.COM | BR240 | Breaker | n/a | 50 |  | 2 Pole | Eaton | Residence |  | 2025-02-03 | 2025-01-27 | 200 LAUREL STREET, APT 14 |  | LEE | MA | 1238 | Breaker does not hold, kept tripping. | FRIGIDAIRE | FCFE2425AS |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17551587069
2025-02-06 14:52 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | OWNER/VP | JOHN@HENRYSELECTRICINC.COM | BR240 | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2025-02-03 | 2025-01-27 | 200 LAUREL STREET, APT 16 |  | LEE | MA | 01238-1641 | Breaker does not hold, kept tripping. | FRIGIDAIRE | FCFE2425AS |  | APARTMENT | KITCHEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/17551640920
2025-02-11 10:16 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-11 | 2025-02-10 | 660 Main St. |  | Worcester | MA |  | Apt 602¦¦Oven portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17569454314
2025-02-11 10:28 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-11 | 2025-02-10 | 660 Main St. |  | Worcester | MA |  | Apt 502¦¦Oven portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17569523765
2025-02-11 10:43 | Sean | Matthes | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-11 | 2025-02-10 | 660 Main St. |  | Worcester | MA |  | Apt 402¦¦Oven portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17569608869
2025-02-11 11:35 | Matt | Elder | 20748 | 40 BEDFORD PARK, UNIT 2 |  | Bridgewater | MA | 2324 | 781-340-0740 | President | matt@elderelectric.net | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2025-02-04 | 2025-02-10 | 3368 Washington Street |  | Boston | MA |  | Randomly tripping out | Whirlpool | WFC315S0JW3 |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17569916265
2025-02-11 11:39 | Matt | Elder | 20748 | 40 BEDFORD PARK, UNIT 2 |  | Bridgewater | MA | 2324 | 781-340-0740 | President | matt@elderelectric.net | THQL2150GFT | Breaker | N/A | 50 |  | 2 Pole | ABB | Residence |  | 2025-02-04 | 2025-02-10 | 3368 Washington Street |  | Boston | MA |  | Randomly tripping out. | Whirlpool | WFC315S0JW3 |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17569940148
2025-02-11 11:43 | Matt | Elder | 20748 | 40 BEDFORD PARK, UNIT 2 |  | Bridgewater | MA | 2324 | 781-340-0740 | President | matt@elderelectric.net | THQL2120GFT | Breaker | N/A | 20 |  | 2 Pole | ABB | Residence |  | 2025-02-04 | 2025-02-10 | 3368 Washington Street |  | Boston | MA |  | Randomly tripping out | Whirlpool | RCS2012RS10 |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17569965503
2025-02-11 11:45 | Matt | Elder | 20748 | 40 BEDFORD PARK, UNIT 2 |  | Bridgewater | MA | 2324 | 781-340-0740 | President | matt@elderelectric.net | THQL2120GFT | Breaker | N/A | 20 |  | 2 Pole | ABB | Residence |  | 2025-02-04 | 2025-02-10 | 3368 Washington Street |  | Boston | MA |  | Randomly tripping out | Whirlpool | RCS2012RS10 |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17569979024
2025-02-11 11:46 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5072977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-11 | 2025-02-10 | 660 Main St. |  | Worcester | MA |  | Apt 302¦¦Oven portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17569982886
2025-02-11 11:48 | Matt | Elder | 20748 | 40 BEDFORD PARK, UNIT 2 |  | Bridgewater | MA | 2324 | 781-340-0740 | President | matt@elderelectric.net | THQL2120GFT | Breaker | N/A | 20 |  | 2 Pole | ABB | Residence |  | 2025-02-04 | 2025-02-10 | 3368 Washington Street |  | Boston | MA |  | Randomly tripping out | Whirlpool | RCS2012RS10 |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17569995753
2025-02-11 11:50 | Matt | Elder | 20748 | 40 BEDFORD PARK, UNIT 2 |  | Bridgewater | MA | 2324 | 781-340-0740 | President | matt@elderelectric.net | THQL2120GFT | Breaker | N/A | 20 |  | 2 Pole | ABB | Residence |  | 2025-02-04 | 2025-02-10 | 3368 Washington Street |  | Boston | MA |  | Randomly tripping out | Whirlpool | RCS2012RS10 |  | Apartment | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17570013038
2025-02-11 12:23 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | hom240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-11 | 2025-02-10 | 660 Main St. |  | Worcester | MA |  | Apt 202¦¦Oven portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | ge | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17570239102
2025-02-12 13:28 | Bernardo | Marzilli | 28106 | 112 Pine Street |  | Auburndale | MA | 2466 | 617-872-2744 | owner | marzillielectrical@gmail.com | Siemens M25401040316 | Breaker | QPF | 40 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17575892204 | 2025-02-12 | 2025-02-11 | 19 Arlington Road |  | Waltham | MA | 2453 | when range is plugged in, circuit breaker won't stay in the ""ON"" position | General Electric | GRS600AV1FS | none | single family home | kitchen range | No | Yes | No | No | https://www.formstack.com/admin/download/file/17575892225 | https://www.formstack.com/admin/download/file/17575892228
2025-02-12 18:09 | Peter | Keller | 13379 | 114 Boston Post Rd |  | Wayland | MA | 1778 | 5088898049 | President | peter.keller.electric@gmail.com | THQL2150GFT | Breaker | breaker | 50 |  | 2 Pole | ABB | Residence |  | 2025-01-24 | 2025-01-24 | 10 Dudley Rd. |  | Sudbury | MA | 1776 | Breaker trips as soon as appliance is turned on | LG | WDES9428F | none | Kitchen | Kitchen wall oven | No | No | No | No |  | https://www.formstack.com/admin/download/file/17577559658
2025-02-12 20:29 | Peter | Keller | 13379 | 114 Boston Post Rd |  | Wayland | MA | 1778 | 5083587087 | President | peter.keller.electric@gmail.com | THQL2160GFT | Breaker | breaker | 60 |  | 2 Pole | ABB | Residence |  | 2025-01-24 | 2025-01-24 | 10 Dudley Rd |  | Sudbury | MA | 1776 | Cooktop trips the GFCI breaker immeadiatly when unit is turned on. | LG | CBIS3618BE | one | single family dwelling | Kitchen Cooktop | No | No | No | No |  | https://www.formstack.com/admin/download/file/17578086572
2025-02-14 09:11 | Brian | Bradley | 29707 | 266 Sudbury Street |  | Marlborough | MA | 1752 | 9782128014 | Owner/Operator | Bbelectric.permits@gmail.com | Siemens US2:QF120AP | Breaker | Single Pole | 20 |  | 1 Pole | Siemens | Residence |  | 2025-02-13 | 2025-02-12 | 21 Chiltern Rd |  | Weston | MA | 2493 | Sauna is not designed to operate on GFCI protected circuit. Once sauna is heating breaker will nuisance trip. Occurs every time the sauna is heating. | Finnleo | Piccolo Mini (9806-6820) 2.2 kW | none. (dedicated) | Residential | The sauna itself is the only thing affected as it is a dedicated circuit. | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17584587231 | https://www.formstack.com/admin/download/file/17584587232
2025-02-14 11:22 | Michael | Hall | 51887 | 68 Industrial Way |  | Wilmington | MA | 1887 | 8023438008 | Project Manager | mhall@deccorp.com | SQD QOB220GFI | Breaker | Bolton | 20 |  | 2 Pole | Schneider Electric | Commercial |  | 2025-02-03 | 2025-02-03 | 148 Cambridge St |  | Boston | MA | 2114 | Breaker instantly trips when connected to GFI breaker, when connecting to standard breaker no issues are present | Maytag | SYN030DNOHZYU20COBA | none | Suffic Univerty Athletic Building | Laundry Room - Units are hardwired | No | No | Yes | No | https://www.formstack.com/admin/download/file/17585219519 | https://www.formstack.com/admin/download/file/17585219520
2025-02-14 15:11 | Philip | Mendonca | 10757 | 6R Mount Vernon St. |  | Arlington | MA | 2476 | 6178885434 | electrician | philipselectric@gmail.com | QF250A | Breaker | GFCI | 50 |  | 2 Pole | Siemens | Residence |  | 2025-02-05 | 2025-02-12 | 200 Summer St, |  | Arlington | MA | 2474 | stove tripping gfci breaker | Frigidaire Gallery | FGIH3047VFC |  | kitchen | kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/17586412993
2025-02-16 16:42 | Jesse | Kuhlman | 21804 | 313 Eastern Avenue |  | Lynn | MA | 1902 | 6178406252 | Owner | ervis.kes@gmail.com | Homeline HOM250GFIC | Breaker | none | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-31 | 2025-01-31 | 9 Bayard St. |  | Dedham | MA | 2026 | Needed to install the new breaker after running a new line after we did a service upgrade.¦Cooktop works fine but the oven trips after 10 min. Oven is about 15 years old. | General Electric Stove | J BP23D R3WW | No | Single family house | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17591040986
2025-02-18 17:11 | David | Briley | 57645 | 135 ELM ST | 2 | AMESBURY | MA | 1913 | 6179215506 | Owner | 978electrician@gmail.com | Siemens 40 amp GFCI pigtail breaker | Breaker | n/a | 40 |  | 2 Pole | Siemens | Residence |  | 2025-02-10 | 2025-02-12 | 135 ELM ST, 2 |  | AMESBURY | MA | 1913 | Continuous tripping of existing older electric range.¦Tested with GFCI breaker of higher ampacity and still tripped.¦Removed GFCI protection and tripping no longer occurred. | general electric | JB640DP1ww | none | kitchen | kitchen only | No | No | No | No |  | https://www.formstack.com/admin/download/file/17600026324
2025-02-19 09:12 | Richard | Carl | 31458 | 321 East Falmouth Highway |  | East Falmouth | MA | 2536 | 5082744267 | Owner | rich@ikitchensetc.com | 1597TRW | Receptacle | Tamper Resistant | 15 |  | 2 Pole | Legrand | Residence |  | 2025-02-02 | 2025-02-02 | 48 Priscilla Ave |  | East Falmouth | MA | 2536 | Dishwasher trips GFI at beginning of cycle. Replaced dishwasher. Same results. | GE | CDD420P2TS1 | None | Single Family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17602305642 | https://www.formstack.com/admin/download/file/17602305643
2025-02-19 12:37 | David | briley | 57645 | 135 ELM ST | 2 | AMESBURY | MA | 1913 | 6179215506 | owner | 978electrician@gmail.com | siemens | Breaker | n/a | 30 |  | 2 Pole | Siemens | Residence |  | 2025-02-11 | 2025-02-11 | 12 Cottage St |  | Peabody | MA | 1960 | Continuous tripping of existing older electric range.¦Tested with GFCI breaker of higher ampacity and still tripped.¦Removed GFCI protection and tripping no longer occurred. | GE | JB640DP1ww | n/a | single family | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17603402476
2025-02-20 00:27 | Herneceau | Marcelin | 59815 | 8 maxwell street |  | Tauton | MA | 2780 | 8572664899 | electrician | marcelinelectric@gmail.com | Square D homeline | Breaker | NA | 50 |  | 2 Pole | Tower Manufacturing | Residence |  | 2025-02-13 | 2025-02-13 | [5 empty] | Gfci breaker tripping when feeding the stove. But regular breaker works fine. | GE | JB256RMSS |  | 2 family | kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/17606511705
2025-02-20 07:25 | Jesse | Kuhlman | 21804 | 313 Eastern Avenue | 46-4305562 | Lynn | MA | 1902 | 774.315.4077 | owner | ervis.kes@gmail.com | HOM250GFIC | Breaker | none | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-04 | 2024-11-04 | 10 Oakland Ave |  | Newton | MA | 2466 | Cook top tripped immediately when turned on | Samsung | NZ30K7880US/AA | NO | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17607116488
2025-02-20 09:36 | Jesse | Kuhlman | 21804 | 313 Eastern Avenue |  | Lynn | MA | 1902 | 7743154077 | Owner | ervis.kes@gmail.com | HOM250GFIC | Breaker | none | 50 | no | 2 Pole | Schneider Electric | Residence |  | 2024-12-04 | 2024-12-04 | 170 Worcester St. |  | Watertown | MA | 2472 | Cooktop tripped instantly when put in use | Bosch | NIT8060UC | NO | Single family | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17607548290
2025-02-20 16:27 | Peter | Keller | 13379 | 114 Boston Post Rd |  | Wayland | MA | 1778 | 5088898049 | President | peter.keller.electric@gmail.com | QF230A | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2024-11-20 | 2024-11-20 | 218 Willis Rd. |  | Sudbury | MA | 1776 | The GFCI circuit breaker trips the moment the appliance is turned on at the controls | Wolfe | DF36650/S/P | none | residential kitchen | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17609937043 | Chrome 133.0.0.0 / Windows | 151.203.56.70 | 1316806124 | 42.3513, -71.3626
2025-02-20 16:54 | Peter | Keller | 13379 | 114 Boston Post Rd |  | Wayland | MA | 1778 | 5088898049 | President | peter.keller.electric@gmail.com | GF230A | Breaker | breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2025-01-08 | 2025-01-08 | 308 Old Connecticut Path |  | Wayland | MA | 1778 | Range trips the GFCI breaker after turning power on to the appliance | Thermador | PRD366WHU | none | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17610090704 | Chrome 133.0.0.0 / Windows | 151.203.56.70 | 1316816730 | 42.3513, -71.3626
2025-02-20 16:59 | Peter | Keller | 13379 | 114 Boston Post Rd | Boston Post Rd | Wayland | MA | 1778 | 5083587087 | President | peter.keller.electric@gmail.com | Q120GF | Breaker | breaker | 20 |  | 1 Pole | Siemens | Residence |  | 2025-01-08 | 2025-01-08 | 308 Old Connecticut Path |  | Wayland | MA | 1778 | Appliance trips the GFCI breaker. Usually within 30 minutes of turning power on | Thermador | T36FT820NS | none | Kitchen | Kitchen refrigerator | No | No | No | No |  | https://www.formstack.com/admin/download/file/17610123255 | Chrome 133.0.0.0 / Windows | 151.203.56.70 | 1316818931 | 42.3513, -71.3626
2025-02-21 08:41 | Michael | Gallerane | 52746 | 149 Uxbridge RD, unit #3 |  | Mendon | MA | 1756 | 5089880991 | Owner | mike@coreelectricalservices.com | Eaton CH250GFT | Breaker | breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-07-08 | 2024-07-08 | 46 Munroe Rd |  | Lexington | MA | 2421 | Stove tripped gfci breaker as soon as installed. ¦Installed stove on regular breaker to make sure it works. ¦Ran stove to try & burn off the element to see if it work on gfci breaker.¦Tried to reinstall after a month of working on the regular breaker, stills trips as soon as the stove is plugged in. | Fisher & Paykel | RHV3 | no | Single Family | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/17612334409 | Chrome 133.0.0.0 / Windows | 76.37.202.151 | 1316995907 | 44.2157, -70.558
2025-02-21 08:41 | Michael | Gallerane | 52746 | 149 Uxbridge RD, unit #3 |  | Mendon | MA | 1756 | 5089880991 | Owner | mike@coreelectricalservices.com | Eaton CH250GFT | Breaker | breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2024-07-08 | 2024-07-08 | 46 Munroe Rd |  | Lexington | MA | 2421 | Stove tripped gfci breaker as soon as installed. ¦Installed stove on regular breaker to make sure it works. ¦Ran stove to try & burn off the element to see if it work on gfci breaker.¦Tried to reinstall after a month of working on the regular breaker, stills trips as soon as the stove is plugged in. | Fisher & Paykel | RHV3 | no | Single Family | Kitchen | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/17612334973 | Chrome 133.0.0.0 / Windows | 76.37.202.151 | 1316995956 | 44.2157, -70.558
2025-02-21 10:21 | Sean | Dixon | 56309 | 110 Hamilton St. |  | Saugus | MA | 1906 | 781 520 3281 | General Foreman | sdixon@elpelec.com | Seimens 40AQPFGFCI | Breaker | Standard | 40 |  | 2 Pole | Siemens | Residence |  | 2025-02-21 | 2025-02-14 | 485 Mystic Valley Pky. |  | Somerville | MA | 2145 | Nuisance trip on bake mode. | GE | JS645FL8SS |  | Kitchen | Kitchens | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17612776097 | Chrome 133.0.0.0 / Windows | 100.0.18.213 | 1317031876 | 42.6028, -71.2319
2025-02-21 11:47 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 101 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613231186 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317064709 | 42.724, -71.479
2025-02-21 11:52 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 102 |  | Wilmington | MA | 1887 | When warming up the oven | Kitcen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613260931 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317066749 | 42.724, -71.479
2025-02-21 11:56 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 103 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613285594 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317068591 | 42.724, -71.479
2025-02-21 11:58 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 104 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613296917 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317069353 | 42.724, -71.479
2025-02-21 12:00 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 105 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613306902 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317070035 | 42.724, -71.479
2025-02-21 12:05 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 106 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613350704 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317073680 | 42.724, -71.479
2025-02-21 12:11 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 107 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613402472 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317077840 | 42.724, -71.479
2025-02-21 12:14 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 109 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613417653 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317078948 | 42.724, -71.479
2025-02-21 12:16 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 113 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613432569 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317080014 | 42.724, -71.479
2025-02-21 12:17 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 114 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613443877 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317080835 | 42.724, -71.479
2025-02-21 12:19 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 115 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613453683 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317081566 | 42.724, -71.479
2025-02-21 12:21 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 116 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613465437 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317082438 | 42.724, -71.479
2025-02-21 12:28 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 117 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613510456 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317085879 | 42.724, -71.479
2025-02-21 12:33 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 118 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613540273 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317088028 | 42.724, -71.479
2025-02-21 12:35 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 119 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen AId | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613550564 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317088895 | 42.724, -71.479
2025-02-21 12:36 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 120 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613560762 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317089674 | 42.724, -71.479
2025-02-21 12:38 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 201 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613569503 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317090362 | 42.724, -71.479
2025-02-21 12:46 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 202 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613614378 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317093548 | 42.724, -71.479
2025-02-21 12:48 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 203 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613623769 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317094249 | 42.724, -71.479
2025-02-21 12:49 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 204 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613631758 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317094815 | 42.724, -71.479
2025-02-21 12:51 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 205 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613640803 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317095413 | 42.724, -71.479
2025-02-21 12:52 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 207 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613650034 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317096023 | 42.724, -71.479
2025-02-21 12:54 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 208 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613658425 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317096641 | 42.724, -71.479
2025-02-21 12:55 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 211 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613667178 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317097285 | 42.724, -71.479
2025-02-21 12:58 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 213 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613684368 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317098508 | 42.724, -71.479
2025-02-21 12:59 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 214 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613691889 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317099090 | 42.724, -71.479
2025-02-21 13:01 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 215 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613700746 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317099739 | 42.724, -71.479
2025-02-21 13:02 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 216 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613710614 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317100490 | 42.724, -71.479
2025-02-21 13:04 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 217 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613720951 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317101229 | 42.724, -71.479
2025-02-21 13:06 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 218 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613728748 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317101824 | 42.724, -71.479
2025-02-21 13:07 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HPOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 219 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613736596 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317102367 | 42.724, -71.479
2025-02-21 13:09 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 220 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613746389 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317103053 | 42.724, -71.479
2025-02-21 13:15 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 301 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613783544 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317105663 | 42.724, -71.479
2025-02-21 13:17 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 302 |  | Wilmington | ME | 1887 | When warming up the oven | Schneider Electric HOM250GFI | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613795646 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317106542 | 42.724, -71.479
2025-02-21 13:19 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 303 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613804231 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317107128 | 42.724, -71.479
2025-02-21 13:20 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 304 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613811017 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317107648 | 42.724, -71.479
2025-02-21 13:22 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 305 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613819314 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317108227 | 42.724, -71.479
2025-02-21 13:23 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 306 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613827749 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317108812 | 42.724, -71.479
2025-02-21 13:25 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 307 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613837133 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317109443 | 42.724, -71.479
2025-02-21 13:26 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 308 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613845435 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317110087 | 42.724, -71.479
2025-02-21 13:28 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 311 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613856085 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317110843 | 42.724, -71.479
2025-02-21 13:30 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 313 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613868787 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317111707 | 42.724, -71.479
2025-02-21 13:32 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 314 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613878513 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317112364 | 42.724, -71.479
2025-02-21 13:34 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 315 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613891195 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317113197 | 42.724, -71.479
2025-02-21 13:39 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 316 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613919371 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317115105 | 42.724, -71.479
2025-02-21 13:40 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 317 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613926786 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317115615 | 42.724, -71.479
2025-02-21 13:42 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 318 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613936551 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317116234 | 42.724, -71.479
2025-02-21 13:43 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 319 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613945677 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317116887 | 42.724, -71.479
2025-02-21 13:45 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-13 | 2025-02-14 | 203 Lowell Street Unit 320 |  | Wilmington | MA | 1887 | When warming up the oven | Kitchen Aid | KSGG700E |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17613952907 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317117409 | 42.724, -71.479
2025-02-23 16:56 | Robert | Devlin | 1226426784 | 17 Harrisson Ave |  | GLOUCESTER | MA | 1930 | 9787045151 | Homeowner & electrican | rdevlin@gloucesterschools.com | Leviton AGTR2-W | Receptacle | none | 20 |  | 1 Pole | Leviton | Residence |  | 2025-01-03 | 2024-12-10 | 17 Harrisson Ave |  | GLOUCESTER | MA | 1930 | When the New Refrigerator was first plugged in The AFCI/GFCI outlet tripped. I reset the AFCI / GFCI outlet and it would trip after about 30 seconds. I then plugged in the old refrigerator and the AFCI / GFCI outlet didn't trip. I then replaced the AFCI / GFCI outlet with just an AFCI outlet and it didn't trip. | Frigdaire | GRFN2023AF | NONE | Single Family Kitchen | Just the Refrigerator circuit.¦In the Refrigerator use & Care on page's 6 & 7 it recommends not to plug into a GFCI protected circuit | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/17619753996 | Chrome 132.0.0.0 / Windows | 73.249.93.11 | 1317569163 | 42.6219, -70.6762
2025-02-24 09:36 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 101 |  | North Reading | MA | 1864 | When warming up th eoven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17621999623 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317718155 | 42.724, -71.479
2025-02-24 09:38 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 102 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622007990 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317718679 | 42.724, -71.479
2025-02-24 09:39 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 103 |  | North Reading | MA | 1864 | When warming up the oven | Whirpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622014860 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317719139 | 42.724, -71.479
2025-02-24 09:40 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 104 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622021414 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317719557 | 42.724, -71.479
2025-02-24 09:42 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 105 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622028016 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317720039 | 42.724, -71.479
2025-02-24 09:43 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 106 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622034837 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317720530 | 42.724, -71.479
2025-02-24 09:45 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 107 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622044653 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317721149 | 42.724, -71.479
2025-02-24 09:46 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 108 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622052896 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317721642 | 42.724, -71.479
2025-02-24 09:48 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 109 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622060254 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317722117 | 42.724, -71.479
2025-02-24 09:49 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 110 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622068023 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317722629 | 42.724, -71.479
2025-02-24 09:51 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 111 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622075707 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317723138 | 42.724, -71.479
2025-02-24 09:52 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 112 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622084267 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317723653 | 42.724, -71.479
2025-02-24 09:53 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 113 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622091034 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317724138 | 42.724, -71.479
2025-02-24 09:55 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 201 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622101027 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317724790 | 42.724, -71.479
2025-02-24 09:58 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 202 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622116370 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317725823 | 42.724, -71.479
2025-02-24 10:02 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 203 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622138159 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317727365 | 42.724, -71.479
2025-02-24 10:29 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 204 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622305470 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317738424 | 42.724, -71.479
2025-02-24 10:30 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 205 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622315404 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317739065 | 42.724, -71.479
2025-02-24 10:32 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 206 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622325357 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317739670 | 42.724, -71.479
2025-02-24 10:42 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 207 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622392808 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317744043 | 42.724, -71.479
2025-02-24 10:45 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 208 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622410778 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317745246 | 42.724, -71.479
2025-02-24 10:46 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 209 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622419048 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317745806 | 42.724, -71.479
2025-02-24 10:48 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 210 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622430091 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317746538 | 42.724, -71.479
2025-02-24 10:49 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 211 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622437954 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317747049 | 42.724, -71.479
2025-02-24 10:51 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFi | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 212 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622446658 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317747607 | 42.724, -71.479
2025-02-24 10:52 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 213 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622457001 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317748250 | 42.724, -71.479
2025-02-24 10:55 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 301 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622476973 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317749550 | 42.724, -71.479
2025-02-24 10:57 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 302 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622488366 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317750244 | 42.724, -71.479
2025-02-24 10:59 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 303 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622506089 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317751348 | 42.724, -71.479
2025-02-24 11:01 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 304 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622515934 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317752000 | 42.724, -71.479
2025-02-24 11:02 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 305 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622524281 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317752533 | 42.724, -71.479
2025-02-24 11:04 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 306 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622533497 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317753147 | 42.724, -71.479
2025-02-24 11:05 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 307 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622543856 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317753820 | 42.724, -71.479
2025-02-24 11:07 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HPM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 308 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622553422 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317754463 | 42.724, -71.479
2025-02-24 11:08 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFi | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 309 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622561631 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317754996 | 42.724, -71.479
2025-02-24 11:10 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 310 |  | North Reading | MA | 1864 | When warming up the oven | Whirlool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622576642 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317755964 | 42.724, -71.479
2025-02-24 11:12 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 311 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622585793 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317756557 | 42.724, -71.479
2025-02-24 11:13 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 312 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622596232 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317757278 | 42.724, -71.479
2025-02-24 11:15 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 313 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622607253 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317758362 | 42.724, -71.479
2025-02-24 11:17 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 401 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622618322 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317759122 | 42.724, -71.479
2025-02-24 11:36 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 402 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622741437 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317767251 | 42.724, -71.479
2025-02-24 11:37 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 403 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622751723 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317767927 | 42.724, -71.479
2025-02-24 11:39 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 404 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622760975 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317768569 | 42.724, -71.479
2025-02-24 11:40 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 405 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622769380 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317769131 | 42.724, -71.479
2025-02-24 11:41 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 406 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622776948 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317769651 | 42.724, -71.479
2025-02-24 11:42 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 407 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622784878 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317770221 | 42.724, -71.479
2025-02-24 11:44 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HO250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 408 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622795201 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317770923 | 42.724, -71.479
2025-02-24 11:46 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 409 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622810564 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317771944 | 42.724, -71.479
2025-02-24 11:47 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | /A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 410 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622819638 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317772546 | 42.724, -71.479
2025-02-24 11:49 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 411 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622829750 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317773195 | 42.724, -71.479
2025-02-24 11:50 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 412 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622837786 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317773737 | 42.724, -71.479
2025-02-24 11:51 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 501 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622846289 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317774303 | 42.724, -71.479
2025-02-24 11:53 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 502 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622856454 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317774951 | 42.724, -71.479
2025-02-24 11:54 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 503 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622865091 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317775506 | 42.724, -71.479
2025-02-24 11:55 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 504 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622874330 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317776099 | 42.724, -71.479
2025-02-24 11:58 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFi | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 505 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622894231 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317777465 | 42.724, -71.479
2025-02-24 12:00 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HO250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 506 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622907900 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317778346 | 42.724, -71.479
2025-02-24 12:01 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 507 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpol | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622916495 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317778946 | 42.724, -71.479
2025-02-24 12:03 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 508 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622925892 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317779610 | 42.724, -71.479
2025-02-24 12:11 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 509 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622981374 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317783377 | 42.724, -71.479
2025-02-24 12:13 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 510 |  | North Reading | MA | 1864 | When warming up the oven | Wirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17622991596 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317784033 | 42.724, -71.479
2025-02-24 12:14 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 511 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623002824 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317784694 | 42.724, -71.479
2025-02-24 12:18 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 300 Martins Landing Unit 512 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623026773 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317786273 | 42.724, -71.479
2025-02-24 12:38 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 4 Stratton Drive Unit # 103 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623157683 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317794957 | 42.724, -71.479
2025-02-24 12:40 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 4 Stratton Drive Unit # 205 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623167324 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317795601 | 42.724, -71.479
2025-02-24 12:41 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 4 Stratton Drive Unit # 301 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623176708 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317796210 | 42.724, -71.479
2025-02-24 12:43 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-30 | 2025-01-31 | 4 Stratton Drive Unit # 407 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE975H0HZ4 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623186708 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317796837 | 42.724, -71.479
2025-02-24 12:48 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 101 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623224013 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317799167 | 42.724, -71.479
2025-02-24 12:50 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 102 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623235269 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317799880 | 42.724, -71.479
2025-02-24 12:52 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 103 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623245449 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317800533 | 42.724, -71.479
2025-02-24 12:53 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 104 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623255614 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317801183 | 42.724, -71.479
2025-02-24 12:55 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 105 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623265336 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317801818 | 42.724, -71.479
2025-02-24 12:56 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 106 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623274458 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317802395 | 42.724, -71.479
2025-02-24 12:58 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 107 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623283800 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317803061 | 42.724, -71.479
2025-02-24 12:59 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 108 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623291979 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317803547 | 42.724, -71.479
2025-02-24 13:01 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 109 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623302267 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317804252 | 42.724, -71.479
2025-02-24 13:02 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 110 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623310994 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317804852 | 42.724, -71.479
2025-02-24 13:03 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 111 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623319710 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317805462 | 42.724, -71.479
2025-02-24 13:05 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM50GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 112 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623328823 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317806071 | 42.724, -71.479
2025-02-24 13:06 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 113 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623336957 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317806583 | 42.724, -71.479
2025-02-24 13:08 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 201 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623351884 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317807565 | 42.724, -71.479
2025-02-24 13:11 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 202 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623368169 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317808635 | 42.724, -71.479
2025-02-24 13:12 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 203 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623376974 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317809201 | 42.724, -71.479
2025-02-24 13:14 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 204 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623386150 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317809755 | 42.724, -71.479
2025-02-24 13:15 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 205 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623394823 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317810324 | 42.724, -71.479
2025-02-24 13:17 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 206 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623406957 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317811117 | 42.724, -71.479
2025-02-24 13:19 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 207 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623417971 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317811895 | 42.724, -71.479
2025-02-24 13:20 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 208 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623427026 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317812461 | 42.724, -71.479
2025-02-24 13:21 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 209 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623437640 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317813141 | 42.724, -71.479
2025-02-24 13:23 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 210 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623446829 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317813744 | 42.724, -71.479
2025-02-24 13:24 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 211 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623456864 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317814416 | 42.724, -71.479
2025-02-24 13:26 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 212 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623466592 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317815082 | 42.724, -71.479
2025-02-24 13:27 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 213 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623478642 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317815893 | 42.724, -71.479
2025-02-24 13:40 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 301 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623556977 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317821208 | 42.724, -71.479
2025-02-24 13:41 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 302 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623565157 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317821760 | 42.724, -71.479
2025-02-24 13:42 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 303 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623574884 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317822346 | 42.724, -71.479
2025-02-24 13:43 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 304 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623583634 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317822912 | 42.724, -71.479
2025-02-24 13:45 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 305 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623592756 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317823508 | 42.724, -71.479
2025-02-24 13:46 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 306 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623601711 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317824111 | 42.724, -71.479
2025-02-24 13:48 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 307 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623610409 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317824699 | 42.724, -71.479
2025-02-24 13:49 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 308 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623618576 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317825266 | 42.724, -71.479
2025-02-24 13:50 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 309 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623628462 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317825873 | 42.724, -71.479
2025-02-24 13:52 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 310 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623636227 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317826441 | 42.724, -71.479
2025-02-24 13:53 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 311 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623644459 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317827010 | 42.724, -71.479
2025-02-24 13:55 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM25GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 312 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623655508 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317827727 | 42.724, -71.479
2025-02-24 13:59 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 401 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623683515 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317829652 | 42.724, -71.479
2025-02-24 14:00 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 402 |  | woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623695632 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317830507 | 42.724, -71.479
2025-02-24 14:02 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 403 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623704174 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317831079 | 42.724, -71.479
2025-02-24 14:03 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 404 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623712716 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317831656 | 42.724, -71.479
2025-02-24 14:04 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 405 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623719285 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317832141 | 42.724, -71.479
2025-02-24 14:06 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 406 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623727833 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317832779 | 42.724, -71.479
2025-02-24 14:07 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 407 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623737348 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317833365 | 42.724, -71.479
2025-02-24 14:08 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 408 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623746065 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317833919 | 42.724, -71.479
2025-02-24 14:09 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 409 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623755149 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317834516 | 42.724, -71.479
2025-02-24 14:10 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 410 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623762454 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317835013 | 42.724, -71.479
2025-02-24 14:12 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 411 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623770459 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317835535 | 42.724, -71.479
2025-02-24 14:13 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-20 | 2025-02-21 | 6 Stratton Drive Unit # 412 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17623779855 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1317836132 | 42.724, -71.479
2025-02-24 17:03 | David | Barth | 30821 | 21 Washburn Street, Northborough, M |  | Northborough | AL | 1532 | 7746960901 | Contractor | barthelec@verizon.net | QO260GFI | Breaker | NO | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-24 | 2025-02-24 | 138 Bartlett St |  | Northborough | MA | 1532 | breaker trip when stove is turned on | Viking | VISC5304BSS | NONE | HOME | kITCHEN | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17624875884 | Chrome 133.0.0.0 / Windows | 72.74.152.27 | 1317908316 | 42.3182, -71.6429
2025-02-25 12:45 | Alan | Stearns | 17349 | 261 Main Street |  | Oxford | MA | 1540 | 5089876225 | Owner | al.stearns@stearnselectricinc.com | Siemens QPFB | Breaker | Circuit Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2025-02-19 | 2025-02-19 | 110 High Street |  | Shrewsbury | MA | 1545 | GFCI Circuit Breaker will trip when oven is turned on. | Wolf Appliance, Inc. | DF30450/S/P |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17628927064 | Chrome 133.0.0.0 / Windows | 71.11.16.75 | 1318174376 | 42.0491, -71.8944
2025-02-25 12:58 | Alan | Stearns | 17349 | 261 Main Street |  | Oxford | MA | 1540 | 5089876225 | Owner | al.stearns@stearnselectricinc.com | Siemens QPFB | Breaker | Circuit Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2025-02-19 | 2025-02-19 | 110 High Street |  | Shrewsbury | MA | 1545 | GFCI circuit breaker will trip when oven is turned on. | Wolf Appliance, Inc. | DF30450/S/P |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17629013702 | Chrome 133.0.0.0 / Windows | 71.11.16.75 | 1318179915 | 42.0491, -71.8944
2025-02-25 20:39 | Richard | Chase | 21093 | P.O. Box 8112 |  | Ward Hill | MA | 1835 | 7815890262 | Master Electrician/Proprietor | RChaseElectric@gmail.com | CHFN120DF | Breaker | Breaker | 20 |  | 1 Pole | Eaton | Residence |  | 2025-01-06 | 2024-12-18 | 26 Gould Rd. |  | Andover | MA | 1810 | Refrigerator nuisance tripped at least once daily since initial installation. Three attempts were made to replace the circuit breaker with the same model, and the same problem occurred. Called inspector of wires, and was advised to replace breaker with AFCI and replaced receptacle with a single receptacle. | Whirlpool | GZ25FSRXYY0 | None | Single Family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17631591810 | Firefox 135.0 / Windows | 104.236.212.124 | 1318349783 | 40.8364, -74.1403
2025-02-26 10:45 | Jorge | Romero | 21628 | 2 Neptune Rd | #407 | Boston | MA | 2128 | 6179089677 | Electrician | jorge@rokocorp.com | GFTCB250 | Breaker | GFCI 2POLE 50AMP BREAKER EATON | 50 |  | 2 Pole | Eaton | Residence |  | 2025-02-07 | 2023-01-31 | 432 RINDGE AVE |  | CAMBRIDGE | MA | 2140 | Breaker for oven started to trip the GFCI. After checking everything, found that the GFCI breaker was causing nuisance tripping. | General Electric | JB625DKBWW |  | Residential | Kitchen stove | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/17633855355 | Chrome 133.0.0.0 / OS X | 174.226.87.128 | 1318494640 | 42.2518, -71.0805
2025-02-26 12:07 | Matthew | Doremus | 21923 | 244 Cedar St. #3 |  | Somerville | MA | 2145 | 7817386180 | Owner | matt@symmetry-electric.com | Siemens QF250A | Breaker | n/a | 50 |  | 2 Pole | Siemens | Residence |  | 2025-02-19 | 2025-02-19 | 60 Whittier St |  | Melrose | MA | 2176 | GFCI breaker trips when oven is turned on. | viking | VOSC305-4BSS |  | single family | Kitchen range | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17634401001 | Firefox 134.0 / OS X | 71.235.121.19 | 1318530055 | 42.3399, -71.1245
2025-02-26 12:39 | Chris | Christoforou | 33902 | 12 Knollwood Rd Paxton |  | Paxton | MA | 1612 | 5084148685 | Electrician | chrischristoforou508@gmail.com | Eaton | Breaker | Br 240v | 30 |  | 2 Pole | Eaton | Residence |  | 2025-01-16 | 2024-10-17 | 11 Lincoln rd |  | Wellesley | MA | 1870 | Dryer Would trip GFCI breaker every other load homeowner Notified Yale electric about problem and they came out and replaced it. New dryer would do the same I Took apart receptacle and wire off GFI circuit breaker Perform continuity on wires everything was okay replaced GFI breaker With regular circuit breaker 30 amp 240 V Eaton That held | GE | PFD5ESPIDS | No | Single-family home | Only clothes dryer | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17634602073 | Mobile Safari 18.1.1 / iOS | 107.77.223.67 | 1318542884 | 41.8483, -87.6517
2025-02-26 14:01 | James | Rickenberg | 58376 | 31 Fortunes Furrow Way |  | Brewster | MA | 2631 | 2014930231 | Owner | nrickenberg64@gmail.com | hom250gfi | Breaker | o | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-26 | 2025-02-26 | 31 Fortunes Furrow Way |  | Brewster | MA | 2631 | When turned on it instantly trips. | Bertazzoni | MAST365INSXT | None | Kitchen | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17635129645 | https://www.formstack.com/admin/download/file/17635129646 | Chrome 133.0.0.0 / OS X | 73.182.212.67 | 1318576961 | 42.0857, -70.999
2025-02-28 07:01 | William | Cooke | 18314 | PO BOX 950 | 543 North Washington St | North Attleboro | MA | 2761 | 5082940827 | Master Electrician | bill@pachecocooke.com | GFTCB240 | Breaker | Eaton Breaker | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17647297650 | 2025-02-25 | 2024-12-03 | 26 Avery Way |  | Norfolk | MA | 2056 | Trip's 1.3 times daily when stove is not in use | LG | LSIS6338FE | NONE | Kitchen | Kitchen Range | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17647297664 | https://www.formstack.com/admin/download/file/17647297665 | Chrome 133.0.0.0 / Windows | 76.119.111.51 | 1319355523 | 42.3687, -71.0863
2025-02-28 09:27 | David | Santos | 22784 | 341 Oak St |  | Swansea | MA | 2777 | 401-255-6368 | Electrician | aplus.santos@gmail.com | Siemens QF250A | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17647894608 | 2024-12-23 | 2024-12-23 | 8 Barnes Way |  | Walpole | MA | 2081 | We installed the GFCI breaker which held without issues prior to the installation of the stove. Once the induction oven was installed immediately upon plugging it in it tripped the breaker we tried to reset the breaker several times and it continued to trip. We replace it with two other breakers all the same outcome instant tripping. W e investigated the Range for neutral / ground bonded which they were not bonded inside the unit. | Electrolux | ECFI3668AS | NONE | single family home | Kitchen Range | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17647894622 | https://www.formstack.com/admin/download/file/17647894623 | Chrome 133.0.0.0 / Windows | 158.123.187.117 | 1319397885 | 41.8451, -71.4388
2025-03-02 10:06 | Frano | Irvine | 54256 | 44 Ralph Street |  | Medford | MA | 2155 | 7819226035 | Homeowner | franoirvine@gmail.com | E82617 | Breaker | none | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17656492983 | 2024-12-13 | 2024-12-13 | [5 empty] | After Cranney Home Services upgraded my panel and installed a new QPF breaker, the breaker trips every time the oven is turned on for more than 2 mins. This makes the oven unusable. | LG | LRE30453SB/02 | None | Kitchen | This affects the Oven in the Kitchen and makes it unusable. | No | No | No | No | https://www.formstack.com/admin/download/file/17656492996 | https://www.formstack.com/admin/download/file/17656492997 | Chrome 133.0.0.0 / Windows | 72.74.49.31 | 1319968974 | 42.4597, -71.0638
2025-03-03 07:43 | DANIEL | WHITELEY | 22453 | 52 COTTAGE ST |  | EASTHAMPTON | MA | 1027 | 4135271440 | PRESIDENT | WHITELEYELECTRIC@AOL.COM | EATON | Breaker | NONE | 40 |  | 2 Pole | Eaton | Residence |  | 2025-03-01 | 2025-02-12 | 334 MAIN ST UNIT 4 |  | EASTHAMPTON | MA | 1027 | NEW RANGE CAUSES GFI BREAKER TO CONSTANTLY TRIP | GE | J82560M3WW | NONE | DWELLING | KITCHEN | Yes | No | No | No | https://www.formstack.com/admin/download/file/17659947353 | https://www.formstack.com/admin/download/file/17659947354 | Safari 18.3 / OS X | 96.39.48.177 | 1320194842 | 42.1763, -72.5771
2025-03-03 10:56 | Josh | Hernandez | 23723 | 14a Wendover rd |  | worcester | MA | 1606 | 5083405972 | owner | joshhernandezelectric@gmail.com | QO250GFIC | Breaker | no | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17661167594 | 2025-02-28 | 2025-02-28 |  |  | Shrewsbury | MA | 1545 | When the GFCI breaker is installed it will hold for about 10 minutes then it will trip. | Kithcen Aid | KXD4636YSS7 | No | Single Family Residential | This 50a circuit is controlling a cooktop kitchen appliance. | No | No | No | No | https://www.formstack.com/admin/download/file/17661167619 | https://www.formstack.com/admin/download/file/17661167620 | Safari 18.3 / OS X | 104.28.76.74 | 1320269540 | 42.2624, -71.8011
2025-03-04 07:14 | Ryan | LaBrache | 22042 | 1 Summer St |  | Watertown | MA | 2472 | 617-924-8866 | Owner | ryan@lampasonabloomer.com | Q120DF | Breaker | NA | 20 |  | 1 Pole | Siemens | Residence |  | 2025-02-27 | 2025-02-20 | 19 Chauncy St |  | Cambridge | MA | 2138 | Dual function breaker would trip instantly when turning on disposal | Insinkerator | pro cvr cntrl-8 |  | multifamily | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17666738208 | Chrome 133.0.0.0 / Windows | 174.168.255.194 | 1320623098 | 43.6444, -72.2455
2025-03-04 09:13 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-03-04 | 2025-03-03 | 660 Main St. |  | Worcester | MA |  | Apt 604¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667146720 | Chrome 133.0.0.0 / Windows | 66.168.40.27 | 1320653331 | 42.2555, -71.7719
2025-03-04 09:21 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-04 | 2025-03-03 | 660 Main St. |  | Worcester | MA |  | Apt 504¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17667188037 | Chrome 133.0.0.0 / Windows | 66.168.40.27 | 1320656353 | 42.2555, -71.7719
2025-03-04 09:28 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 6034906301 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #101 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667220680 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320658651 | 42.724, -71.479
2025-03-04 09:28 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-04 | 2025-03-03 | 660 Main St. |  | Worcester | MA |  | Apt 404¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17667221515 | Chrome 133.0.0.0 / Windows | 66.168.40.27 | 1320658710 | 42.2555, -71.7719
2025-03-04 09:29 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 6034906301 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #102 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667228149 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320659227 | 42.724, -71.479
2025-03-04 09:31 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 6034906301 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #103 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667237348 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320659837 | 42.724, -71.479
2025-03-04 09:32 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 6034906301 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #104 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667243591 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320660291 | 42.724, -71.479
2025-03-04 09:34 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-04 | 2025-03-03 | 660 Main St. |  | Worcester | MA |  | Apt 304¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17667250433 | Chrome 133.0.0.0 / Windows | 66.168.40.27 | 1320660771 | 42.2555, -71.7719
2025-03-04 09:34 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 6034906301 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #105 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667251062 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320660822 | 42.724, -71.479
2025-03-04 09:36 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #106 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667260573 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320661468 | 42.724, -71.479
2025-03-04 09:39 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #107 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667279729 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320662748 | 42.724, -71.479
2025-03-04 09:41 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #108 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667289300 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320663400 | 42.724, -71.479
2025-03-04 09:41 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-04 | 2025-03-03 | 660 Main St. |  | Worcester | MA |  | Apt 204¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17667291676 | Chrome 133.0.0.0 / Windows | 66.168.40.27 | 1320663575 | 42.2555, -71.7719
2025-03-04 09:42 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #109 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667295992 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320663864 | 42.724, -71.479
2025-03-04 09:44 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #110 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667304371 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320664480 | 42.724, -71.479
2025-03-04 09:45 | Mark | Thibault | 146667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #111 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667311148 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320664957 | 42.724, -71.479
2025-03-04 09:46 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #112 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667317926 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320665423 | 42.724, -71.479
2025-03-04 09:48 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #113 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667325014 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320665945 | 42.724, -71.479
2025-03-04 09:49 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #201 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667332448 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320666508 | 42.724, -71.479
2025-03-04 09:51 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #202 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667340882 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320667061 | 42.724, -71.479
2025-03-04 09:52 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #203 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667347147 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320667527 | 42.724, -71.479
2025-03-04 09:53 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #204 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667353128 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320667957 | 42.724, -71.479
2025-03-04 09:55 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #205 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667359964 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320668405 | 42.724, -71.479
2025-03-04 09:56 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #206 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667369299 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320669048 | 42.724, -71.479
2025-03-04 09:58 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #207 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667376763 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320669576 | 42.724, -71.479
2025-03-04 09:59 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #208 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667384090 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320670109 | 42.724, -71.479
2025-03-04 10:01 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #209 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667398339 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320671126 | 42.724, -71.479
2025-03-04 10:03 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #210 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667408003 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320671853 | 42.724, -71.479
2025-03-04 10:05 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #211 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667417032 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320672466 | 42.724, -71.479
2025-03-04 10:06 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #212 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667424101 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320673006 | 42.724, -71.479
2025-03-04 10:07 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #213 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667432625 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320673665 | 42.724, -71.479
2025-03-04 10:09 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #301 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667441594 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320674353 | 42.724, -71.479
2025-03-04 10:10 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #302 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667449684 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320674972 | 42.724, -71.479
2025-03-04 10:11 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #303 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667456145 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320675519 | 42.724, -71.479
2025-03-04 10:13 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #304 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667464353 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320676170 | 42.724, -71.479
2025-03-04 10:14 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #305 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667472110 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320676731 | 42.724, -71.479
2025-03-04 10:15 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #306 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667480128 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320677395 | 42.724, -71.479
2025-03-04 10:16 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #307 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667489134 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320678141 | 42.724, -71.479
2025-03-04 10:18 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #308 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667497916 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320678933 | 42.724, -71.479
2025-03-04 10:19 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #309 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667508302 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320679820 | 42.724, -71.479
2025-03-04 10:20 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #310 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667518541 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320680722 | 42.724, -71.479
2025-03-04 10:21 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #311 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667528661 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320681550 | 42.724, -71.479
2025-03-04 10:23 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #312 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667540331 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320682502 | 42.724, -71.479
2025-03-04 10:25 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #401 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667559430 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320684028 | 42.724, -71.479
2025-03-04 10:26 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #402 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667569430 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320684826 | 42.724, -71.479
2025-03-04 10:28 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #403 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667580109 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320685714 | 42.724, -71.479
2025-03-04 10:46 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #404 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667709854 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320695647 | 42.724, -71.479
2025-03-04 10:47 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #405 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667723791 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320696700 | 42.724, -71.479
2025-03-04 10:49 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #406 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667732563 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320697383 | 42.724, -71.479
2025-03-04 10:50 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #407 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667741472 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320698067 | 42.724, -71.479
2025-03-04 10:51 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #408 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667750725 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320698786 | 42.724, -71.479
2025-03-04 10:52 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #409 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667760831 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320699478 | 42.724, -71.479
2025-03-04 10:53 | Cole | Powers | 18122 | P.O. Box 4549 |  | Vineyard Haven 1 | MA | 2568 | 5082808272 | Owner | powerselectric@comcast.net | CHN250GF | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2025-03-20 | 2025-03-20 | 13 Wampum Way |  | Chilmark | MA | 2535 | Qualified technician landed 6-3 Romex on 50amp 2-pole GFCI breaker. Upon circuit being energized, the breaker would trip instantly. Technician proceeded to systematically test for continuity between neutral and ground on the range appliance and the wires from the panel. Upon further investigation and inspection of the terminations and the wiring integrity, the issue was made known to the local inspector of wires. | Bosch | HIS8055U/06 | N/A | Kitchen | Small Kitchen, recently renovated. | No | No | No | No |  | https://www.formstack.com/admin/download/file/17667768610 | Chrome 133.0.0.0 / Windows | 76.152.41.177 | 1320700132 | 42.7746, -71.5142
2025-03-04 11:06 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #410 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667864386 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320707474 | 42.724, -71.479
2025-03-04 11:07 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #411 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667874511 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320708231 | 42.724, -71.479
2025-03-04 11:09 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-02-27 | 2025-02-28 | 4 Winslow Lane Unit #412 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667884491 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320708987 | 42.724, -71.479
2025-03-04 11:12 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-10 | 2024-12-11 | 6208 Peters Farm Way |  | Westborough | MA | 1581 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667905761 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320710552 | 42.724, -71.479
2025-03-04 11:13 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-10 | 2024-12-11 | 260 Martins Landing Unit # 105 |  | North Reading | MA | 1864 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667919829 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320711579 | 42.724, -71.479
2025-03-04 11:15 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-12-11 | 2024-12-12 | 2 Winslow Lane Unit # 310 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667933953 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320712546 | 42.724, -71.479
2025-03-04 11:18 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-11-13 | 2024-11-14 | 2 Winslow Lane Unit # 206 |  | Grafton | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667951636 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320713843 | 42.724, -71.479
2025-03-04 11:19 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250GFI | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-07 | 2025-01-08 | 6202 Peters Farm Way |  | Westborough | MA | 1536 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667962689 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320714654 | 42.724, -71.479
2025-03-04 11:20 | Mark | Thibault | 14667 | 1 INDUSTRIAL WAY UNIT #5 |  | TYNGSBORO | MA | 1879 | 9782265946 | President | mark@stelectrical.net | Schneider Electric HOM250HOM | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-03-02 | 2025-03-03 | 2 Stratton Drive Unit # 307 |  | Woburn | MA | 1801 | When warming up the oven | Whirlpool | KSEG700ESS6 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17667972935 | Chrome 133.0.0.0 / Windows | 72.93.233.105 | 1320715407 | 42.724, -71.479
2025-03-04 19:43 | Corey | Hood | 8228 | 66 Bess Road |  | Needham | MA | 2492 | 7819157358 | owner | coreyhoodelectric@gmail.com | BRN240GF | Breaker | 2 Pole | 40 |  | 2 Pole | Eaton | Residence |  | 2025-03-01 | 2025-03-01 | [5 empty] | Trips upon pre heat multiple times. | Thermador | PO302W/05 |  | Single Family | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17671412384 | Chrome 133.0.0.0 / OS X | 73.227.208.137 | 1320956891 | 42.1897, -71.2048
2025-03-04 22:08 | herneceau | marcelin | 59815 | 158 fisher st | unit 3 | north attleboro | MA | 2760 | 8572664899 | electrician | marcelinelectric@gmail.com | square D | Breaker | NA | 50 |  | 2 Pole | Tower Manufacturing | Residence |  | 2025-02-13 | 2025-02-13 | 8 Maxwell St |  | Taunton | MA | 2780 | The gfci Breaker trips anytime we plug the Range. But the range is working when using non gfci breaker. | Frigidaire | FCFE3062AS |  | 2 family house | kitchens | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17671929561 | Chrome 133.0.0.0 / Windows | 75.68.54.208 | 1320991141 | 42.3608, -71.2954
2025-03-05 10:49 | Andy | Woodford | 11549 | 74 SAND ST |  | GARDNER | MA | 1440 | 9787308870 | President | Woodfordelectric@gmail.com | Eaton QBGFT2020 | Breaker | none | 20 |  | 2 Pole | Eaton | Commercial |  | 2025-03-03 | 2025-01-06 | 70 Waterford St |  | Gardner | MA | 1440 | Installed a GFCI 2 pole breaker feeding a new commercial refrigerator. This breaker tripped once before, we replaced the breaker with another GFCI breaker. The second time the breaker tripped the customer lost the content of the refrigerator. ¦ | Atosa | MBF8003GR | none | Commercial kitchen | One appliance | No | No | No | No |  | https://www.formstack.com/admin/download/file/17674150627 | Chrome 133.0.0.0 / Windows | 73.89.71.164 | 1321148517 | 43.0417, -71.0772
2025-03-05 12:57 | Peter | Prus | 51711 | 8 Tulip Circle |  | South Grafton | MA | 1560 | 5082595679 | Electrician | peter.prus@forgeco.com | LB120-DFT | Breaker | None | 20 |  | 1 Pole | Leviton | Residence |  | 2025-01-03 | 2024-01-29 | 2 Launcher Way |  | Wayland | MA | 1778 | Random nuisance tripping from the dishwasher | GE | GDT550PYRFS | None | Single Family Residential | Kitchen appliances are causing nuisance tripping at the breaker. | Yes | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/17675204435 | Chrome 133.0.0.0 / OS X | 173.48.175.14 | 1321213865 | 42.2441, -71.1688
2025-03-05 12:58 | Peter | Prus | 51711 | 8 Tulip Circle |  | South Grafton | MA | 1560 | 5082595679 | Electrician | Peter.prus@forgeco.com | LB120-DFT | Breaker | none | 20 | none | 1 Pole | Leviton | Residence |  | 2025-01-03 | 2024-01-29 | 2 Launcher Way |  | Wayland | MA |  | Random tripping in kitchen | GE | gfe26jymfs | Nothing | single family home | Kitchen | Yes | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/17675213039 | Chrome 131.0.0.0 / OS X | 173.48.175.14 | 1321214405 | 42.2441, -71.1688
2025-03-05 15:46 | Ryan | LaBrache | 22042 | 1 Summer St |  | Watertown | MA | 2472 | 617-538-4851 | onwer | ryan@lampasonabloomer.com | BRN250GF | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2025-03-05 | 2025-02-24 | 986 Memorial Dr. #105 |  | Cambridge | MA | 2138 | Breaker would trip instantly when turning on the range | La Cornue Range | C9PF-I |  | multi family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17676616517 | Chrome 133.0.0.0 / Windows | 174.168.255.194 | 1321301842 | 43.6444, -72.2455
2025-03-06 07:36 | John | Morris | 51054 | 30 Johns Ave |  | Holbrook | MA | 2343 | 339-987-1361 | Electrician | jaylectricity@gmail.com | Square D | Breaker | n/a | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-03-03 | 2025-03-03 | [5 empty] | Range trips gfci breaker as soon as breaker is reset | Cornufe | c1-1 |  | single family | Kitchen | No | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17679703336 | Firefox 135.0 / Windows | 73.149.212.29 | 1321515686 | 42.2463, -70.9972
2025-03-06 10:46 | John | Morris | 51054 | 3 Johns Ave |  | Holbrook | MA | 2045 | 339-987-1361 | Selectivity | jaylectricity@gmail.com | Schneider 4884006004 | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-03-03 | 2025-03-03 | 68 Cross St |  | Hingham | MA | 2043 | Breaker trips as soon as energized | Cornufe | C1-1 |  | Single family | Kitchen range | No | Yes | Yes | Yes | https://www.formstack.com/admin/download/file/17680602263 | https://www.formstack.com/admin/download/file/17680602264 | Chrome Mobile 132.0.0.0 / Android | 72.74.170.150 | 1321576221 | 42.2229, -70.8819
2025-03-06 11:53 | Brian | toto | 13479 | 76 Peaslee Crossing |  | Newton | NH | 3858 | 6038196982 | Owner | briantoto1966@gmail.com | Seimans 2 pole 30 amp gfci breaker | Breaker | Nonr | 30 | None | 2 Pole | Siemens | Residence |  | 2025-03-06 | 2024-12-18 | 108 howard st |  | Saugus | MA | 1906 | Breaker trips when trying to use clothes dryer | Maytag | N/A | None | 1 family | Clothes dryer in laundry | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17681063382 | Chrome Mobile 133.0.0.0 / Android | 73.249.143.124 | 1321607607 | 42.7117, -71.1663
2025-03-06 12:34 | Peter | Prus | 51711 | 8 Tulip Cir |  | South GRafton | MA | 1560 | 5082595679 | Electrician | peter.prus@forgeco.com | LB120-DFT | Breaker | None | 20 |  | 1 Pole | Leviton | Residence |  | 2024-01-03 | 2024-01-29 | 92 Oxbow Rd |  | Wayland | MA | 1778 | Random Nuisance Tripping from Refrigerator | GE | GFE26JYMFS |  | Single Family Residential | Kitchen appliance causing a nuisance trip at breaker | Yes | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/17681350511 | Chrome 133.0.0.0 / OS X | 73.159.242.231 | 1321627364 | 42.3364, -71.0326
2025-03-10 08:50 | William | Cooke | 18314 | PO BOX 950 | 543 North Washington St | North Attleboro | MA | 2761 | 5082940827 | Owner | bill@pachecocooke.com | GFTCB230 | Breaker | Breaker | 30 |  | 2 Pole | Eaton | Residence |  | 2025-03-03 | 2025-03-06 | 41 Avery Way |  | Norfolk | MA | 2056 | Tripping when not in use an d on multiple occasion's¦Febuary 5,6,28,23 ¦ | DRYER(ELECTROLUX) | ELFE7637ATO |  | Laundry Room | Laundry Room | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17697122780 | Chrome 133.0.0.0 / Windows | 76.119.111.51 | 1322718635 | 42.3687, -71.0863
2025-03-10 08:55 | William | Cooke | 18314 | PO BOX 950 | 543 North Washington St | North Attleboro | MA | 2761 | 5082940827 | Owner | bill@pachecocooke.com | GFCB250 | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2025-02-27 | 2025-03-06 | 45 Avery Way |  | Norfolk | MA | 2056 | Feb 25,27,27 March 2,3, and multiple times with unit not being used | LG RANGE | LSIL6336FE/)) |  | Kitchen Area | Kitchen Area | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17697146009 | Chrome 133.0.0.0 / Windows | 76.119.111.51 | 1322720101 | 42.3687, -71.0863
2025-03-10 09:01 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-10 | 2025-03-06 | 660 Main St. |  | Worcester | MA |  | Apt 608¦¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | RAS240DM3WW | GE | NA | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17697170074 | Chrome 133.0.0.0 / Windows | 66.168.40.27 | 1322721635 | 42.2555, -71.7719
2025-03-10 09:12 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-03-10 | 2025-03-06 | 660 Main St. |  | Worcester | MA | 2076 | Apt 508¦¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17697222577 | Chrome 133.0.0.0 / Windows | 66.168.40.27 | 1322724957 | 42.2555, -71.7719
2025-03-10 09:18 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-10 | 2025-03-06 | 660 Main St. |  | Worcester | MA |  | Apt 408¦¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17697247616 | Chrome 133.0.0.0 / Windows | 66.168.40.27 | 1322726632 | 42.2555, -71.7719
2025-03-10 09:26 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-10 | 2025-03-06 | 660 Main St. |  | Worcester | MA |  | Apt 308¦¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17697287568 | Chrome 133.0.0.0 / Windows | 66.168.40.27 | 1322729159 | 42.2555, -71.7719
2025-03-10 09:28 | Sean | Matthies | 23034 | 1667 Central St. |  | Worcester | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-10 | 2025-03-06 | 660 Main St. |  | Worcester | MA |  | Apt 208¦¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen` | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17697298282 | Chrome 133.0.0.0 / Windows | 66.168.40.27 | 1322729848 | 42.2555, -71.7719
2025-03-10 12:07 | Sean | Griffin | 14425 | 19 Oxbow Road |  | Raynham | MA | 2767 | 7745719815 | Project Manager | sean.griffin@thorndikedevelopment.com | BRN240GF | Breaker | Breaker | 40 | 40 | 2 Pole | Eaton | Residence |  | 2025-03-10 | 2025-01-01 | [5 empty] | Cooktop causes breaker to trip | General Electric | PHP9030DTBB |  | Townhome | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17698297564 | Chrome 133.0.0.0 / Windows | 71.162.115.107 | 1322795039 | 42.5945, -71.3571
2025-03-10 20:14 | Edwin | Perez | 55322 | 233 andover st |  | Lawrence | MA | 1843 | 9783829292 | Electrician | edwinperez2@live.com | Qf250a | Breaker | N/a | 50 |  | 2 Pole | Siemens | Residence |  | 2025-03-10 | 2025-03-10 | 45 kensington ave |  | Methuen | MA | 1844 | Everytime the oven was turn on the breaker trip is a combination gas and electric stove. I remove the jumper that is connected and still it trip the breaker. | Bosh | HDS8055U |  | Single family | Kitchen | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17701176942 | Mobile Safari 18.3 / iOS | 24.61.4.69 | 1322980044 | 42.7117, -71.1663
2025-03-11 15:05 | Gustavo | Simoes | 23674 | 12 welles way |  | Chilmark | MD | 2535 | 7745634988 | Electrician | gsselectricmv@gmail.com | LB120DFT | Breaker | n/a | 20 |  | 1 Pole | Leviton | Residence | https://www.formstack.com/admin/download/file/17704979488 | 2025-03-11 | 2025-03-11 | 12 Smith Ln |  | Chilmark | MA | 2535 | Breaker trips when fridge is running. | Subzero | CL4850UFDID/O | dedicated | Single family Dwelling | Main fridge in the kitchen. | No | No | No | No | https://www.formstack.com/admin/download/file/17704979505 | https://www.formstack.com/admin/download/file/17704979509 | Safari 18.3 / OS X | 71.192.41.53 | 1323229903 | 41.2727, -70.0971
2025-03-12 06:15 | Bethany | Ramsey | 59672 | 70 Manners Ave |  | Brockton | MA | 2301 | 7748267541 | Electrician | bethanyramsey93@gmail.com | LR33607 | Breaker | Bolt in | 20 |  | 1 Pole | Eaton | Commercial | https://www.formstack.com/admin/download/file/17707585986 | 2025-03-11 | 2025-03-11 | 99 High Street |  | Boston | MA | 2110 | 3 GFCI breakers were installed and flipped to ON. Immediately upon plugging in the 3 appliances, breakers tripped. Tried more than once. Unplugged appliances from receptacle and tried again. Breakers remained on. | Fisher & Paykel | RS36A72J1N |  | Tenant Office Space | The room affected is a kitchen/pantry area in a tenant office space. | No | No | Yes | No | https://www.formstack.com/admin/download/file/17707585999 | https://www.formstack.com/admin/download/file/17707586000 | Mobile Safari 18.3 / iOS | 172.56.193.91 | 1323400892 | 42.415, -71.0527
2025-03-12 11:37 | scott | m sullivan | 13830 | 138 hobart st |  | Danvers | MA | 1923 | 7817275756 | electrician | mbfelectriccorp@gmail.com | siemens type QPFB AJ869000H104QG | Breaker | none | 30 |  | 2 Pole | Siemens | Residence |  | 2025-03-12 | 2024-12-10 | 63 ATLANTIC AVE |  | BOSTON | MA | 2113 | Instant trip upon energizing | wolf | induction/electric cooktop | none | condo | kitchen | No | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17708866285 | Chrome 133.0.0.0 / Windows | 174.224.171.231 | 1323490118 | 42.3498, -71.0765
2025-03-12 16:28 | Moises | Docanto | 14127 | 4980 N main st Apt 408 |  | Fall River | MA | 2720 | 617 849-0920 | Owner | info@docantoelectrical.com | Q120DFP | Breaker | AFCI/GFCI Dual Function | 20 |  | 1 Pole | Siemens | Residence |  | 2025-03-10 | 2025-02-28 | 4980 N main st Apt 408 |  | Fall River | MA | 2720 | We had the circuit on a dual function breaker 20 amp soon we turn it on it trip right away once we put it on a regular breaker it stay on. Manufacture recommend to not put it on a gfci breaker. | Brisas By Zephyr | BML-E30BG | No | House | Kitchen | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/17710744060 | Chrome 134.0.0.0 / Windows | 73.17.22.7 | 1323612460 | 42.2934, -71.2356
2025-03-14 08:21 | Michael | white | 12151 | 62 Kings Rd |  | Canton | MA | 2021 | 61789832611 | owner operator | mcwhite825@gmail.com | m2406210668 | Breaker | 2 pole | 50 |  | 2 Pole | Siemens | Residence |  | 2025-02-13 | 2025-01-13 | 16 bonwood rd |  | needham | MA | 2492 | new kitchen remodel ¦New circuit and receptacle provide for Bosch range¦Will not hold on Gfci breaker¦Tried 3 breakers as well as different manufacturers breaker¦Contacted Yale appliance who contacted Bosch ¦They provided a second range ¦Instant tripping still occurs | bosch | his8655u/06 | none | single family home | New induction range is only affected | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17718486080 | Safari 18.3.1 / OS X | 108.20.163.166 | 1324209923 | 42.1648, -71.1379
2025-03-14 11:47 | Sean | Griffin | 14425 | 30 Oxbow Road |  | Raynham | MA | 2767 | 7745719815 | Project Manager | sean.griffin@thorndikedevelopment.com | BRN240GF | Breaker | Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2025-03-14 | 2025-03-14 | 30 Oxbow Road |  | Raynham | MA | 2767 | Stove causes breaker to trip | General Electric | GRF500PVSS | None | Townhome | Stove causes breaker to trip | No | No | No | No |  | https://www.formstack.com/admin/download/file/17719500119 | Chrome 134.0.0.0 / Windows | 71.162.115.107 | 1324283665 | 42.2878, -71.3587
2025-03-16 17:24 | Robert | Gilbert | 11895 | 40 vineyard meadows farm rd |  | Vineyard haven | MA | 2568 | 5079220426 | Electrician | electricianrobgilbert@gmail.com | Qo | Breaker | 2 pole 50 amp | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-03-14 | 2025-03-14 | [5 empty] | Induction cook top immediately trips circuit when turned on | Meile | 7730 fr | None | Single family dwelling | Kitchen induction cook top ( meile) | No | No | No | No |  | https://www.formstack.com/admin/download/file/17726021381 | Mobile Safari 18.3 / iOS | 73.249.250.227 | 1324762216 | 42.724, -71.479
2025-03-17 08:49 | Adilson | De Aguiar | 51188 | 168 fuller street |  | Everett | MA | 2149 | 7817065265 | Owner | adilsonelectric@hotmail.com | 0091212 E82617 | Breaker | QPF | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17727979542 | 2025-03-06 | 2025-03-06 | 11 powder house |  | Medford | MA |  | The GFCI breaker tripped soon as plug the power cord. The neutral wire and grounded wire wasn't bonded together.¦ | Miele | HR 1421-3 E | No | Single family | Kitchen | No | Yes | Yes | No | https://www.formstack.com/admin/download/file/17727979556 | https://www.formstack.com/admin/download/file/17727979557 | Chrome 134.0.0.0 / Linux | 209.6.210.135 | 1324899988 | 42.4125, -71.0034
2025-03-17 18:48 | ryan | pigott | 56365 | 32 syracuse road |  | nashua | NH | 3064 | 7815074390 | owner | rpelectrical22@gmail.com | Q120DFN | Breaker | 20 amp dual function | 20 |  | 1 Pole | Siemens | Residence |  | 2025-03-06 | 2025-01-21 | 8 ruben duran way |  | bedford | MA | 1730 | installed dual function breaker on a dedicated 20 amp feed. when fridge compressor kicks it trips the breaker. moved fridge to plugged into counter circuit and as well tripped the dual function supplying counter power. | fisher and paykel | RF201AHUSX1_FPSC | NONE | SINGLE FAMILY HOME | fridge only | No | No | No | No |  | https://www.formstack.com/admin/download/file/17731555635 | Safari 15.6.1 / OS X | 76.24.76.97 | 1325134185 | 42.7746, -71.5142
2025-03-18 08:04 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-17 | 2025-03-14 | 660 Main St. |  | Worcester | MA |  | Apt 606¦Oven portion cannot be used without tripping breaker.¦Have contacted GE before and they have stated it is a¦known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17733419846 | Chrome 133.0.0.0 / Windows | 66.189.80.15 | 1325254728 | 42.2555, -71.7719
2025-03-18 08:22 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-17 | 2025-03-14 | 660 Main St. |  | Worcester | MA |  | Apt 506¦Oven portion cannot be used without tripping breaker.¦Have contacted GE before and they have stated it is a¦known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | NA | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17733489285 | Chrome 133.0.0.0 / Windows | 66.189.80.15 | 1325258970 | 42.2555, -71.7719
2025-03-18 08:26 | Sean | Matthies | 23034 | 1667 Central St |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-17 | 2025-03-14 | 660 Main St. |  | Worcester | MA |  | Apt 406¦Oven portion cannot be used without tripping breaker.¦Have contacted GE before and they have stated it is a¦known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17733506740 | Chrome 133.0.0.0 / Windows | 66.189.80.15 | 1325260081 | 42.2555, -71.7719
2025-03-18 08:41 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-17 | 2025-03-14 | 660 Main St. |  | Worcester | MA |  | Apt 306¦Oven portion cannot be used without tripping breaker.¦Have contacted GE before and they have stated it is a¦known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | NA | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17733566627 | Chrome 133.0.0.0 / Windows | 66.189.80.15 | 1325264075 | 42.2555, -71.7719
2025-03-18 08:46 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-17 | 2025-03-14 | 660 Main St. |  | Worcester | MA |  | Apt 206¦Oven portion cannot be used without tripping breaker.¦Have contacted GE before and they have stated it is a¦known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17733583451 | Chrome 133.0.0.0 / Windows | 66.189.80.15 | 1325265167 | 42.2555, -71.7719
2025-03-18 09:11 | Peter | Prus | 51711 | 8 Tulip Circle |  | South Grafton | ME | 1560 | 5082595679 | Electrician | peter.prus@forgeco.com | LB120-DFT | Breaker | None | 20 | None | 1 Pole | Leviton | Residence |  | 2025-01-03 | 2025-01-29 | 92 Oxbow Rd |  | Wayland | MA | 1778 | Random Nuisance Tripping from Refrigerator | GE | GFE26JYMFS |  | Single Family Residential | Kitchen appliance causing a nuisance trip at breaker | Yes | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/17733697807 | Chrome 134.0.0.0 / OS X | 173.48.175.14 | 1325272708 | 42.2441, -71.1688
2025-03-18 12:11 | James | Loughlin | 17387 | PO BOX 72, |  | Franklin | MA | 2038 | 5085280765 | Owner | sales@loughlinelectric.com | Square d Homeline HOM250GFI | Breaker | Homeline GFCI | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-03-12 | 2025-03-12 | 8 Wyllie Road |  | Franklin | MA | 2038 | Oven is on for 10-15 minutes then it trips, but not every day. The appliance vendor requested homeowner to remove the gfci breaker | Kitchen Aid | KFEG500ESS | no | Residential | Electric range in the kitchen | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17734886516 | https://www.formstack.com/admin/download/file/17734886517 | Chrome 134.0.0.0 / Windows | 98.118.109.186 | 1325360568 | 42.0622, -71.3412
2025-03-19 16:42 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 9783376541 | Contractor | castlecp@hotmail.com | Q120dfn | Breaker | Breaker | 20 |  | 1 Pole | Siemens | Residence |  | 2024-03-17 | 2024-03-17 | 6 Musket Dr. |  | Acton | MA | 1720 | Installed a new 20 amp dual function breaker, for a new microwave. It continually trips. | Thermador | MD24WS/04 |  | Single family | Kitchen. | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17742536551 | Chrome 132.0.0.0 / Windows | 38.242.7.253 | 1325888416 | 42.3574, -71.0618
2025-03-19 16:59 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 9783376541 | Contractor | castlecp@hotmail.com | QF 230GFN | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2024-03-17 | 2024-03-17 | 6 Musket Dr. |  | Acton | MA | 1720 | Installed a new 30 amp gfci breaker on a new dryer. It continually trips. | Electrolux | ELE7537AW |  | Single family | Laundry Room. | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17742633408 | Chrome 132.0.0.0 / Windows | 38.242.7.253 | 1325895079 | 42.3574, -71.0618
2025-03-19 17:33 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor | castlecp@hotmail.com | QF 230GFN | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2025-03-17 | 2025-03-17 | 6 Musket Dr. |  | Acton | MA | 1720 | Installed a new 30 amp GFCI breaker on a new dryer. It continuously trips. | Electrolux | ELE7537AW | None | Single Family | Laundry Room. | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17742811767 | Chrome 134.0.0.0 / Windows | 98.118.86.140 | 1325907666 | 42.3491, -71.5431
2025-03-19 18:18 | Philip | Mendonca | 10757 | 6R Mount Vernon St. |  | Arlington | MA | 2476 | 6178885434 | Electrician | philipselectric@gmail.com | Siemens QPF 50-amp 2-Pole Gfci Circuit Breaker | Breaker | Siemens QPF 50-amp 2-Pole Gfci Circuit Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2025-03-11 | 2023-02-18 | 6R Mount Vernon St. |  |  |  |  | Tripping circut breaker on stove warm up period | Frigidaire | gcre302laff |  | kitchen stove | kitchen stove | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17743019628 | Chrome 134.0.0.0 / Windows | 146.115.72.91 | 1325922665 | 42.4188, -71.1557
2025-03-21 10:02 | Cole | Powers | 36860 | 26 SHURTLEFFS WAY |  | Edgartown | MA | 2539 | 5086966400 ext 101 | President/Master Electrician | powerselectric@comcast.net | SQD QO230GFI | Breaker | Plug On | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-24 | 2024-07-20 | [5 empty] | Qualified Technician landed 8/3 Romex on 30amp 2-pole GFCI breaker. Upon circuit being energized, the breaker would trip instantly. Technician proceeded to systematically test for continuity between neutral and ground on the range appliance and the wires from the panel. No issues found with wiring. | Thermador | PO301W/04 | N/A | Residential House | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17750464421 | https://www.formstack.com/admin/download/file/17750464422 | Chrome 134.0.0.0 / Windows | 76.152.41.177 | 1326449001 | 42.7746, -71.5142
2025-03-21 10:03 | Cole | Powers | 36860 | 26 SHURTLEFFS WAY |  | Edgartown | MA | 2539 | 5086966400 ext 101 | President/Master Electrician | powerselectric@comcast.net | SQD QO230GFI | Breaker | Plug On | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2024-07-24 | 2024-07-20 | [5 empty] | Qualified Technician landed 8/3 Romex on 30amp 2-pole GFCI breaker. Upon circuit being energized, the breaker would trip instantly. Technician proceeded to systematically test for continuity between neutral and ground on the range appliance and the wires from the panel. No issues found with wiring. | Thermador | PO301W/04 | N/A | Residential House | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17750467262 | https://www.formstack.com/admin/download/file/17750467263 | Chrome 134.0.0.0 / Windows | 76.152.41.177 | 1326449230 | 42.7746, -71.5142
2025-03-23 12:35 | gregory | comeau | 16659 | 2 Avery Street |  | Wilmington | MA | 1887 | 6178390191 | Master Electrician | comeauelectric@yahoo.com | Siemens. Q230GF | Breaker | none | 30 |  | 2 Pole | Siemens | Residence |  | 2025-03-20 | 2025-03-20 |  |  | Belmont | MA | 2478 | The GFI breaker trips instantly when turned on.¦We tried a second breaker with the same results. | LG | DLE3400W | nothing | single family home | laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/17756634638 | Chrome 116.0.0.0 / OS X | 73.219.246.83 | 1326908646 | 42.6351, -71.3014
2025-03-24 14:49 | YOVANI | HERNANDEZ | 12931 | 29 AGATHA st |  | revere | MA | 2151 | 6172307537 | electrician | yovaelectrician@gmail.com | chs950p2m6s1 | Breaker | stove | 50 |  | 2 Pole | Siemens | Residence |  | 2024-12-18 | 2024-12-17 | 32 walnut hill rd |  | brookline | MA | 2467 | everytime the stove turns on it will trip the ground fault breaker in the panel. the instructions mention that the stove doesn't require a ground fault breaker . | cafe | chs950p2m6s1 | no | kitchen stove | kitchen stove | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17761245922 | Chrome 134.0.0.0 / Windows | 172.56.193.100 | 1327233460 | 42.364, -71.0265
2025-03-25 08:29 | Jake | Carlan | 1971 | 895 Salem St | Unit 2A | Groveland | MA | 1834 | 9783731393 | Electrician | office@danielsel.com | L2106082479 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2025-03-21 | 2025-03-21 | 54 brook st |  | Haverhill | MA | 1832 | Breaker trips when oven preheats. | Semiens | Jb25DM2bb |  | Apartment | Kitchen Stove | No | No | No | No |  |  | Chrome 133.0.0.0 / Windows | 50.187.12.233 | 1327457746 | 42.3725, -71.1814
2025-03-25 09:38 | Tyler | Daniels | 1971 | 895 Salem St | Unit 2A | Groveland | MA | 1834 | 9783731393 | Electrician | office@danielsel.com | BRN250GF | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2025-03-06 | 2025-03-06 | 24 Follinsbee Lane |  | West Newbury | MA | 1985 | Breaker trips when oven us not running and trips when oven is running separately. | Electrolux | FCFI3083ASC |  | Single Family | Kitchen | No | No | No | Yes |  |  | Chrome 133.0.0.0 / Windows | 50.187.12.233 | 1327477137 | 42.3725, -71.1814
2025-03-25 09:38 | Carl | Perkins | 11876 | 79 Cooley St |  | Agawam | MA | 1001 | 4132043063 | Electrician Service | no72gto@Yahoo.com | Hom 250 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17764802003 | 2025-03-20 | 2025-03-11 | 181 silver street |  | Greenfield | MA | 1301 | GFI trips when oven and burner are on together. | Samsung | NE63A6711SS/AA | None | Dwelling | Only the stove. | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17764802017 | Mobile Safari 18.2 / iOS | 174.192.9.255 | 1327477203 | 41.7958, -72.5241
2025-03-25 16:23 | Richard | Clapp | 8026 | 534 Shunpike Rd |  | Sheffield | MA | 1257 | 4134414468 | Electrician | rac1945@gmail.com | ITE | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2025-03-25 | 2025-03-25 | Rt7 |  | Sheffield | MA | 1257 | Trips when plugged in | Admiral | ADE7005AYW |  | Laundry Rm | Laundry Rm | No | No | No | No |  | https://www.formstack.com/admin/download/file/17767329611 | Safari 17.10 / OS X | 24.194.7.213 | 1327645503 | 42.1927, -73.3606
2025-03-26 10:03 | All-Phase Electrical | John Jordan | 11566 | 811 Washington Street | Suite #5 | Pembroke | ME | 2359 | 781-826-5300 | Owner | Johnjordan@al-phaseelectrical.com | General Electric/THQL2150GFT2 THQL | Breaker | NA | 50 |  | 2 Pole | ABB | Residence |  | 2025-02-03 | 2025-02-03 | [5 empty] | Tripping occurs when breaker is turned on | CAFE | CTD70DP2N4S1 |  | Single Family Home | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17776195184 | https://www.formstack.com/admin/download/file/17776195189 | Chrome 132.0.0.0 / Windows | 151.203.74.221 | 1328182832 | 42.1194, -70.8611
2025-03-26 14:46 | Dennis | Grillo | 18229 | 305 Union St |  | Franklin | MA | 2038 | 5089898706 | Owner | grilloelectricinc@gmail.com | GFTCB250 | Breaker | Eaton | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17779677501 | 2025-03-26 | 2025-03-26 | 5 Royal Heights Dr |  | Medway | MA | 2053 | Breaker refuses to engage at initial operation. Continuous tripping. | Wolf Appliance | DO3050PE/S/P |  | Kitchen | Double oven in kitchen. | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17779677517 | https://www.formstack.com/admin/download/file/17779677523 | Chrome 134.0.0.0 / Windows | 73.126.176.80 | 1328409294 | 42.0834, -71.3967
2025-03-27 11:39 | Eric | Conrad | 40723 | 23 Buttonwoods Ave |  | Haverhill | MA | 1830 | 781-844-8676 | Electrician | conradelectric23@gmail.com | Siemans Q115DFP | Breaker | dual function | 15 |  | 1 Pole | Siemens | Residence |  | 2023-03-01 | 2023-03-01 | 27 Govenors Rd |  | Groveland | MA | 1834 | constant tripping of refrigerator | KitchenAid | KRFC704fps06 |  | House | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17784383590 | Safari 17.6 / OS X | 73.60.203.178 | 1328730099 | 42.6283, -71.3311
2025-03-27 16:10 | Randy | Alves | 8999 | 116 Hopping Brook Rd |  | Holliston | MA | 1746 | 508-306-5254 | Assistant Project Manager | ralves@wjgei.com | Square D QOB220 | Breaker | N/A | 20 |  | 2 Pole | Schneider Electric | Commercial |  | 2024-09-02 | 2024-08-15 | Walpole Middle School - 625 Washinston St |  | Walpole | MA | 2032 | Ware-washers repeatedly causes GFCI breaker to trip (Typical of 6 locations all same breaker type all same equipment model) | LABCONO Corp | 402001010 |  | School | Science Classroom | No | No | No | No |  | https://www.formstack.com/admin/download/file/17786196276 | Chrome 134.0.0.0 / Windows | 50.170.64.26 | 1328857339 | 42.3611, -71.0518
2025-03-27 16:13 | Randy | Alves | 8999 | 116 Hopping Brook Rd |  | Holliston | MA | 1746 | 5083065254 | Assistant Project Manager | ralves@wjgei.com | Sq D QOB220 | Breaker | NA | 20 |  | 2 Pole | Schneider Electric | Commercial |  | 2024-09-02 | 2024-08-15 | Walpole Middle School - 625 Washinston St |  | Walpole | MA | 2032 | Cooktops in classrooms repeatedly cause GFCI breakers to trip (Typical of 2 locations all same breaker all same cooktop models) | GE Appliances | PHP9030S71SS |  | School | Special Education Classrooms | No | No | No | No |  | https://www.formstack.com/admin/download/file/17786216656 | Chrome 134.0.0.0 / Windows | 50.170.64.26 | 1328858736 | 42.3611, -71.0518
2025-03-27 16:14 | Eric | Caldon | 21306 | 100 Deanville Rd |  | Attleboro | MA | 2703 | 7742296409 | owner | Ecaldonmidstate@gmail.com | Cutler Hammer BR | Breaker | n/a | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17786218576 | 2025-03-20 | 2025-03-20 | 33 Sherborn Ave |  | Ashland | MA |  | Just installed a new breaker for client | Wolf | 1G15/S |  | Kitchen | Installed a new wolf grill top in kitchen, and range will not turn on immediately | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17786218589 | Chrome 134.0.0.0 / Windows | 96.230.233.54 | 1328858877 | 42.1398, -71.5162
2025-03-27 16:18 | Eric | Caldon | 21306 | 100 Deanville Rd |  | Attleboro | MA | 2703 | 7742296409 | owner | Ecaldonmidstate@gmail.com | Cutler Hammer | Breaker | n/a | 50 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17786246774 | 2025-03-20 | 2025-03-20 | 33 Sherborn Ave |  | ashland | MA |  | microwave oven will not immediately turn on | Bosch | HMC80242UC/07 | none | kitchen | Will not turn on instantly | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17786246788 | Chrome 134.0.0.0 / Windows | 96.230.233.54 | 1328860766 | 42.1398, -71.5162
2025-03-28 14:20 | paul | magalhes | 16722 | 10 CONDUIT ST |  | Acushnet | MA | 2743 | 5089953826 | vice president | paul@mvelectrical.net | eaton | Breaker | none | 40 |  | 2 Pole | Eaton | Residence |  | 2025-01-07 | 2024-12-01 | 10 oak st |  | plymouth | MA | 2360 | breaker trips when appliance is in use | frididaire | FFEC3025UB |  | Apt. unit C | Kitchen | Yes | Yes | No | No |  | https://www.formstack.com/admin/download/file/17792186070 | Chrome 134.0.0.0 / Windows | 96.95.174.113 | 1329322912 | 42.5334, -70.9653
2025-03-28 14:38 | paul | magalhes | 16722 | 10 CONDUIT ST |  | Acushnet | MA | 2743 | 5089953826 | vice president | paul@mvelectrical.net | eaton GFTCB220 | Breaker | NONE | 20 |  | 2 Pole | Eaton | Residence |  | 2025-01-07 | 2024-12-01 | 10 oak st |  | plymouth | MA | 2360 | BREAKER TRIPS WHEN APPLIANCE IS IN USE | GE | JKS3000/SN |  | APT. UNIT C | KITCHEN | Yes | Yes | No | No |  | https://www.formstack.com/admin/download/file/17792305780 | Chrome 134.0.0.0 / Windows | 96.95.174.113 | 1329330124 | 42.5334, -70.9653
2025-03-28 14:51 | paul | magalhes | 16722 | 10 CONDUIT ST |  | Acushnet | MA | 2743 | 5089953826 | VICE PRESIDENT | paul@mvelectrical.net | GFTCB250 | Breaker | NONE | 50 |  | 2 Pole | Eaton | Residence |  | 2025-01-07 | 2024-12-01 | 10 oak st |  | plymouth | MA | 2360 | BREAKER TRIPS WHEN APPLIANCE IN USE | HOTPOINT | RAS240DMWW |  | APT. UNIT A | KITCHEN | Yes | Yes | No | No |  | https://www.formstack.com/admin/download/file/17792387488 | Chrome 134.0.0.0 / Windows | 96.95.174.113 | 1329335378 | 42.5334, -70.9653
2025-03-28 14:59 | paul | magalhes | 16722 | 10 CONDUIT ST |  | Acushnet | MA | 2743 | 5089953826 | vice president | paul@mvelectrical.net | GFTCB250 | Breaker | NONE | 50 |  | 2 Pole | Eaton | Residence |  | 2025-01-07 | 2024-12-01 | 10 oak st |  | plymouth | MA | 2360 | BREAKER TRIPS WHEN APPLIANCE IN USE | HOTPOINT | RAS240DMWW |  | APT. UNIT B | KITCHEN | Yes | Yes | No | No |  | https://www.formstack.com/admin/download/file/17792447358 | Chrome 134.0.0.0 / Windows | 96.95.174.113 | 1329339091 | 42.5334, -70.9653
2025-03-28 16:17 | Jake | Carlan | 1971 | 895 Salem St | Unit 2A | Groveland | MA | 1834 | 9783731393 | Electrician | office@danielsel.com | m2412090142 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2025-03-25 | 2025-03-25 | 500 Broadway |  | Malden | MA | 2148 | Breaker trips when turning on oven/stove | G.E | JBs160DM5WW |  | Apartment | Kitchen | No | No | No | No |  |  | Chrome 133.0.0.0 / Windows | 50.187.12.233 | 1329368805 | 42.3725, -71.1814
2025-03-28 16:26 | Jake | Carlan | 1971 | 895 Salem St | Unit 2A | Groveland | MA | 1834 | 9783731393 | electrician | office@danielsel.com | L2208040009 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2025-03-26 | 2025-03-26 | 23 victor street |  | Haverhill | MA | 1832 | breaker trips when oven is on | GE | JB256DM4BB |  | Apartment | Kitchen | No | No | No | No |  |  | Chrome 133.0.0.0 / Windows | 50.187.12.233 | 1329371932 | 42.3725, -71.1814
2025-03-28 16:30 | Jake | Carlan | 1971 | 895 Salem St | Unit 2A | Groveland | MA | 1834 | 9783731393 | electrician | office@danielsel.com | L2305020020 | Breaker | breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2025-03-26 | 2025-03-26 | 23 victor street unit 22 |  | Haverhill | MA | 1832 | breaker trips when oven is on. | GE | JB258DMSBB |  | Apartment | Kitchen | No | No | No | No |  |  | Chrome 133.0.0.0 / Windows | 50.187.12.233 | 1329373491 | 42.3725, -71.1814
2025-03-28 16:40 | Patrick | Walsh | 22263 | 16r Jonspin Road |  | Wilmington MA 0188 | MA | 1887 | 6175153494 | VP | pwalsh@capelectric.net | Siemens QF250 | Breaker | stab in | 50 |  | 2 Pole | Siemens | Residence |  | 2025-03-10 | 2025-02-18 | 298 Commercial St |  | Braintree | MA | 2184 | Oven would trip frequently even after trying the ""burn off method"" | GE | JB645DK |  | Kitchen | kitchen stove | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17793018670 | Chrome 134.0.0.0 / Windows | 108.49.107.124 | 1329376726 | 42.5575, -71.1736
2025-03-28 17:42 | Michael | Young | 3657 | 105 pleasant st |  | North Andover | MA | 1845 | 6176991363 | Electrician | youngelectric@gmail.com | qf250a 50 | Breaker | Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2025-03-28 | 2025-03-28 | 100 Grant st |  | Lexington | MA | 2420 | The equipment doesn't work with GFCI breaker | Fisher & Paykel | C1365dtb2 |  | Residencial | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17793303928 | Mobile Safari 18.3.1 / iOS | 67.189.196.13 | 1329396319 | 42.4188, -71.1557
2025-04-01 08:10 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-03-31 | 2025-03-27 | 660 Main St. |  | Worcester | MA |  | Apt 610¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17807118078 | Chrome 134.0.0.0 / Windows | 66.189.80.15 | 1330434443 | 42.2555, -71.7719
2025-04-01 08:18 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-31 | 2025-03-27 | 660 Main St. |  | Worcester | MA |  | Apt 510¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17807150459 | Chrome 134.0.0.0 / Windows | 66.189.80.15 | 1330436897 | 42.2555, -71.7719
2025-04-01 08:24 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | hom240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-31 | 2025-03-27 | 660 Main St. |  | Worcester | MA |  | Apt 410¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17807173368 | Chrome 134.0.0.0 / Windows | 66.189.80.15 | 1330438660 | 42.2555, -71.7719
2025-04-01 08:33 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-31 | 2025-03-27 | 660 Main St. |  | Worcester | MA |  | Apt 310¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | NA | Apartment | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17807210855 | Chrome 134.0.0.0 / Windows | 66.189.80.15 | 1330441539 | 42.2555, -71.7719
2025-04-01 08:38 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-03-31 | 2025-03-27 | 660 Main St. |  | Worcester | MA |  | Apt 210¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | NA | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17807232063 | Chrome 134.0.0.0 / Windows | 66.189.80.15 | 1330443164 | 42.2555, -71.7719
2025-04-01 10:53 | Matt | Doremus | 21923 | 244 Cedar St |  | Somerville | MA | 2145 | 7817386180 | Electrician | matt@symmetry-electric.com | Eaton | Breaker | BRN230GF | 30 |  | 2 Pole | Eaton | Residence |  | 2025-03-24 | 2025-03-10 | 47 Grafton St |  | Newton | MA | 2459 | Oven trips immediately when bake feature is turned on | Thermador | MED301WS |  | Home | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17807997801 | Chrome 134.0.0.0 / OS X | 73.126.4.46 | 1330501484 | 42.3253, -71.0951
2025-04-01 11:35 | Philippe | Thibeault | 50440 | 10076 horizion dr |  | Spring hill | FL | 34608 | 97881560000 | Owner | cmkillion@yahoo.com | Square d | Breaker | Stove | 50 |  | 2 Pole | Legrand | Residence |  | 2025-04-01 | 2025-04-01 | 67 elliot dr |  | Dracut | MA |  | Stove will not hold in gfi | Ge | 50 amp stove |  | House | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17808298271 | Mobile Safari 17.6 / iOS | 107.122.105.84 | 1330524304 | 39.8079, -86.0949
2025-04-01 13:24 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | OWNER/VP | JOHN@HENRYSELECTRICINC.COM | SQUARE D / Q240 | Breaker | N/A |  |  | 2 Pole | Schneider Electric | Residence |  | 2025-03-21 | 2020-05-31 | 495 LAURAL STREET |  | LEE | MA | 1238 | BREAKER DOES NOT HOLD, KEPT TRIPPING. | FRIGIDAIRE | FFEF3054TW |  | SINGLE FAMILY | KITCHEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/17809120379 | Chrome 134.0.0.0 / Windows | 184.74.9.210 | 1330589901 | 42.3006, -73.2376
2025-04-01 13:47 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | OWNER/VP | JOHN@HENRYSELECTRICINC.COM | B250 | Breaker | N/A |  |  | 2 Pole | Eaton | Residence |  | 2025-03-25 | 2025-02-18 | 200 LAUREL STREET, APT 13 |  | LEE | MA | 1238 | BREAKER DOES NOT HOLD, KEPT TRIPPING. | FRIGIDAIRE | FCFE2425AS |  | APARTMENT | KITCHEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/17809268700 | Chrome 134.0.0.0 / Windows | 184.74.9.210 | 1330600872 | 42.3006, -73.2376
2025-04-01 13:55 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | OWNER/VP | JOHN@HENRYSELECTRICINC.COM | B250 | Breaker | N/A |  |  | 2 Pole | Eaton | Residence |  | 2025-03-25 | 2025-01-27 | 200 LAUREL STREET, APT 15 |  | Lee | MA | 1238 | BREAKER DOES NOT HOLD, KEPT TRIPPING. | FRIGIDAIRE | FCFE2425AS |  | APARTMENT | KITCHEN | No | No | No | No |  | https://www.formstack.com/admin/download/file/17809327319 | Chrome 134.0.0.0 / Windows | 184.74.9.210 | 1330605111 | 42.3006, -73.2376
2025-04-02 09:15 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-04-02 | 2025-04-01 | 660 Main St. |  | Worcester | MA |  | Apt 612¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17813226467 | Chrome 134.0.0.0 / Windows | 66.189.80.15 | 1330902790 | 42.2555, -71.7719
2025-04-02 09:20 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-04-02 | 2025-04-01 | 660 Main St. |  | Worcester | MA |  | Apt 512¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | NA | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17813249580 | Chrome 134.0.0.0 / Windows | 66.189.80.15 | 1330904620 | 42.2555, -71.7719
2025-04-02 09:29 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-04-02 | 2025-04-01 | 660 Main St. |  | Worcester | MA |  | Apt 412¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17813295251 | Chrome 134.0.0.0 / Windows | 66.189.80.15 | 1330908189 | 42.2555, -71.7719
2025-04-02 09:32 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-04-02 | 2025-04-01 | 660 Main St. |  | Worcester | MA |  | Apt 312¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17813310091 | Chrome 134.0.0.0 / Windows | 66.189.80.15 | 1330909332 | 42.2555, -71.7719
2025-04-02 12:00 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-04-02 | 2025-04-01 | 660 Main St. |  | Worcester | MA |  | Apt 212¦¦Oven portion cannot be used without tripping breaker. Have¦contacted GE¦before and they have stated it is a known issue with their stoves¦and they¦cannot fix it. | GE | HOm240GFIC | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17814198795 | Chrome 134.0.0.0 / Windows | 66.189.80.15 | 1330974985 | 42.2555, -71.7719
2025-04-02 12:09 | Sean | Griffin | 14425 | 8 Pleasant Street Suite A2 |  | Natick | MA | 1760 | 7745719815 | Project Manager | sean.griffin@thorndikedevelopment.com | BRN240GF | Breaker | Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2025-04-02 | 2025-04-02 | 39 Oxbow Road |  | Raynham | MA | 2767 | stove trips breaker | General Electric | PB935YPFS |  | Townhome | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17814258951 | Chrome 134.0.0.0 / Windows | 71.162.115.107 | 1330979486 | 42.5945, -71.3571
2025-04-02 12:13 | Sean | Griffin | 14425 | 8 Pleasant Street Suite A2 |  | Natick | MA | 1760 | 7745719815 | Project Manager | sean.griffin@thorndikedevelopment.com | BRN240GF | Breaker | Breaker | 40 | 40 | 2 Pole | Eaton | Residence |  | 2025-04-02 | 2025-04-02 | 35 Oxbow Road |  | Raynham | MA | 2767 | stove trips breaker | General Electric | CHS900P2MS1 |  | Townhome | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17814283738 | Chrome 134.0.0.0 / Windows | 71.162.115.107 | 1330981363 | 42.5945, -71.3571
2025-04-02 13:43 | Steven | Marchand | 586386 | 72 Rolfe Avenue |  | Shrewsbury, MA | MA | 1545 | 5085606344 | electrician | s.marchand86@yahoo.com | BRN250GFCS | Breaker | plug on circuit breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2025-03-31 | 2025-03-31 | 226 May st |  | Needham | MA | 2492 | trips when appliance isnt in use and also while being used. Appliance works for a little bit 10 maybe 15 mins and trips. | Thernador | CIT365YB 3-5 |  | Single family | JUst isolated to cook top appliance | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17814884798 | Chrome 134.0.0.0 / Windows | 216.195.10.36 | 1331025631 | 42.2831, -71.7237
2025-04-07 05:46 | Christopher | Mulcahy | 54993 | 130 Richmond Ave |  | Worcester | MA | 1602 | 774-272-3497 | Electrician | cmulcahy@mulcahy-electrical.com | Square D HOM250GFIC | Breaker | Square D | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-04-03 | 2025-04-03 | [5 empty] | The circuit works properly with the stovetop for at least a minute but the GFCI function will trip after the oven is on for more than a minute. | Frigidaire | GCFI30608FC |  | Single Family Dwelling | Kitchen Range | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/17839286697 | Mobile Safari 18.3.1 / iOS | 174.196.195.220 | 1332584904 | 42.3364, -71.0326
2025-04-08 09:47 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Assistant Project Manager | paul@cesinc.biz | 2212080772 | Breaker | n/a | 20 |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2025-12-22 | 124 Elm Street |  | Cohasset | MA | 2025 | Refrigerator breaker keeps tripping | Thermodor | 22400000000000000 |  | Condo | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17845912078 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333026380 | 41.7465, -70.5914
2025-04-08 09:53 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Assistant Project Manager | paul@cesinc.biz | H2212140510 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 124 Elm Street |  | Cohasset | MA | 2025 | Unit-305 ¦¦Refrigerator breaker keeps tripping | Thermodor | 2.23e+17 |  | Condo | Unit-305 Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17845943490 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333028458 | 41.7465, -70.5914
2025-04-08 09:57 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | 2212080781 | Breaker | N/A | 20 |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 124 Elm Street |  | Cohasset | MA | 2025 | Unit-208 ¦Refrigerator breaker keeps tripping | Thermodor | 2.24e+17 |  | Condo | Unit-208¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17845970628 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333030267 | 41.7465, -70.5914
2025-04-08 10:02 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | J2212080844 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 124 Elm Street |  | Cohasset | MA | 2025 | Unit-204 ¦Refrigerator breaker keeps tripping | Thermodor | 22300000000000000 |  | Condo | Unit-204¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17845996852 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333032062 | 41.7465, -70.5914
2025-04-08 10:17 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | N2212160106 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 124 Elm Street |  | Cohasset | MA | 2025 | Unit-307 ¦Refrigerator breaker keeps tripping | Thermodor | 2.23e+17 |  | Condo | Unit-307¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17846084960 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333038250 | 41.7465, -70.5914
2025-04-08 10:22 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | Q2212150555 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 124 Elm Street |  | Cohasset | MA | 2025 | Unit-306¦Kitchen Breaker keeps tripping | Thermodor | 2.23e+17 |  | Condo | Unit-306 | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17846107735 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333039836 | 41.7465, -70.5914
2025-04-08 10:36 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | N2212010803 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 124 Elm Street |  | Cohasset | MA | 2025 | Unit-201¦Refrigerator breaker keeps tripping | Thermodor | 2.24e+17 |  | Condo | Unit-201¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17846319141 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333045881 | 41.7465, -70.5914
2025-04-08 11:02 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | J2212150681 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 124 Elm Street |  | Cohasset | MA | 2025 | Unit-202¦Refrigerator Breaker keeps tripping | Thermodor | 2.23e+17 |  | Condo | Unit-202¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17846662621 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333056349 | 41.7465, -70.5914
2025-04-08 11:10 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | T2212010557 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 124 Elm Street |  | Cohasset | MA | 2025 | Unit-313 ¦Refrigerator Breaker keeps tripping | Thermodor | 2.23e+17 |  | Condo | Unit-313¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17846834513 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333060218 | 41.7465, -70.5914
2025-04-08 11:29 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | Q2212081126 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 124 Elm Street |  | Cohasset | MA | 2025 | Unit-312¦Refrigerator Breaker keeps tripping | Thermodor | 2.23e+17 |  | Condo | Unit-312¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17846962368 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333067929 | 41.7465, -70.5914
2025-04-08 11:35 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | R2212080776 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 124 Elm Street |  | Cohasset | MA | 2025 | Unit-211¦Refrigerator Breaker keeps tripping | Thermodor | 2.23e+17 |  | Condo/Kitchen | Unit-211¦Refrigerator Breaker keeps on tripping | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17846997593 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333070319 | 41.7465, -70.5914
2025-04-08 11:47 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | R2212080645 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-03-19 | 124 Elm Street |  | Cohasset | MA | 2025 | Unit-210¦Refrigerator Breaker keeps tripping | Thermodor | 2.23e+17 |  | Condo/Kitchen | Unit-210¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17847077328 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333075511 | 41.7465, -70.5914
2025-04-08 11:52 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | T2212010744 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 87 Elm Street |  | Cohasset | MA | 2025 | Unit-214¦Refrigerator Breaker keeps tripping | Thermodor | 2.23e+17 |  | Condo/Kitchen | Unit-214¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17847109268 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333077632 | 41.7465, -70.5914
2025-04-08 11:59 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | T2212081129 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 87 Elm Street |  | Cohasset | MA | 2025 | Unit-215¦Refrigerator Breaker keeps tripping | Thermodor | 2.23e+17 |  | Condo/Kitchen | Unit-215¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17847154837 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333080701 | 41.7465, -70.5914
2025-04-08 12:04 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | R2212080646 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 87 Elm Street |  | Cohasset | MA | 2025 | Unit-216¦Refrigerator Breaker keeps on tripping | Thermodor | 2.23e+17 |  | Condo/Kitchen | Unit-216¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17847187712 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333082926 | 41.7465, -70.5914
2025-04-08 12:34 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | P2210210261 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 87 Elm Street |  | Cohasset | MA | 2025 | Unit-217¦Refrigerator Breaker keeps on tripping | Thermodor | 2.23e+17 |  | Condo/Kitchen | Unit-217¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17847371879 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333095446 | 41.7465, -70.5914
2025-04-08 12:43 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | J2212010731 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 87 Elm Street |  | Cohasset | MA | 2025 | Unit-319¦Refrigerator Breaker keeps on tripping | Thermodor | 2.23e+17 |  | Condo/Kitchen | Unit-319¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17847429872 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333099330 | 41.7465, -70.5914
2025-04-08 13:15 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 58-388-6169 | Project Manager | paul@cesinc.biz | 2212080811 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 87 Elm Street |  | Cohasset | MA | 2025 | Unit-320¦Refrigerator Breaker keeps tripping circuit | Thermodor | 2.23e+17 |  | Condo/Kitchen | Unit-320¦kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17847626374 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333113069 | 41.7465, -70.5914
2025-04-08 13:21 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | K2210211388 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-09 | 2024-12-22 | 87 Elm Street |  | Cohasset | MA | 2025 | Unit-321¦Kitchen Breaker keeps tripping circuit | Thermodor | 2.23e+17 |  | Condo/Kitchen | Unit-321¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17847656171 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333115238 | 41.7465, -70.5914
2025-04-08 13:27 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | H2212150223 | Breaker | N/A |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 87 Elm Street |  | Cohasset | MA | 2025 | Unit-318¦Refrigerator Breaker keeps tripping circuit | Thermodor | 2.23e+17 |  | Condo/kitchen | Unit-318¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17847693692 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333117836 | 41.7465, -70.5914
2025-04-08 13:40 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | Q2212010784 | Breaker | n/a |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 87 Elm Street |  | Cohasset | MA | 2025 | Unit-322 ¦Refrigerator Breaker keeps tripping circuit | Thermodor | 2.23e+17 |  | Condo/Kitchen | Unit-322¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17847772229 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333123238 | 41.7465, -70.5914
2025-04-08 13:44 | Paul | Myers | 21609 | 55 Portside Drive |  | Pocasset | MA | 2559 | 508-388-6169 | Project Manager | paul@cesinc.biz | G2212150267 | Breaker | N/a |  |  | 1 Pole | Siemens | Residence |  | 2025-03-19 | 2024-12-22 | 87 Elm Street |  | Cohasset | MA | 2025 | Unit-323¦Refrigerator Breaker keeps tripping circuit | Thermodor | 2.23e+17 |  | Condo/Kitchen | Unit-323¦Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17847800521 | Chrome 134.0.0.0 / Windows | 73.47.34.255 | 1333125123 | 41.7465, -70.5914
2025-04-09 13:44 | Steven | Rooney | 13678 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service Manager | Steven@Giombettielectric.com | Culter hammer | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2022-10-20 | 2022-10-20 | 31 Avebury Lane |  | Marlborough | MA | 1752 | Breaker would randomly trip when not in use | Fridge Air Galley | GCRE3060BF |  | Kitchen | Range stopped working | No | No | No | No |  | https://www.formstack.com/admin/download/file/17852910759 | Chrome 135.0.0.0 / Windows | 98.118.122.8 | 1333484014 | 42.415, -71.1061
2025-04-14 11:05 | Brooke | Heisler-Leary | 58767 | 4 Open Square Way |  | Holyoke | MA | 1040 | (413)265-8094 | Electrician | brooke.heisler-leary@trinity-solar.com | Schneider Electric Square D Homeline | Breaker | 40a 2 pole breaker | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-04-14 | 2025-04-16 | 1638 North St |  | Pittsfield | MA | 1201 | Breaker trips when preheating oven. Occurred multiple times. | GE | JBP84T0H2WW | None | Single family | Kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/17870213785 | Mobile Safari 15.3 / iOS | 174.192.1.81 | 1334785589 | 42.101, -72.5737
2025-04-14 12:43 | Lucas | Da Silva | 23636 | 27 farm st |  | Bellingham | MA | 2019 | 7812667491 | Master electrician | marqueselectrician@gmail.com | QPFB 30 | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/17870926451 | 2025-01-15 | 2025-01-25 |  |  | 115 loring rd, weston | MA | 2493 | Breakers tripping 2 minutes after turning the appliance | Wolf oven | S030TM/S/TH |  | Single family | Kitchen oven | No | No | No | No |  | https://www.formstack.com/admin/download/file/17870926464 | Mobile Safari / iOS | 172.56.193.201 | 1334836823 | 42.4125, -71.0034
2025-04-15 07:59 | Joshua | Laclair | 22548 | 9 KIDDER RD | Suite B&C | CHELMSFORD | MA | 01824-3398 | 9782564845 | Master Electrician | josh@villagehomeservices.com | QF250A | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2025-03-06 | 2025-03-06 | 28 Alton Place #E |  | Brookline | MA | 2446 | Breaker trips during appliance usage. | Thermador | PRI30LBHU/04 | None | Single Family Condo | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17874709731 | https://www.formstack.com/admin/download/file/17874709732 | Chrome 135.0.0.0 / OS X | 72.74.55.214 | 1335105110 | 42.5945, -71.3571
2025-04-15 08:06 | Joshua | Laclair | 22548 | 9 KIDDER RD | Suite B& C | CHELMSFORD | MA | 01824-3398 | 9782564845 | Master Electrician | josh@villagehomeservices.com | Q120DF | Breaker | N/A | 20 |  | 1 Pole | Siemens | Residence |  | 2025-03-06 | 2025-03-06 | 28 Alton Place #E |  | Brookline | MA | 2446 | Appliance trips the breaker upon use | Insikerator | pro 750 | none | Single Family Condo | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17874730788 | https://www.formstack.com/admin/download/file/17874730789 | Chrome 135.0.0.0 / OS X | 72.74.55.214 | 1335106939 | 42.5945, -71.3571
2025-04-15 08:09 | Joshua | Laclair | 22548 | 9 Kidder Rd | STE B&C | CHELMSFORD | MA | 01824-3398 | 9782564845 | Master Electrician | josh@villagehomeservices.com | Q120DF | Breaker | N/A | 20 |  | 1 Pole | Siemens | Residence |  | 2025-03-06 | 2025-03-06 | 28 Alton Place #E |  | Brookline | MA | 2446 | Appliance trips breaker upon use | Thermador | DWHD660EFP/01 | None | Single Family Condo | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17874740595 | https://www.formstack.com/admin/download/file/17874740596 | Chrome 135.0.0.0 / OS X | 72.74.55.214 | 1335107775 | 42.5945, -71.3571
2025-04-15 08:12 | Joshua | Laclair | 22548 | 9 Kidder Rd | STE B&C | CHELMSFORD | MA | 01824-3398 | 9782564845 | Master Electrician | josh@villagehomeservices.com | Q120DF | Breaker | N/A | 20 |  | 1 Pole | Siemens | Residence |  | 2025-03-06 | 2025-03-06 | 28 Alton Place #E |  | Brookline | MA | 2548 | Appliance trips breaker upon use | Signature | SKSMD2401A | None | Single Family Condo | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17874750124 | https://www.formstack.com/admin/download/file/17874750125 | Chrome 135.0.0.0 / OS X | 72.74.55.214 | 1335108534 | 42.5945, -71.3571
2025-04-15 08:16 | Joshua | Laclair | 22548 | 9 Kidder Rd | STE B&C | CHELMSFORD | MA | 01824-3398 | 9782564845 | Master Electrician | josh@villagehomeservices.com | Q120DF | Breaker | N/A | 20 |  | 1 Pole | Siemens | Residence |  | 2025-03-06 | 2025-03-06 | 28 Alton Place #E |  | Brookline | MA | 2446 | Appliance trips upon use | Fisher & Paykel | RD36A72U1N | None | Single Family Condo | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17874761626 | https://www.formstack.com/admin/download/file/17874761627 | Chrome 135.0.0.0 / OS X | 72.74.55.214 | 1335109540 | 42.5945, -71.3571
2025-04-15 08:19 | Joshua | Laclair | 22548 | 9 Kidder Rd | STE B&C | CHELMSFORD | MA | 01824-3398 | 9782564845 | Master Electrician | josh@villagehomeservices.com | Q120DF | Breaker | N/A | 20 |  | 1 Pole | Siemens | Residence |  | 2025-03-06 | 2025-03-06 | 28 Alton Place #E |  | Brookline | MA | 2446 | Appliance trips upon use | Hotte De La Cuisine | PCHBL630S | None | Single Family Condo | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/17874770408 | https://www.formstack.com/admin/download/file/17874770409 | Chrome 135.0.0.0 / OS X | 72.74.55.214 | 1335110222 | 42.5945, -71.3571
2025-04-15 08:32 | Chris | Polny | 11660 | 325 Hopping Brook |  | Holliston | MA | 1746 | 7742178986 | VP Electrical Operations | christopherpolny@rodenhiser.com | Siemens QF250 | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2025-04-14 | 2025-04-08 | 4 Eustis Rd |  | Lexington | MA |  | New electric range would trip GFCI Breaker | Aga | Elise36IND |  | Single family dwelling | Only range is affected | No | No | No | No |  | https://www.formstack.com/admin/download/file/17874816421 | Chrome 135.0.0.0 / Windows | 174.242.72.231 | 1335113888 | 42.3464, -71.0975
2025-04-15 08:59 | Gerald | McGraw | 18146 | 5 Minnesota Ave |  | Warwick | RI | 2888 | 401 739 9473 | owner | jjelectric2003@aol.com | square d HOM230GFI | Breaker | none | 30 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/17874919020 | 2025-03-30 | 2025-03-30 | 3102 Cranberry Highway Building 1 & 2 |  | Wareham | MA | 2532 | When stove is turned on it trips the GFI breaker. | GE | jbs460dm5bb jts5000dv1bb jp3030dw1bb | none | apartment | kitchen stove | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17874919034 | https://www.formstack.com/admin/download/file/17874919035 | Chrome 135.0.0.0 / Windows | 71.245.68.165 | 1335121468 | 41.8219, -71.5067
2025-04-15 12:03 | Jason | Curran | 21794 | 695 S Main Street |  | Bellingham | MA | 2019 | 774-573-7535 | Master Electrician | jasoncurranelectrician@gmail.com | Eaton/BRN250GF | Breaker | Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2025-04-15 | 2025-04-15 | 695 S Main Street |  | Bellingham | MA | 2019 | Breaker randomly trips without any load. | GE | GRS600AVFS |  | Single Family | Kitchen. | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17875906619 | Chrome 131.0.0.0 / OS X | 71.10.248.177 | 1335191799 | 42.0509, -71.7543
2025-04-16 06:40 | Jesse | Kuhlman | 21804 | 313 Eastern Avenue | 46-4305562 | Lynn | MA | 1902 | 617.890.6905 | owner | ervis.kes@gmail.com | HOM250GFICP | Breaker | none | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-04-10 | 2025-04-10 | 5 Howe Stree |  | Quincy | MA | 2169 | Breaker tripped when stove was on, about 10 min in | Frigidaire | GCFI3060BFC |  | single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17879803702 | Chrome 135.0.0.0 / Windows | 209.6.193.104 | 1335464376 | 42.4125, -71.0034
2025-04-16 06:49 | Jesse | Kuhlman | 21804 | 313 Eastern Avenue |  | Lynn | MA | 1902 | 6178906905 | owner | ervis.kes@gmail.com | HOM250GFICP | Breaker | none | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-03-27 | 2025-03-27 | 24 Mount Ash Rd. |  | Boston | MA | 2136 | Breaker immediately tripped when stove was put on. Worked fine on cook top | Frigidaire | GCFI3060BFC | no | single family | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17879817644 | Chrome 135.0.0.0 / Windows | 209.6.193.104 | 1335465416 | 42.4125, -71.0034
2025-04-16 13:14 | Peter | Garofalo | 14831 | 65 New Salem Street Unit A |  | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton #BRN230GF | Breaker | n/a | 30 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 101 |  | Cambridge | MA | 2114 | Breaker trips when the dryer runs | Samsung | DV25B6900EW | NONE | Apartment/Laundry Room | Just the dryer | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881560406 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335585461 | 42.481, -71.1563
2025-04-16 13:19 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN230GF | Breaker | n/a | 30 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 209 |  | Cambridge | MA | 2114 | The breaker trips when the dryer runs | Samsung | DV25B6900EW | NONE | Apartment/Laundry | Laundry Room | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881588221 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335587585 | 42.481, -71.1563
2025-04-16 13:21 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN230GF | Breaker | n/a | 30 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 211 |  | Cambridge | MA | 2114 | The breaker trips when the dryer runs | Samsung | DV25B6900EW | NONE | apartment | laundry room | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881603050 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335588862 | 42.481, -71.1563
2025-04-16 13:23 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN230GF | Breaker | n/a | 30 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 212 |  | Cambridge | MA | 2114 | the breaker trips when the dryer runs | Samsung | DV25B6900EW | NONE | apartment | laundry room | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881615371 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335589923 | 42.481, -71.1563
2025-04-16 13:25 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN230GF | Breaker | n/a | 30 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 212 |  | Cambridge | MA | 2114 | the breaker trips when the dryer runs | Samsung | DV25B6900EW | NONE | apartment | laundry room | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881632676 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335591274 | 42.481, -71.1563
2025-04-16 13:28 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN230GF | Breaker | n/a | 30 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 214 |  | Cambridge | MA | 2114 | the breaker trips when the dryer runs | Samsung | DV25B6900EW | NONE | apartment | laundry room | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881644699 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335592084 | 42.481, -71.1563
2025-04-16 13:30 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN230GF | Breaker | n/a | 30 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 215 |  | Cambridge | MA | 2114 | the breaker trips when the dryer runs | samsung | DV25B6900EW | NONE | apartment | laundry room | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881657525 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335592940 | 42.481, -71.1563
2025-04-16 13:32 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN230GF | Breaker | n/a | 30 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 301 |  | Cambridge | MA | 2114 | the breaker trips when the dryer runs | samsung | DV25B6900EW | NONE | apartment | laundry room | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881668149 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335593642 | 42.481, -71.1563
2025-04-16 13:39 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN230GF | Breaker | n/a | 30 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 309 |  | Cambridge | MA | 2114 | the breaker trips when the dryer runs | samsung | DV25B6900EW | NONE | apartment | laundry room | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881708098 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335596473 | 42.481, -71.1563
2025-04-16 13:40 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN230GF | Breaker | n/a | 30 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 313 |  | Cambridge | MA | 2114 | the breaker trips when the dryer runs | samsung | DV25B6900EW | none | apartment | laundry room | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881718463 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335597191 | 42.481, -71.1563
2025-04-16 13:43 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN230GF | Breaker | n/a | 30 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 501 |  | Cambridge | MA | 2114 | the breaker trips when the dryer runs | samsung | DV25B6900EW | non | apartment | laundry room | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881731547 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335598135 | 42.481, -71.1563
2025-04-16 14:04 | Sean | Griffin | 14425 | 8 Pleasant Street Suite A2 |  | Natick | MA | 1760 | 7745719815 | Project Manager | sean.griffin@thorndikedevelopment.com | BRN240GF | Breaker | Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2025-04-16 | 2025-04-16 | 1 Oxbow Road |  | Raynham | MA | 2767 | stove trips breaker | General Electric | PB935YPFS | None | Townhome | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17881857310 | Chrome 135.0.0.0 / Windows | 71.162.115.107 | 1335606812 | 42.5945, -71.3571
2025-04-16 14:12 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 209 |  | Cambridge | MA | 2114 | when the stove runs the breaker trips | GE | GJAS640RMSS | NONE | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881902522 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335609956 | 42.481, -71.1563
2025-04-16 14:13 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 211 |  | Cambridge | MA | 2114 | the breaker trips when the stove runs | GE | GJAS640RMSS | NONE | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881913295 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335610697 | 42.481, -71.1563
2025-04-16 14:18 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 212 |  | Cambridge | MA | 2114 | the breaker trips when the stove runs | GE | GJAS640RMSS | NONE | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881936362 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335612311 | 42.481, -71.1563
2025-04-16 14:20 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 215 |  | Cambridge | MA | 2114 | the breaker trips when the dryer runs | GE | GJAS640RMSS | NONE | apartment | the breaker trips when the dryer runs | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881949369 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335613383 | 42.481, -71.1563
2025-04-16 14:22 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 314 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | GJAS640RMSS | NON | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881961037 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335614227 | 42.481, -71.1563
2025-04-16 14:23 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 404 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | GJAS640RMSS | NONE | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881971174 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335615106 | 42.481, -71.1563
2025-04-16 14:25 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 410 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | GJAS640RMSS | NONE | aparment | ktichen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881981630 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335615860 | 42.481, -71.1563
2025-04-16 14:27 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 412 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | GJAS640RMSS | NONE | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17881991771 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335616665 | 42.481, -71.1563
2025-04-16 14:29 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 414 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | GJAS640RMSS | NONE | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17882004365 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335617619 | 42.481, -71.1563
2025-04-16 14:31 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 415 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | GJAS640RMSS | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17882013551 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335618253 | 42.481, -71.1563
2025-04-16 14:33 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 213 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | JS645SLSS | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17882030181 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335619401 | 42.481, -71.1563
2025-04-16 14:35 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 301 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | JS645SLSS | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17882039694 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335620134 | 42.481, -71.1563
2025-04-16 14:36 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 302 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | JS64SLSS | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17882047156 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335620683 | 42.481, -71.1563
2025-04-16 14:38 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 306 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | JS645SLSS | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17882056349 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335621264 | 42.481, -71.1563
2025-04-16 14:40 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 101 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | JS645SLSS | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17882068389 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335622118 | 42.481, -71.1563
2025-04-16 14:42 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 205 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | JS645SLSS | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17882078777 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335622905 | 42.481, -71.1563
2025-04-16 14:43 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 206 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | JS645SLSS | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17882090360 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335623660 | 42.481, -71.1563
2025-04-16 14:45 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | President | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 503 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | JS645SLSS | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17882100367 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335624363 | 42.481, -71.1563
2025-04-16 14:47 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 504 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | JS645SLSS | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17882111942 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335625220 | 42.481, -71.1563
2025-04-16 14:49 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRN240GF | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 506 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | JS645SLSS | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17882119714 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335625799 | 42.481, -71.1563
2025-04-16 14:52 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton | Breaker | n/a | 40 | n/a | 2 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 511 |  | Cambridge | MA | 2114 | the breaker trips when the oven runs | GE | JS645SLSS | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17882137901 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335627050 | 42.481, -71.1563
2025-04-16 17:31 | Timothy | Seguin | 40591 | 10 Plumleigh Dr |  | North Dartmouth | MA | 2747 | 5083265664 | Electrician | tseguin27@comcast.net | HOM250GFI | Breaker | GFI Square D Homeline Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-04-16 | 2025-04-16 | 40 Nelson Ave |  | Fairhaven | MA | 2719 | Trips as soon as we try to power cooktop, disconnect cooktop breaker holds fine, re-connect breaker trips. There is no neutral on cooktop, straight 220volts | Wolf | C1365C/B |  | Single Family | Kitchen Appliance | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17882996767 | https://www.formstack.com/admin/download/file/17882996768 | Chrome 135.0.0.0 / Windows | 50.250.55.250 | 1335685171 | 42.2743, -71.0972
2025-04-16 17:41 | Timothy | Seguin | 40591 | 10 Plumleigh Dr |  | North Dartmouth | MA | 2747 | 5083265664 | Electrician | tseguin27@comcast.net | HOM230GFI | Breaker | Square D Homeline Breaker | 30 |  | 2 Pole | Schneider Electric | Residence |  | 2025-04-16 | 2025-04-16 | 40 Nelson Ave |  | Fairhaven | MA | 2719 | Oven gets works fine until you turn the unit off and it instantaneously trips the breaker, tried it several times | Wolf | S03050PE/S/P |  | Single Family | Kitchen Appliance | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17883039031 | https://www.formstack.com/admin/download/file/17883039032 | Chrome 135.0.0.0 / Windows | 50.250.55.250 | 1335688009 | 42.2743, -71.0972
2025-04-17 06:41 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a |  | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 215 |  | Cambridge | MA | 2114 | the breaker trips when the microwave runs | GE | GHMV1472BHS | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884663493 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335799269 | 42.481, -71.1563
2025-04-17 06:43 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 314 |  | Cambridge | MA | 2114 | the breaker trips when the microwave runs | GE | GHMV1472BHS |  | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884666043 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335799473 | 42.481, -71.1563
2025-04-17 06:45 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 215 |  | Cambridge | MA | 2114 | the breaker trips when the disposal runs | GE | GGFC535N | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884669504 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335799729 | 42.481, -71.1563
2025-04-17 06:47 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 314 |  | Cambridge | MA | 2114 | the breaker trips when the disposal runs | GE | GGFC535N | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884672210 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335799931 | 42.481, -71.1563
2025-04-17 06:49 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 402 |  | Cambridge | MA | 2114 | the breaker trips when the disposal runs | GE | GGFC535N | none | apartment | kitchen | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884674780 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335800128 | 42.481, -71.1563
2025-04-17 06:59 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 101 |  | Cambridge | MA | 2114 | the breaker trips when the washing machine runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884693491 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335801345 | 42.481, -71.1563
2025-04-17 07:00 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 102 |  | Cambridge | MA | 2114 | the breaker trips when the dishwasher runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884696793 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335801598 | 42.481, -71.1563
2025-04-17 07:02 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 206 |  | Cambridge | MA | 2114 | the breaker trips when the dishwasher runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884699925 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335801845 | 42.481, -71.1563
2025-04-17 07:03 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 208 |  | Cambridge | MA | 2114 | the breaker trips when the washing machine runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884702902 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335802064 | 42.481, -71.1563
2025-04-17 07:05 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 209 |  | Cambridge | MA | 2114 | the breaker trips when the washing machine runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884705315 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335802243 | 42.481, -71.1563
2025-04-17 07:07 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 211 |  | Cambridge | MA | 2114 | the breaker trips when the dishwasher runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884708513 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335802498 | 42.481, -71.1563
2025-04-17 07:08 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 212 |  | Cambridge | MA | 2114 | the breaker trips when the washing machine runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884711399 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335802799 | 42.481, -71.1563
2025-04-17 07:10 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 214 |  | Cambridge | MA | 2114 | the breaker trips when the dishwasher runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884714647 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335803140 | 42.481, -71.1563
2025-04-17 07:11 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 215 |  | Cambridge | MA | 2114 | the breaker trips when the washing machine runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884717310 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335803403 | 42.481, -71.1563
2025-04-17 07:12 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 301 |  | Cambridge | MA | 2114 | the breaker trips when the washing machine runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884720040 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335803653 | 42.481, -71.1563
2025-04-17 07:14 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 302 |  | Cambridge | MA | 2114 | the breaker trips when the washing machine runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884722265 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335803855 | 42.481, -71.1563
2025-04-17 07:15 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 310 |  | Cambridge | MA | 2114 | the breaker trips when the washing machine runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884725436 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335804108 | 42.481, -71.1563
2025-04-17 07:17 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 314 |  | Cambridge | MA | 2114 | the breaker trips when the washing machine runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884728112 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335804366 | 42.481, -71.1563
2025-04-17 07:18 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 501 |  | Cambridge | MA | 2114 | the breaker trips when the washing machine runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884730716 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335804587 | 42.481, -71.1563
2025-04-17 07:20 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | Eaton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 505 |  | Cambridge | MA | 2114 | the breaker trips when the dishwasher runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884732944 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335804782 | 42.481, -71.1563
2025-04-17 07:21 | Peter | Garofalo | 22070 | 65 New Salem Street Unit A | UNIT A | Wakefield | MA | 1880 | 7813890030 | president | rw56pl@yahoo.com | EAton BRP120DF | Breaker | n/a | 20 | n/a | 1 Pole | Eaton | Residence |  | 2024-11-25 | 2024-10-01 | 3 Hawkins Street - Apartment 507 |  | Cambridge | MA | 2114 | the breaker trips when the washing machine runs | Samsung | SWW22K6800AW | none | apartment | laundry | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/17884735809 | Chrome 135.0.0.0 / Windows | 146.115.113.200 | 1335804984 | 42.481, -71.1563
2025-04-17 07:45 | Jonathan | Rossborough | 35645 | 12 Cedar Lane |  | Kingston | MA | 2364 | 6175293755 | installer | clkelectricalservices@gmail.com | Siemens 2pole 40 amp GFCI | Breaker | Breaker | 40 |  | 2 Pole | Siemens | Residence |  | 2024-11-12 | 2024-10-20 | 1 Eagle Terrace |  | Carver | MA | 2330 | The breaker trips when lower wall oven is running. Tried putting on standard 40 amp breaker and ran oven for 4 hours to try a burnout period. Worked for a few months then started tripping again so changed breaker but continued to trip. Called manufacturer then sent out repair tech, he stated no issues with oven and no repair codes. He recommended changing breaker to a standard breaker instead of a GFCI | GE | JTD5000DV1BB | None | Residential | Kitchen | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17884785416 | https://www.formstack.com/admin/download/file/17884785417 | Chrome 135.0.0.0 / Windows | 24.61.159.60 | 1335808813 | 41.8915, -70.7646
2025-04-18 12:43 | Trevor | Hebb | 1971 | 895 Salem St | Unit 2A | Groveland | MA | 1834 | 9783731393 | electrician | office@danielsel.com | SIemens GFCI | Breaker | GFCI | 30 |  | 2 Pole | Siemens | Residence |  | 2025-04-07 | 2025-04-07 | 500 Broadway Unit 5123 |  | Malden | MA | 2148 | tripping mid dry | GE | GTX33EASRWW |  | Apartment | Laundry area | No | No | No | No |  |  | Chrome 133.0.0.0 / Windows | 50.187.12.233 | 1336229006 | 42.5437, -71.6495
2025-04-18 12:50 | Trevor | Hebb | 1971 | 895 Salem St | Unit 2A | Groveland | MA | 1834 | 9783731393 | electrician | office@danielsel.com | Siemens GFCI | Breaker | Breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2025-04-07 | 2025-04-07 | 500 Broadway unit 4123 |  | Malden | MA | 2148 | tripping mid dry | GE | GTX33EASRWW |  | Apartment | Laundry area | No | No | No | No |  |  | Chrome 133.0.0.0 / Windows | 50.187.12.233 | 1336231317 | 42.5437, -71.6495
2025-04-18 20:44 | Andrew | Harland | 21030 | Harland Electric | PO Box 94 | Littleton, MA | MA | 1460 | 9784868154 | President | andy@harlandelectric.com | Square D - QO250GFICP | Breaker | N/A | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-04-10 | 2025-04-10 | 55 Sunset Rd |  | Groton | MA | 1450 | Customer purchased new induction cooktop. Electrician install 50A circuit wiring and install 2 pole 50 GFCI breaker. When breaker is engaged, breaker trips instantly. Electrician checked circuit wiring, no issues. Checked appliance to ensure no continuity phase to phase or each phase to ground- no issue found. Electrician installed standard 50A breaker, tested appliance, which worked as it should. Reinstalled GFCI breaker, which tripped instantly. Due to no issues found with circuit wiring or appliance wiring, Electrician removed GFCI breaker and installed a non GFCI 2 pole 50A breaker. system normal at this time. | Wolf | C1365C/B | none | Single family dwelling | Kitchen appliance | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17891565946 | https://www.formstack.com/admin/download/file/17891565947 | Chrome 135.0.0.0 / Windows | 172.56.199.95 | 1336349610 | 42.4125, -71.0034
2025-04-18 21:09 | Andrew | Harland | 21030 | Harland Electric | PO Box 94 | Littleton, MA | MA | 1460 | 9784868154 | President | andy@harlandelectric.com | Siemens QF250A | Breaker | N/A | 50 |  | 2 Pole | Siemens | Residence |  | 2025-04-16 | 2025-04-16 | 150 Church St. |  | Newton | MA | 2458 | Customer purchased new induction cooktop. Electrician install 50A circuit wiring and installed 2 pole 50 GFCI breaker. When breaker is engaged, breaker trips instantly. Electrician checked circuit wiring, no issues. Checked appliance to ensure no continuity phase to phase or each phase to ground- no issue found. Electrician installed standard 50A breaker, tested appliance, which worked as it should. Reinstalled GFCI breaker, which tripped instantly. Due to no issues found with circuit wiring or appliance wiring, Electrician removed GFCI breaker and installed a non GFCI 2 pole 50A breaker. system normal at this time. | Miele | KM7745FL |  | Single family dwelling | Kitchen appliance | No | No | No | Yes | https://www.formstack.com/admin/download/file/17891604385 | https://www.formstack.com/admin/download/file/17891604386 | Chrome 135.0.0.0 / Windows | 172.56.199.95 | 1336352701 | 42.4125, -71.0034
2025-04-20 19:38 | Mark | Roussel | 21100 | 33 old forge Ln |  | Sudbury | MA | 1776 | 978 443 8888 | Electrician | Baseball78@verizon.net | WEE515SOLS3 RE0949897 | Breaker | ABB Breaker | 50 |  | 2 Pole | ABB | Residence |  | 2025-04-22 | 2025-04-18 | 26 Munroe Place |  | Concord | MA | 1742 | Tripping does not happen at initial plugging in of the range - but instead only occurs in the middle of a baking cycle | Whirlpool | WEE515SOLS3 RE0949897 | nothing | Single family residential kitchen range outlet only | Single family residential kitchen range outlet only | No | No | No | No | https://www.formstack.com/admin/download/file/17894820417 | https://www.formstack.com/admin/download/file/17894820418 | Chrome 135.0.0.0 / Windows | 108.49.70.111 | 1336621684 | 42.3912, -71.4154
2025-04-22 08:47 | Joseph | Penney | 11412 | 3 Daniel Drive |  | Stoneham | MA | 1867 | 6175900558 | ELECTRICIAN | joejr@penneyelec.com | QF250AP | Breaker | SIEMENS | 50 |  | 2 Pole | Siemens | Residence |  | 2025-04-19 | 2025-04-14 | 190 EDGEWATER DRIVE |  | NEEDHAM | MA | 2492 | 2 POLE 50 SIEMENS GFCI BREAKER TRIPS WHEN WALL OVEN IS USED IN KITCHEN. | SIEMENS | BSDEWO30SDV3 | none | single family home | kitchen (wall oven). | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17902067007 | https://www.formstack.com/admin/download/file/17902067008 | Safari 18.3.1 / OS X | 67.189.198.231 | 1337044538 | 42.4188, -71.1557
2025-04-22 09:27 | JOSEPH | REGO | 14348 | 30 OLD MEADOW ROAD |  | BREWSTER | ME | 2631 | 508-896-0011 | OWNER | joe@jregoelectric.com | SQ D HOMLINE HOM250GFCI | Breaker | 2 POLE | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-04-18 | 2025-04-14 | [5 empty] | NEW RANGE INTERMITTENTLY TRIPS GFCI BREAKER | GE | JB256D M4WW | NONE | KITCHEN | KITCHEN RANGE | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17902262955 | Safari 17.5 / OS X | 75.69.236.30 | 1337059579 | 41.6881, -71.1523
2025-04-23 06:46 | Matthew | Holt | 2230 | 3 | Breed Ave Unit F | Woburn | MA | 1801 | 6037656746 | Electrician | mattholtsed@gmail.com | HOM250GFI | Breaker | HOM250 | 50 | 50 | 2 Pole | Schneider Electric | Commercial |  | 2024-09-01 | 2024-09-15 | 893 Boston Rd |  | Haverhill | MA | 1835 | Range Breaker Tripping | Whirlpool | WFES3530RS0 | NA | Apartment | Kitchen Range Unit #'s Attached¦¦4101¦4102¦4103¦4104¦4105¦4106¦4107¦4108¦4109¦4201¦4202¦4203¦4204¦4205¦4206¦4207¦4208¦4209¦4301¦4302¦4303¦4304¦4305¦4306¦4307¦4308¦4309¦4401¦4402¦4403¦4404¦4405¦4406¦4407¦4408¦4409¦4501¦4502¦4503¦4504¦4505¦4506¦4507¦4508¦4509¦¦¦ | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17907084406 | https://www.formstack.com/admin/download/file/17907084407 | Chrome 135.0.0.0 / Windows | 72.74.34.124 | 1337401680 | 42.4539, -71.1414
2025-04-23 07:06 | Matthew | Holt | 2230 | 3 | Breed Ave Unit F | Woburn | MA | 1801 | 6037656746 | Electrician | mattholtsed@gmail.com | HOM250GFI | Breaker | NA | 50 |  | 2 Pole | Schneider Electric | Commercial |  | 2024-10-01 | 2024-10-15 | 891 Boston Rd |  | Haverhill | MA | 1835 | Range Breaker Tripping | Whirlpool | WFES3530RS0 | NA | Apartment | Kitchen Range Unit #'s Attached¦¦3101¦3102¦3102¦3103¦3104¦3105¦3106¦3107¦3108¦3109¦3201¦3202¦3203¦3204¦3205¦3206¦3207¦3208¦3209¦3301¦3302¦3303¦3304¦3305¦3306¦3307¦3308¦3309¦3401¦3402¦3403¦3404¦3405¦3406¦3407¦3408¦3409¦¦ | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17907123969 | https://www.formstack.com/admin/download/file/17907123970 | Chrome 135.0.0.0 / Windows | 72.74.34.124 | 1337404487 | 42.4539, -71.1414
2025-04-23 07:20 | Matthew | Holt | 2230 | 3 | Breed Ave Unit F | Woburn | MA | 1801 | 6037656746 | Electrician | mattholtsed@gmail.com | HOM250GFI | Breaker | NA | 50 |  | 2 Pole | Schneider Electric | Commercial |  | 2025-03-01 | 2025-03-15 | 889 Boston Rd |  | Haverhill | MA | 1835 | Range Breaker Tripping | Whirlpool | WFES3530RS0 | NA | Apartment | Kitchen Range Unit #'s Attached¦¦2101¦2102¦2103¦2104¦2105¦2106¦2107¦2108¦2109¦2201¦2202¦2203¦2204¦2205¦2206¦2207¦2208¦2209¦2301¦2302¦2303¦2304¦2305¦2306¦2307¦2308¦2309¦2401¦2402¦2403¦2404¦2405¦2406¦2407¦2408¦2409¦ | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17907151449 | https://www.formstack.com/admin/download/file/17907151450 | Chrome 135.0.0.0 / Windows | 72.74.34.124 | 1337406455 | 42.4539, -71.1414
2025-04-23 07:29 | Matthew | Holt | 2230 | 3 | Breed Ave Unit F | Woburn | MA | 1801 | 6037656746 | Electrician | mattholtsed@gmail.com | HOM250GFI | Breaker | NA | 50 |  | 2 Pole | Schneider Electric | Commercial |  | 2025-04-01 | 2025-04-15 | 887 Boston Rd |  | Haverhill | MA | 1835 | Range Breaker Tripping | Whirlpool | WFES3530RS0 | NA | Apartment | Kitchen Range Unit #'s Attached¦¦1101¦1102¦1103¦1104¦1105¦1106¦1107¦1108¦1109¦1201¦1202¦1203¦1204¦1205¦1206¦1207¦1208¦1209¦1301¦1302¦1303¦1304¦1305¦1306¦1307¦1308¦1309¦1401¦1402¦1403¦1404¦1405¦1406¦1407¦1408¦1409¦ | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17907169753 | https://www.formstack.com/admin/download/file/17907169754 | Chrome 135.0.0.0 / Windows | 72.74.34.124 | 1337407763 | 42.4539, -71.1414
2025-04-23 12:45 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-04-16 | 2025-04-15 | 660 Main St. |  | Worcester | MA |  | Apt 614¦¦Oven portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17908701775 | Chrome 135.0.0.0 / Windows | 66.189.80.15 | 1337514539 | 42.2555, -71.7719
2025-04-23 12:50 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-04-16 | 2025-04-15 | 660 Main St. |  | Worcester | MA |  | Apt 514¦¦Oven portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17908734091 | Chrome 135.0.0.0 / Windows | 66.189.80.15 | 1337516697 | 42.2555, -71.7719
2025-04-23 13:00 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-04-16 | 2025-04-15 | 660 Main St. |  | Worcester | MA |  | Apt 414¦¦Oven portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17908792055 | Chrome 135.0.0.0 / Windows | 66.189.80.15 | 1337520685 | 42.2555, -71.7719
2025-04-23 13:09 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-04-16 | 2025-04-15 | 660 Main St. |  | Worcester | MA |  | Apt 314¦¦Oven portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17908839030 | Chrome 135.0.0.0 / Windows | 66.189.80.15 | 1337523945 | 42.2555, -71.7719
2025-04-23 13:11 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-04-16 | 2025-04-15 | 660 Main St. |  | Worcester | MA |  | Apt 214¦¦Oven portion cannot be used without tripping breaker. Have contacted GE¦before and they have stated it is a known issue with their stoves and they¦cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17908854939 | Chrome 135.0.0.0 / Windows | 66.189.80.15 | 1337525098 | 42.2555, -71.7719
2025-04-25 12:49 | RICHARD | BAGNI | 16024 | 83 ALEXANDER ROAD | 83 ALEXANDER ROAD | BILLERICA | MA | 1821 | 9788088992 | OWNER/ ELECTRICIAN | JNUZZO@MURRAYHILLS.COM | SQUARE D | Breaker | BREAKER | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-09-16 | 2024-09-02 | 19 FERULLO DRIVE |  | WOBURN | MA | 1801 | OVEN BREAKER TRIPS AS SOON AS YOU TURN ON UNIT | GE CAFE IN MAIN KITCHEN & GE PROFILE IN BASEMENT KITCHEN | CTC912P2NSI - MAIN KITCHEN & PSS93YPFS - BASEMENT KITCHEN | NO | SINGLE FAMILY DWELLING | BOTH FIRST AND BASEMENT KITCHENS | No | No | No | Yes |  | https://www.formstack.com/admin/download/file/17918534292 | Chrome 135.0.0.0 / Windows | 173.14.169.229 | 1338213024 | 42.3687, -71.0863
2025-04-25 16:29 | Sean | Griffin | 14425 | 8 Pleasant Street Suite A2 |  | Natick | MA | 1760 | 7745719815 | Project Manager | sean.griffin@thorndikedevelopment.com | BRN240GF | Breaker | Breaker | 40 | 40 | 2 Pole | Eaton | Residence |  | 2025-04-25 | 2024-10-25 | 33 Oxbow Road |  | Raynham | MA | 2767 | stove trips breaker | General Electric | GRS600AVFS | None | Townhome | stove trips breaker | No | No | No | No |  | https://www.formstack.com/admin/download/file/17919773558 | Chrome 135.0.0.0 / Windows | 71.162.115.107 | 1338301341 | 42.5945, -71.3571
2025-04-28 10:11 | PAUL | SOULE | 11067 | 20 AEGEAN DRIVE / SUITE 3 |  | METHUEN | MA | 1844 | 978-375-5403 | VICE PRESIDENT (STILIAN ELECTRIC, INC) | PSOULE@STILIAN.COM | QO220GFI | Breaker | N/A | 20 |  | 2 Pole | Schneider Electric | Commercial | https://www.formstack.com/admin/download/file/17926513014 | 2025-04-28 | 2025-04-28 | 158 LEWIS STREET |  | LYNN | MA | 1902 | COMMERCIAL WASHING MACHINE UNITS WILL NOT OPERATE WITH GFCI CIRCUIT BREAKERS | LAUNDRYLUX - ELECTROLUX | WASHING MACHINES - EUD-680 / EUD-630 / EUD 645 | N/A | COMMERCIAL LAUNDROMAT | COMMERCIAL LAUNDROMAT FACILITY | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17926513031 | https://www.formstack.com/admin/download/file/17926513032 | Chrome 135.0.0.0 / Windows | 108.26.151.18 | 1338848362 | 42.7287, -71.1834
2025-04-28 10:19 | PAUL | SOULE | 11067 | 20 AEGEAN DRIVE / SUITE 3 |  | METHUEN | MA | 1844 | 978-375-5403 | VICE PRESIDENT (STILIAN ELECTRIC, INC.) | PSOULE@STILIAN.COM | QO120GFI | Breaker | N/A | 20 |  | 1 Pole | Schneider Electric | Commercial | https://www.formstack.com/admin/download/file/17926555280 | 2025-04-28 | 2025-04-28 | 158 LEWIS STREET |  | LYNN | MA | 1902 | COMMERCIAL CLOTHES DRYERS UNITS WILL NOT OPERATE WITH GFCI CIRCUIT BREAKERS | LAUNDRYLUX - ELECTROLUX | DE-683 / DE-650S | N/A | COMMERCIAL LAUNDROMAT | COMMERCIAL LAUNDROMAT FACILITY | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/17926555294 | https://www.formstack.com/admin/download/file/17926555295 | Chrome 135.0.0.0 / Windows | 108.26.151.18 | 1338851357 | 42.7287, -71.1834
2025-04-28 19:28 | Carlos | Franco | 59006 | 108 Fay Rd |  | Framingham | MA | 1702 | 5087406672 | Electritian | cf1electrical@outlook.com | Siemens | Breaker | GFCI Breaker | 50 |  | 2 Pole | Siemens | Residence |  | 2025-02-28 | 2024-09-07 | 65 Grove St apto 249 |  | Wellesley | MA | 2482 | Is keep on tripping for on beginning than start to keep on tripping mor often | GE CAFE | CHS950P4M6W2 |  | Apto | Kitchen | No | Yes | No | No | https://www.formstack.com/admin/download/file/17929774319 | https://www.formstack.com/admin/download/file/17929774320 | Mobile Safari 18.4 / iOS | 174.168.152.137 | 1339071738 | 42.3737, -71.1284
2025-04-28 20:48 | Colm | curran | 37206 | p.o box 41 |  | wollaston Ma 02170 | MA | 2170 | 6172402430 | president | amcelectrical@verizon.net | Brn250gf | Breaker | breaker | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17930038567 | 2025-04-25 | 2025-05-25 | 52 Ashworth st |  | quincy | MA | 2170 | GFI BREAKER TRIPS DAILY WHEN ELECTRIC OVEN IS USED | GE | PT9800SHSS |  | SINGLE FAMILY HOME | KITCHEN | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17930038580 | https://www.formstack.com/admin/download/file/17930038581 | Chrome 135.0.0.0 / Windows | 75.69.15.2 | 1339089518 | 42.2667, -71.0192
2025-04-29 19:51 | Ryan | Oliphant | 57759 | 16 Jonspin Rd, Wilmington, Massachusetts, 01887 |  | Wilmington | MA | 1887 | 7815689444 | Project Manager | roliphant@capelectric.net | GE THQB1120GFT | Breaker | None | 20 |  | 1 Pole | ABB | Commercial |  | 2025-03-27 | 2025-03-07 | 1995 Massachusetts Ave |  | Cambridge | MA | 2140 | Breaker randomly trips. This is a dedicated circuit for the fridge. | ATOSA | MGF8406GR |  | Coffee Shop | Coffee Shop | No | No | No | No | https://www.formstack.com/admin/download/file/17935277219 | https://www.formstack.com/admin/download/file/17935277220 | Chrome 135.0.0.0 / Windows | 50.210.71.190 | 1339443111 | 42.0774, -71.0446
2025-04-29 19:56 | Ryan | Oliphant | 57759 | 16 Jonspin Rd |  | Wilmington | MA | 1887 | 7815689444 | Project Manager | roliphant@capelectric.net | GE THQB1120GFT | Breaker | NONE |  |  | 1 Pole | ABB | Commercial |  | 2025-04-14 | 2025-03-07 | 1995 Massachusetts Ave |  | Cambridge | MA | 2140 | Breaker randomly trips when machine being used. | La Marzocco | KB90 | None | Coffee Shop | Coffee Shop | Yes | No | No | No | https://www.formstack.com/admin/download/file/17935295846 | https://www.formstack.com/admin/download/file/17935295847 | Chrome 135.0.0.0 / Windows | 50.210.71.190 | 1339444515 | 42.0774, -71.0446
2025-04-29 20:02 | Ryan | Oliphant | 557759 | 16 Jonspin Rd |  | Wilmington | MA | 1887 | 7815689444 | Project Manager | roliphant@capelectric.net | GE THQB1120GFT | Breaker | NONE | 20 |  | 1 Pole | ABB | Commercial |  | 2025-03-23 | 2025-03-07 | 1995 Massachusetts Ave |  | Cambridge | MA | 2140 | Refrigerator randomly tripped over night multiple times. | Atosa | MGF8420GR |  | Coffee Shop | Coffee Shop | Yes | No | No | No | https://www.formstack.com/admin/download/file/17935315619 | https://www.formstack.com/admin/download/file/17935315620 | Chrome 135.0.0.0 / Windows | 50.210.71.190 | 1339446537 | 42.0774, -71.0446
2025-04-29 20:09 | Ryan | Oliphant | 557759 | 16 Jonspin Rd, Wilmington, Massachusetts, 01887 |  | Wilmington | MA | 1887 | 7815689444 | Project Manager | roliphant@capelectric.net | GE THQB1120GFT | Breaker | NONE | 20 |  | 1 Pole | ABB | Commercial |  | 2025-04-01 | 2025-03-07 | 1995 MAssachusetts Ave |  | Cambridge | MA | 2140 | Proofer thrips randomly when in use. Proofer is on a dedicated circuit. | Moffat Turbofan | P8M |  | Coffee Shop | Coffee Shop | Yes | No | No | No | https://www.formstack.com/admin/download/file/17935338012 | https://www.formstack.com/admin/download/file/17935338013 | Chrome 135.0.0.0 / Windows | 50.210.71.190 | 1339448972 | 42.0774, -71.0446
2025-04-30 14:15 | Jose | Andrade | 54336 | 22 Monmouth St. |  | East Boston | MA | 2128 | 6179700068 | Sub-Contractor | jdandrade617@gmail.com | QF230AP | Breaker | Siemem | 30 |  | 2 Pole | Siemens | Residence |  | 2025-04-16 | 2025-04-16 | 159 High st. |  | Hingham | MA |  | Replacing the dryer cord from a 3 prong to a 4 prong. No ground jumper. Breaker trips. | Whirlpool | LEQ9858PW0 |  | Residential | Laudry, cloth dryer¦ | No | No | No | No | https://www.formstack.com/admin/download/file/17939281217 | https://www.formstack.com/admin/download/file/17939281218 | Chrome Mobile 135.0.0.0 / Android | 172.56.192.97 | 1339712999 | 42.4125, -71.0034
2025-04-30 16:31 | Robert | Kimberley | 10984 | 51 Town Hill Rd. |  | WEST OTIS | MA | 01245-9736 | 4132696211 | Electrician | RRKIM71@GMAIL.COM | Leviton | Breaker | LB240-G | 40 |  | 2 Pole | Leviton | Residence |  | 2025-04-30 | 2025-04-30 | 155 Moose Drive |  | Lee | MA | 1238 | Range instructions say it will not work with a GFCI breaker. We tried it but trips. | Bosch HIS8655U 36"" induction Industrial Style | Bosch HIS8655U 36"" induction Industrial Style | none | Kitchen | Kitchen Range | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17940158559 | Chrome 135.0.0.0 / Windows | 38.52.245.107 | 1339772636 | 42.1938, -73.0903
2025-04-30 18:22 | David | Caron | 18208 | 418 Potter Road |  | Framingham | MA | 1701 | 508-292-8783 | Owner | David@Caronelectrical.com | GFTCB250 | Breaker | none | 50 |  | 2 Pole | Eaton | Residence |  | 2025-04-01 | 2025-04-01 | 194 Waltham Street |  | Lexington | MA | 1731 | Upon plugging in the range the ground fault breaker trips after unplugging the unit you can reset the breaker. checked the strap was removed and the cable was fine. tried replacing the breaker to see if defective and that didn't work. Distributor was reached out too and they said that this range cannot be on a Gfi breaker . | CornuFe' | C1WF-I | none | Single family home | The room affected by the trip is the kitchen | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/17940720008 | https://www.formstack.com/admin/download/file/17940720009 | Chrome 135.0.0.0 / Windows | 174.168.3.80 | 1339812238 | 42.3026, -71.4306
2025-05-01 06:56 | Andy | Courtade | 39574 | 11 1st Ave |  | Bellingham | MA | 2019 | 5088162001 | Electrician/owner | ezek1@verizon.net | KCIG550JSS01 | Breaker | Square D | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2024-04-29 | 2024-04-29 | 11 1st Ave |  | Bellingham | MA | 2019 | Appliance will not work with the GFCI but works fine with a regular breaker. | KitchenAid | KCIG550JSS01 |  | Single-family dwelling | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/17942584465 | Safari 18.4 / OS X | 96.230.230.237 | 1339946699 | 42.1398, -71.5162
2025-05-01 08:11 | Francis | Baudanza | 20326 | 328 Great Rd |  | Bedford | MA | 1730 | 781-275-6662 | pres/owner | baudanza@erols.com | Leviton | Breaker | GFCI breaker | 30 |  | 2 Pole | Leviton | Residence |  | 2025-04-30 | 2025-02-19 | 102 South Rd |  | Bedford | MA | 1730 | breaker trips as soon as appliance is plugged in | LG | DLEX400W |  | Laundry | Laundry Dryer | No | No | No | No |  | https://www.formstack.com/admin/download/file/17942749799 | Firefox 115.0 / Windows 7 | 73.234.196.146 | 1339960357 | 42.2904, -71.0712
2025-05-02 09:06 | Marcin | Plewa | 52635 | 89 Old Southbridge Rd |  | Dudley | MA | 1571 | 5084505610 | electrician | plewaelectric@gmail.com | BRN230GF | Breaker | EATON BR230 | 30 | 30 | 2 Pole | Eaton | Residence |  | 2025-04-07 | 2025-04-01 | 902 Mammoth Rd |  | Dracut | MA | 1571 | Wall Owen is tripping gfci circuit breaker GE service technician diagnose the oven and sead that circuit breaker is to sensitive for this oven. | General Electric | JTS3000DNWW | NO OTHER EQUIPMENT | RESIDANCE | Common kitchen for residance | Yes | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17948481504 | Chrome 136.0.0.0 / Windows | 156.19.81.118 | 1340395182 | 42.0738, -72.0303
2025-05-02 10:12 | Stephen | Meade | 21445 | 740 | Quaker Highway | UXBRIDGE, MA MA 01569 | MA | 1569 | 5082783200 | Senior Project Manager | smeade@eecne.com | Eaton GFTCB240 | Breaker | N/a | 40 |  | 2 Pole | Eaton | Residence |  | 2025-01-08 | 2024-10-01 | 386 Kilburn Street |  | Fall River | MA | 2724 | GFCI tripping for the Ranges throughout 101 apartments. | general Electric | JB 645 RKB SS | N/A | APARTMENT/KITCHEN | KITCHEN STOVE | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/17948775863 | Chrome 135.0.0.0 / Windows | 71.83.63.218 | 1340416201 | 42.1501, -71.8684
2025-05-02 10:47 | Marcus | Pisapia | 12561 | 50 Harbor View Park |  | Milton | MA | 2186 | 781 632 3500 | Electrician | MarcusPisapia@Hotmail.com | CUT BRP 120 DF | Breaker | A | 20 |  | 1 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17949604982 | 2025-04-27 | 2025-04-27 | 88 Mears Avenue |  | Quincy | MA | 2169 | Occasionally trips | Phillips | 3300 EP3326/90 | none | single family home | Kitchen | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/17949605027 | Chrome 135.0.0.0 / Windows | 185.190.141.157 | 1340487832 | 42.3574, -71.0618
2025-05-02 10:59 | Marcus | Pisapia | 12561 | 50 Harbor View Park |  | Milton | MA | 2186 | 781 632 3500 | Electrician | MarcusPisapia@Hotmail.com | CUT BRP120 DF | Breaker | A | 20 |  | 1 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17949744546 | 2025-04-27 | 2025-04-27 | 88 Mears Avenue |  | Quincy | MA | 2169 | It occasionally trips, much too often. | Breville | BOV900 BSSUSC/A | none | single family home | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17949744560 | https://www.formstack.com/admin/download/file/17949744561 | Chrome 135.0.0.0 / Windows | 185.190.141.157 | 1340499018 | 42.3574, -71.0618
2025-05-02 11:18 | Marcus | Pisapia | 12581 | 50 Harbor View Park |  | Milton | MA | 2186 | 781-632-3500 | Electrician | MarcusPisapia@Hotmail.com | CUT BRN225GF BR | Breaker | A | 30 | 25 | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17949855966 | 2025-04-27 | 2025-04-27 | 88 Mears Ave. |  | Quincy | MA | 2169 | When the wall oven was turned on, it started to heat for a few minutes and then it tripped and needed to be reset. It never even began to reach the set temperature of 350 degrees F. | Kitchenaid single wall oven | KOES430RSS00 | none | Single family residence | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17949855980 | https://www.formstack.com/admin/download/file/17949855981 | Chrome 135.0.0.0 / Windows | 185.190.141.157 | 1340506534 | 42.3574, -71.0618
2025-05-02 11:27 | Marcus | Pisapia | 12561 | 50 Harbor View Park |  | Milton | MA | 2186 | 781-632-3500 | Electrician | MarcusPisapia@Hotmail.com | CUT BRP120 DF | Breaker | A | 20 |  | 1 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17949903522 | 2025-04-27 | 2025-04-27 | 88 Mears Avenue |  | Quincy | MA | 2169 | Sometimes it trips, at least 2-4 times so far. | Bosch | ENR: B26CL80ENS/43 FD 407 | none | single family home | Kitchen | Yes | No | No | No | https://www.formstack.com/admin/download/file/17949903536 | https://www.formstack.com/admin/download/file/17949903537 | Chrome 135.0.0.0 / Windows | 185.190.141.157 | 1340509936 | 42.3574, -71.0618
2025-05-02 11:38 | Marcus | Pisapia | 12561 | 50 Harbor View Park |  | Milton | MA | 2186 | 7816323500 | Electrician | MarcusPisapia@Hotmail.com | CUT BRN240GF | Breaker | A | 40 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/17949970340 | 2025-04-27 | 2025-04-27 | 88 Mears Ave. |  | Quincy | MA | 2169 | It is wired correctly but when the two live wires are connected, the system trips, every time. | Fornebo | 70537757 | none | single family home | kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17949970354 | https://www.formstack.com/admin/download/file/17949970355 | Chrome 135.0.0.0 / Windows | 185.190.141.157 | 1340514320 | 42.3574, -71.0618
2025-05-02 13:09 | James | Loughlin | 17387 | PO BOX 72 | PO BOX 72 | Franklin | MA | 2038 | 5085280765 | owner | sales@loughlinelectric.com | GE profile pb911sjss | Breaker | ITE | 50 |  | 2 Pole | Siemens | Residence |  | 2025-03-10 | 2025-03-04 | PO BOX 72, |  | Franklin | MA | 2038 | GFCI breaker trips when using the electric stove | GE | PB911SJSS | NO | Single family | Kitchen electric range | No | No | No | No | https://www.formstack.com/admin/download/file/17950490803 | https://www.formstack.com/admin/download/file/17950490804 | Chrome 135.0.0.0 / Windows | 98.118.109.186 | 1340549789 | 42.0622, -71.3412
2025-05-06 11:10 | Jake | Carlan | 1971 | 895 Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Electrician | office@danielsel.com | L1908020198 | Breaker | NA | 50 |  | 2 Pole | Siemens | Residence |  | 2025-04-30 | 2025-04-30 | 27 Victor Unit 7 |  | Haverhill | MA | 1832 | Stove breaker continually trips during preheat | GE | JB250DF4WW |  | Apartment | Kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/17965313412 | Chrome 135.0.0.0 / Windows | 50.187.12.233 | 1341612846 | 42.5437, -71.6495
2025-05-06 14:49 | Eric | Caldon | 21306 | 100 Deanville Rd |  | Attleboro | MA | 2703 | 7742296409 | owner | Ecaldonmidstate@gmail.com | Eaton CAT BRN230GF | Breaker | for dryer | 50 |  | 2 Pole | Eaton | Residence |  | 2025-04-08 | 2025-04-08 | 33 Tulip Ct |  | Attleboro | MA | 2703 | Installed new breaker for dryer | GE Appliances - dryer | PFD87ESPV0RS | none | laundry room | n/a | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/17966670323 | https://www.formstack.com/admin/download/file/17966670324 | Chrome 136.0.0.0 / Windows | 96.230.233.54 | 1341706547 | 42.1398, -71.5162
2025-05-07 07:35 | Angela | Callery | 58376 | 43 Arbutus Trail |  | Chatham | MA | 2633 | 508-241-1083 | Homeowner | runituni@charter.net | Q250gfi | Breaker | 0 |  |  | 2 Pole | Siemens | Residence |  | 2025-05-06 | 2025-04-15 | [5 empty] | After 30 seconds trips the stove | Themador | PRD366WGU /09 |  | Single Family | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/17969609696 | Chrome 136.0.0.0 / Windows | 73.100.92.61 | 1341915241 | 41.6896, -70.1564
2025-05-09 11:35 | William | LeMay | 17175 | 36 Evans Rd. |  | Needham | MA | 2492 | 781-444-5200 | Field Supervisor | bill@hillcrestelectric.com | THQL2150GFT2 | Breaker | Plug-in Line | 50 |  | 2 Pole | ABB | Residence |  | 2025-05-09 | 2025-05-09 | 67 Arch St. |  | Needham | MA | 2492 | Circuit breaker trips as soon as energized. Holds when wires disconnected. | Bertazzoni | MAST365IRTXT |  | Single family. | Kitchen. | No | No | No | No |  | https://www.formstack.com/admin/download/file/17981359253 | Safari 18.4 / OS X | 173.76.205.11 | 1342766891 | 42.2934, -71.2356
2025-05-12 17:20 | Robert | Kimberley | 10984 | 51 Town Hill Rd. |  | WEST OTIS | MA | 01245-9736 | 4132696211 | ELECTRICIAN | RRKIM71@GMAIL.COM | Leviton LB120-DFT | Breaker | AFCI/GFCI Dual Function | 20 | 20 | 1 Pole | Leviton | Residence |  | 2025-05-12 | 2025-05-12 | 73 MOOSE DR. |  | LEE | MA | 1238 | THE BREAKER WILL TRIP AFTER RUNNING A FEW MINUTES, POSSIBLY WHEN ENTERING THE DEFROST CYCLE. | BOSCH | B36CL80ENS | NONE | KITCHEN | REFRIGERATOR ONLY | No | No | No | No |  | https://www.formstack.com/admin/download/file/17991905855 | Chrome 136.0.0.0 / Windows | 38.52.245.107 | 1343539261 | 42.1938, -73.0903
2025-05-14 13:04 | Matt | Elder | 20748 | 40 Bedford Park, Unit 2 |  | Bridgewater | MA | 2324 | 6175933008 | President | matt@elderelectric.net | Tipo-HOM 120/240 volt - AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-05-08 | 2024-03-24 | 872 Morton Street |  | Boston | MA |  | Breaker keeps randomly tripping when cooking or warming up stove. | G.E. | JS645SL5SS |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18001265451 | Chrome 136.0.0.0 / Windows | 73.100.133.251 | 1344195685 | 41.977, -70.971
2025-05-14 13:13 | Matt | Elder | 20748 | 40 Bedford Park, Unit 2 |  | Bridgewater | MA | 2324 | 6175933008 | President | matt@elderelectric.net | Tipo-HOM 120/240 volt - AD-910 | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-05-08 | 2024-03-25 | 872 Morton Street |  | Boston | MA |  | Breaker keeps randomly tripping when cooking or warming up stove. | G.E. | JS645SL5SS |  | Kitchen | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18001320615 | Chrome 136.0.0.0 / Windows | 73.100.133.251 | 1344199596 | 41.977, -70.971
2025-05-14 16:37 | David | Short | 21476 | 705 Arlington St. |  | Dracut | MA | 1826 | 6172570522 | Owner | dshort@shortelectric.com | THQL2130GFT | Breaker | none | 30 |  | 2 Pole | ABB | Residence |  | 2025-05-14 | 2022-07-27 | 1 Dalton St. Unit 5201 |  | Boston | MA | 2115 | We did not wire or install the Oven. The oven is new, as we are working for the first owner. The breaker was tripped. We reset it and it tripped after 5 seconds without any major load. I checked the wiring to the oven and inspected the internal wioring of the oven. Everything seems fine. I nstalled a regular breaker and the oven works fine. I reinstalled the GFCI breaker and the same thing happens. | Wolf | so30cm/b | none | Multi family dwelling unit | It is the oven in the kitchen. | No | No | No | No | https://www.formstack.com/admin/download/file/18002531320 | https://www.formstack.com/admin/download/file/18002531321 | Chrome 135.0.0.0 / Windows | 73.182.181.167 | 1344281609 | 43.0206, -70.9049
2025-05-18 19:06 | Jesse | Kuhlman | 21804 | 313 Eastern Avenue |  | Lynn | MA | 1902 | 617.741.5043 | Owner | ervis.kes@gmail.com | Q120DFP | Breaker | none | 20 |  | 1 Pole | Siemens | Residence |  | 2025-04-08 | 2025-04-08 | 102 Hancock Street Unit 4 |  | Cambridge | MA | 2139 | Miele washer tripped at the spin cycle. Yale distributor and the manufacturer both say that the washer can't be on a GFCI breaker or outlet. | Miele | WWD160 | no | Apartment | Laundry room | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/18017293683 | Chrome 136.0.0.0 / Windows | 209.6.193.104 | 1345430195 | 42.4125, -71.0034
2025-05-18 19:15 | Jesse | Kuhlman | 21804 | 313 Eastern Avenue | 46-4305562 | Lynn | MA | 1902 | 617.741.5043 | Owner | ervis.kes@gmail.com | Q120DFP | Breaker | no | 20 |  | 1 Pole | Siemens | Residence |  | 2025-04-21 | 2025-04-22 | 68 Charles St |  | Arlington | MA | 2474 | Panasonic microwave would trip the breaker a few seconds in the cycle. The unit is brand new and holds fine on an arc fault. | Panasonic | NN-SN66KB | no | House | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18017315888 | Chrome 136.0.0.0 / Windows | 209.6.193.104 | 1345432875 | 42.4125, -71.0034
2025-05-19 09:21 | Daniel | Greenberg | 54913 | 05 Chippewa Way |  | West Bridgewater | MA | 2379 | 7812647746 | Construction Superintendent | Dgreenberg@stonebridgehomesinc.com | DP-4075 | Breaker | - | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/18019032364 | 2025-05-01 | 2025-04-28 | [5 empty] | Each time we start the oven up, the breaker trips at the panel. We are new home builders and see this with many of the electric ranges we are installing. | Frigidaire | GCFE3060BFE |  | Single Family Home | Electrical range in kitchen of new home. | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/18019032377 | https://www.formstack.com/admin/download/file/18019032381 | Chrome 135.0.0.0 / Windows | 174.168.242.252 | 1345569254 | 42.0857, -70.999
2025-05-19 09:26 | Daniel | Greenberg | 54913 | 04 Chippewa Way |  | West Birdgwater | MA | 2379 | 7812647746 | Construction Superintendent | Dgreenberg@stonebridgehomesinc.com | DP-4075 | Breaker | - | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/18019056966 | 2025-05-01 | 2025-04-28 | [5 empty] | Each time we start the oven up, the breaker trips at the panel. We are new home builders and see this with many of the electric ranges we are installing. | Frigidaire | VF43905386 |  | Single Family Home | Kitchen of new home | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/18019056996 | https://www.formstack.com/admin/download/file/18019056997 | Chrome 135.0.0.0 / Windows | 174.168.242.252 | 1345571040 | 42.0857, -70.999
2025-05-19 10:40 | Eric | Caldon | 21306 | 100 Deanville Rd |  | Attleboro | MA | 2703 | 7742296409 | Owner | Ecaldonmidstate@gmail.com | Cutler Hammer | Breaker | n/a | 50 |  | 2 Pole | Eaton | Residence |  | 2025-05-09 | 2025-05-01 | 3 Muriel Way |  | Rehoboth | MA |  | Breaker tripped when the oven was in use | GE | WAS-30 | warmer | single family | When oven is on and warmer is turned on, breaker trips | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/18019445212 | https://www.formstack.com/admin/download/file/18019445213 | Chrome 136.0.0.0 / Windows | 96.230.233.54 | 1345600245 | 42.1398, -71.5162
2025-05-19 10:46 | Eric | Caldon | 21306 | 100 Deanville Rd |  | Attleboro | MA | 2703 | 7742296409 | owner | Ecaldonmidstate@gmail.com | Cutler Hammer | Breaker | n/a | 20 |  | 1 Pole | Eaton | Residence |  | 2025-05-09 | 2025-05-01 | 3 Muriel Way |  | Rehoboth | MA |  | When a second appliance is turned on, breaker trips | Bosch | HWD5051UC/03 | oven | single family | When oven is on and then the warmer is turned on, the breaker trips | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/18019478994 | https://www.formstack.com/admin/download/file/18019478995 | Chrome 136.0.0.0 / Windows | 96.230.233.54 | 1345602938 | 42.1398, -71.5162
2025-05-19 10:52 | Eric | Caldon | 21306 | 100 Deanville Rd |  | Attleboro | MA | 2703 | 7742296409 | owner | Ecaldonmidstate@gmail.com | Eaton | Breaker | n/a | 30 |  | 2 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/18019522469 | 2025-05-10 | 2025-05-02 | 10 Starr Lane |  | Rehoboth | MA |  | Dryer breaker randomly trips | LG | DLE8400WE | none | single family | Dryer breaker randomly trips | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/18019522483 | https://www.formstack.com/admin/download/file/18019522484 | Chrome 136.0.0.0 / Windows | 96.230.233.54 | 1345607221 | 42.1398, -71.5162
2025-05-20 18:39 | Adrian | OMalley | 2414 | 41 Roberts Road |  | Waltham | MA | 2453 | 6172930382 | Electrician | electricpower99@gmail.com | Leviton 2E31O0 | Breaker | Breaker | 50 |  | 2 Pole | Leviton | Residence |  | 2025-04-28 | 2025-04-28 | 230 Clark Road |  | Brookline | MA | 2445 | As soon as stove was turned on the breaker tripped. | Bosch | 1BOS.HIS80 |  | Single Family Home | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18027566390 | Chrome 136.0.0.0 / Windows | 71.232.53.220 | 1346204564 | 42.3427, -71.0922
2025-05-20 21:43 | Jesus | Tejeda | 14285 | 265 Neponset valley parkway |  | Hyde park | MA | 2136 | 6175902479 | Electrician | jt7electrical@yahoo.com | ITN | Breaker | Gfi breaker | 30 |  | 2 Pole | Eaton | Residence |  | 2025-05-01 | 2025-05-01 | 197 eighth st |  | Boston | MA | 2129 | After 3 min the breaker trips | Thermador | PO301W | Cook top | Kitchen | Kitchen oven | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/18028136432 | Mobile Safari 18.4 / iOS | 24.60.193.75 | 1346243103 | 42.3399, -71.1245
2025-05-21 09:18 | Todd | Whitney | 51157 | 639 Townsend Harbor Road |  | Lunenburg | MA | 1462 | 9785824698 | President | Whitney_electric@hotmail.com | BR Eaton 2-pole breaker | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2025-04-30 | 2025-04-03 | 15 Whittemore Street |  | Concord | MA | 1742 | As soon as unit gets plugged in and turned on breaker tripped. | WOLF | IR30450/S/T |  | Kitchen | Kitchen stove | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/18029532490 | Chrome 136.0.0.0 / Windows | 24.2.171.37 | 1346340657 | 42.5301, -71.7553
2025-05-21 11:59 | Carl | Perkinsw | 11876 | 79 Cooley St |  | Agawam | MA | 1001 | 4132043063 | Service Electrician | no72gto@Yahoo.com | QO250GFI | Breaker | Breaker | 50 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/18030377564 | 2025-05-09 | 2025-04-08 | 40 Brighton Ave |  | Pittsfield | MA | 1201 | Tripping breaker when using oven. | Whirlpool | Rf364pxkw | None | Kitchen | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/18030377590 | https://www.formstack.com/admin/download/file/18030377592 | Mobile Safari 18.5 / iOS | 174.242.129.18 | 1346398377 | 41.667, -72.5968
2025-05-21 15:15 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor | castlecp@hotmail.com | Siemens | Breaker | breaker | 30 |  | 2 Pole | Siemens | Residence |  | 2025-05-07 | 2024-11-07 | 11 Guswood |  | Acton, | MA | 1719 | Installed a 30-amp GFCI breaker on a new cooktop. It was fine for the 1st few months. Then it started continuously tripping. | Thermador | CIT36YWBB | none | Single family | Kitchen | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/18031489619 | Chrome 136.0.0.0 / Windows | 38.146.55.40 | 1346476143 | 42.366, -71.2271
2025-05-21 15:22 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor | castlecp@hotmail.com | Siemens | Breaker | Breaker | 20 |  | 1 Pole | Siemens | Residence |  | 2025-05-14 | 2025-05-14 | 11 Guswood |  | Acton | MA | 1720 | Installed a new 20-amp dual-function breaker on a new down draft. It continuously trips. | Thermador | UCYM36XS |  | Single family. | Kitchen. | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/18031527976 | Chrome 136.0.0.0 / Windows | 38.146.55.40 | 1346478952 | 42.366, -71.2271
2025-05-21 15:39 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor | castlecp@hotmail.com | Siemens | Breaker | Breaker | 40 |  | 2 Pole | Siemens | Residence |  | 2025-05-14 | 2024-11-08 | 292 Westford St. |  | Carlisle | MA | 1741 | Installed a new 2-pole 40-amp GFCI breaker on a new wall oven. It was fine for a few months. Now it continually trips. | GE Profile | PTD7000SN55 |  | Single Family | Kitchen. | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/18031628518 | Chrome 136.0.0.0 / Windows | 38.146.55.40 | 1346486511 | 42.366, -71.2271
2025-05-21 15:52 | Gustavo | Simoes | 19280 | 12 Welles way |  | Chilmark | MA | 2535 | 7745634988 | Electrician | jbsimoes2@gmail.com | LB250GFR | Breaker | GFCI Breaker | 50 |  | 2 Pole | Leviton | Residence |  | 2025-05-20 | 2025-05-20 | 426 Bigelow rd |  | Vineyard Haven | MA | 2568 | breaker trips and does not arm whenever the range is plugged in | Bosch | B-1774-657ER |  | Single family Dwelling | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/18031704324 | Mobile Safari 18.3.1 / iOS | 107.122.189.70 | 1346491880 | 29.3959, -98.4761
2025-05-21 16:50 | phillip | Aiello | 23342 | 399 Page St |  | lunenburg | MA | 1462 | 9788360515 | owner/electrician | philaielloelec@gmail.com | Siemens 2 pole 50 GFCI breaker | Breaker | NA | 50 |  | 2 Pole | Siemens | Residence |  | 2025-05-21 | 2025-05-20 | 20 Sand Hill Rd. |  | Groton | MA | 1450 | Installed 2 pole 50 GFCI breaker. Breaker would stay on. As soon as the electric range was plugged in it would immediately trip. Checked and made sure cord and range were wired correctly and neutrals and ground were separate. | Electrolux | ECFI3668AS |  | Kitchen | kitchen appliance. | No | Yes | Yes | No |  | https://www.formstack.com/admin/download/file/18032037688 | Chrome 136.0.0.0 / Windows | 71.234.92.61 | 1346514304 | 42.5301, -71.7553
2025-05-21 20:45 | Ruiming | Liang | 58245 | 13 Kilby Street,Unit#2 |  | Quincy | MA | 2169 | 617-383-16556 | Journeyman Electrician | Alaing1656@gmail.com | Siemens Single Phase @-Pole GFCI Circuit Breaker/QPF | Breaker | Class A | 40 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/18032918230 | 2025-05-12 | 2025-05-11 | Kitchen |  | 36 Breakwater Drive Chelsea | MA | 2150 | SIEMENS 40AMP Single Phase 2-Pole GFCI breaker is able to be energized and function correctly under the oven unused condition.It trips within 30 seconds when the oven starts working. | Thermador | PODS302B | N/A | CONDO/TOWN HOUSE | A combination built-In oven is 4-wire hard-wire connection by AWG#8 on an dedicated 40amp appliance brand circuit installed in kitchen cabinet. | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/18032918244 | https://www.formstack.com/admin/download/file/18032918245 | Safari 18.4 / OS X | 98.229.82.73 | 1346574257 | 42.1648, -71.1379
2025-05-22 09:35 | Sean | Griffin | 14425 | 8 Pleasant Street Suite A2 |  | Natick | MA | 1760 | 7745719815 | Project Manager | sean.griffin@thorndikedevelopment.com | BRN240GF | Breaker | Breaker | 40 | 40 | 2 Pole | Eaton | Residence |  | 2025-05-22 | 2025-04-22 | 10 Oxbow Road |  | Raynham | MA | 2767 | stove causes breaker to trip | General Electric | JS760SPSS |  | townhome | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18034514708 | Chrome 136.0.0.0 / Windows | 71.162.115.107 | 1346697880 | 42.5945, -71.3571
2025-05-22 11:37 | Scott | Webster | 21363 | 65 North Main Street |  | Laneaborough | MA | 1237 | 413-655-0180 | Owner | scott@websterelectricllc.com | BRN250GF | Breaker | EATON Plug in Breaker | 50 |  | 2 Pole | Eaton | Residence |  | 2025-05-21 | 2025-05-21 | 379 McNearny Raod |  | Becket | MA | 1011 | The new Miele Double Oven would trip instantly on the new Eaton GFI 50 AMP 2 pole Breaker that we installed. We checked all connections at the panel, and the junction box for the unit and they were all good. | Miele | H 7780 BP2 | none | New Kitchen | The New double oven was the only item on this new circuit in the new kitchen that would trip instantly. | No | No | No | No | https://www.formstack.com/admin/download/file/18035226725 | https://www.formstack.com/admin/download/file/18035226726 | Chrome 136.0.0.0 / Windows | 141.126.239.67 | 1346751638 | 41.4826, -73.4096
2025-05-22 11:58 | Scott | Webster | 21363 | 65 North Main Street |  | Lanesborough | MA | 1237 | 413-655-0180 | Owner | scott@websterelectricllc.com | Eaton | Breaker | Eaton Plug IN Breaker | 60 |  | 2 Pole | Eaton | Residence |  | 2025-05-21 | 2025-05-25 | 379 McNearny Road |  | Becket | MA | 1011 | The New Miele cook top trips instantly when the New Eaton 60 amp 2 pole GFI breaker is turned on. All connections were checked and all were good. | Miele | KM 7745 FL | None | New Kitchen | The New Circuit to the new Miele Cook Top in the new kitchen would trip instantly when the New Eaton GFI Breaker was turned on. | No | No | No | No | https://www.formstack.com/admin/download/file/18035416140 | https://www.formstack.com/admin/download/file/18035416142 | Chrome 136.0.0.0 / Windows | 141.126.239.67 | 1346768480 | 41.4826, -73.4096
2025-05-22 11:59 | Scott | Webster | 21363 | 65 North Main Street |  | Lanesborough | MA | 1237 | 413-655-0180 | Owner | scott@websterelectricllc.com | Eaton | Breaker | Eaton Plug IN Breaker | 60 |  | 2 Pole | Eaton | Residence |  | 2025-05-21 | 2025-05-25 | 379 McNearny Road |  | Becket | MA | 1011 | The New Miele cook top trips instantly when the New Eaton 60 amp 2 pole GFI breaker is turned on. All connections were checked and all were good. | Miele | KM 7745 FL | None | New Kitchen | The New Circuit to the new Miele Cook Top in the new kitchen would trip instantly when the New Eaton GFI Breaker was turned on. | No | No | No | No | https://www.formstack.com/admin/download/file/18035427054 | https://www.formstack.com/admin/download/file/18035427055 | Chrome 136.0.0.0 / Windows | 141.126.239.67 | 1346769494 | 41.4826, -73.4096
2025-05-23 12:22 | Eric | Caldon | 21306 | 100 Deanville Rd |  | Attleboro | MA | 2703 | 7742296409 | owner | Ecaldonmidstate@gmail.com | Cutler Hammer | Breaker | n/a | 30 |  | 3 Pole | Eaton | Residence | https://www.formstack.com/admin/download/file/18040452361 | 2025-05-19 | 2024-12-18 | 27 Ledge Hill Rd |  | Rehoboth | MA |  | Breaker trips randomly when both washer and dryer are being used. | LG | DLE8400BE |  | single family | Laundry room | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/18040452374 | https://www.formstack.com/admin/download/file/18040452375 | Chrome 136.0.0.0 / Windows | 96.230.233.54 | 1347125707 | 42.1398, -71.5162
2025-05-26 13:13 | James | Finnegan | 37717 | 61 S Main St | South Main St | Ashburnham | MA | 1430 | 9786608327 | Electrician | finnegan65@verizon.net | ABB | Breaker | ? | 50 |  | 2 Pole | ABB | Residence |  | 2025-08-09 | 2025-08-09 | 100-102 Central St |  | Concord | MA |  | GFI breaker tripped when using stove in any function. It held until you tried any any function. | GE | CHS950P2M8S1 | 0 | Kitchen | Kitchen circuits in both apartments. Same stoves, same breakers | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/18047687322 | Chrome 136.0.0.0 / Windows | 73.100.48.3 | 1347673667 | 42.6789, -72.0477
2025-05-27 15:19 | William | Leiser | 7930 | 8 Sibley Road |  | Weston | MA | 2493 | 781-893-5966 | Project Manager | leisercorp@aol.com | Cutler Hammer CH-BR250 | Breaker | n-a | 50 |  | 2 Pole | Eaton | Residence |  | 2025-05-14 | 2025-05-14 | 41 Wessex Road |  | Westwood | MA | 2090 | Consistent tripping with GFI in place | AGA Induction Elise stove | AEL-361NWHT |  | Single family home | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18052684598 | Chrome 136.0.0.0 / Windows | 73.16.176.27 | 1348023446 | 42.3104, -71.2741
2025-05-28 07:05 | William | Cooke | 18314 | PO BOX 950 | 543 North Washington St | North Attleboro | MA | 2761 | 5082940827 | Electrician | bill@pachecocooke.com | GFTCB240 | Breaker | Breaker | 40 |  | 2 Pole | Eaton | Residence |  | 2025-05-23 | 2025-03-22 | 43 Avery Way |  | Norfolk | MA | 2052 | Tripping when Oven not in use multiple times over many days | CAFE | CHS900P2M8S1 | NO | Kitchen | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/18055405479 | https://www.formstack.com/admin/download/file/18055405480 | Chrome 136.0.0.0 / Windows | 75.67.150.10 | 1348214838 | 42.0581, -70.8077
2025-05-28 07:25 | William | Cooke Jr. | 18314 | PO BOX 950 | 543 North Washington St | North Attleboro | MA | 2761 | 5082940827 | Electrician | bill@pachecocooke.com | GFTCB230 | Breaker | Breaker | 30 |  | 2 Pole | Eaton | Residence |  | 2025-03-21 | 2025-05-23 | 353 Mount Vernon |  | Dedham | MA | 2026 | Tripping multiple times when oven is not in use | WOLF | S03050PM/S/P | NO | Kitchen | Kitchen | Yes | No | Yes | No | https://www.formstack.com/admin/download/file/18055450469 | https://www.formstack.com/admin/download/file/18055450470 | Chrome 136.0.0.0 / Windows | 75.67.150.10 | 1348218317 | 42.0581, -70.8077
2025-05-29 06:53 | Mark | Roussel | 21100 | 33 old forge Ln |  | Sudbury | MA | 1776 | 9784438888 | electrician | Baseball78@verizon.net | QF250AP | Breaker | circuit breaker | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/18061271255 | 2025-05-28 | 2025-05-28 | 51 Fox Run |  | Sudbury | MA | 1776 | Unit trips within first 60 seconds of turning on stove top | GE Cafe | CHP95362M1SS | nothing | single family home | kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/18061271269 | https://www.formstack.com/admin/download/file/18061271270 | Chrome 136.0.0.0 / Windows | 108.49.70.111 | 1348658597 | 42.5275, -71.1032
2025-05-29 11:14 | Cal | Harvey | 14426 | 13 Oxbow Road |  | Raynham | MA | 2767 | 5086500650 | Assistant Project Manager | cal.harvey@thorndikedevelopment.com | BRN250GF | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2025-05-28 | 2025-05-26 | [5 empty] | Dryer and Range Causing Breaker to trip | GE | GRF500PVSS |  | Townhome | Kitchen and Laundry Room | No | No | No | No |  | https://www.formstack.com/admin/download/file/18062317823 | Chrome 136.0.0.0 / Windows | 71.162.115.107 | 1348749940 | 42.5945, -71.3571
2025-05-29 11:15 | Cal | Harvey | 14426 | 13 Oxbow Road |  | Raynham | MA | 2767 | 5086500650 | Assistant Project Manager | cal.harvey@thorndikedevelopment.com | BRN250GF | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2025-05-28 | 2025-05-26 | [5 empty] | Dryer and Range Causing Breaker to trip | GE | GRF500PVSS |  | Townhome | Kitchen and Laundry Room | No | No | No | No |  | https://www.formstack.com/admin/download/file/18062319235 | Chrome 136.0.0.0 / Windows | 71.162.115.107 | 1348750034 | 42.5945, -71.3571
2025-05-29 11:22 | Cal | Harvey | 14426 | 17 Oxbow Road |  | Raynham | MA | 2767 | 5086500650 | Assistant Project Manager | cal.harvey@thorndikedevelopment.com | BRN250GF | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2025-05-28 | 2025-05-28 | [5 empty] | Range causing breaker to trip | GE | GRF500PVSS |  | Townhome | Kitchen, laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/18062358280 | Chrome 136.0.0.0 / Windows | 71.162.115.107 | 1348753195 | 42.5945, -71.3571
2025-05-29 11:25 | Cal | Harvey | 14426 | 12 Oxbow Road |  | Raynham | MA | 2767 | 5086500650 | Assistant Project Manager | cal.harvey@thorndikedevelopment.com | BRN250GF | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2025-05-28 | 2025-05-28 | 8, Pleasant Street, A-2 |  |  |  |  | Range causing breaker to trip | GE | GRF500PVSS |  | Townhome | Kitchen, laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/18062379277 | Chrome 136.0.0.0 / Windows | 71.162.115.107 | 1348754775 | 42.5945, -71.3571
2025-05-29 11:32 | Cal | Harvey | 14426 | 41 Oxbow Road |  | Raynham | MA | 2767 | 5086500650 | Assistant Project Manager | cal.harvey@thorndikedevelopment.com | BRN250GF | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2025-05-28 | 2025-05-28 | [5 empty] | Range causing breaker to trip | GE | GRS600AVFS |  | Townhome | kitchen, laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/18062420136 | Chrome 136.0.0.0 / Windows | 71.162.115.107 | 1348757894 | 42.5945, -71.3571
2025-05-29 12:34 | Chris | Polny | 11660 | 325 Hopping Brook | Rodenhiser Home Services | Holliston | MA | 1746 | 7742178986 | VP Electrical Operations | christopherpolny@rodenhiser.com | GFTCB250CS | Breaker | NA | 50 |  | 2 Pole | Eaton | Residence |  | 2025-05-29 | 2025-05-29 | 23 Tammer Lane |  | Hopkinton | MA | 1748 | Installed on circuit for Charge Point EV charger and tripped immediately. Inspected circuit and all filed accessible wiring | Chargepoint | Home Flex Series charger | None | Single Family Dwelling | Only EV charger affective | No | No | No | No |  | https://www.formstack.com/admin/download/file/18062781577 | Chrome 136.0.0.0 / Windows | 71.184.196.53 | 1348784661 | 42.232, -71.5361
2025-05-29 18:05 | Thomas | Rogan | 16426 | 84 Seminole Rd |  | Acton | MA | 1720 | 9782634948 | Electrician | roganelectric@aol.com | Eaton | Breaker | None | 50 |  | 2 Pole | Eaton | Residence |  | 2025-05-14 | 2020-11-01 | 30 Union |  |  | MA | 1742 | When cooking stove top it oven the gfi breaker trips. | GE Profile | PHS930SL4SS |  | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/18064568534 | https://www.formstack.com/admin/download/file/18064568535 | Mobile Safari 18.5 / iOS | 146.75.253.253 | 1348917445 | 42.2934, -71.2356
2025-05-29 19:22 | Jeff | McLaughlin | 12014 | 3 Ross Circle |  | Assonet | MA | 2702 | 7742977436 | Owner | jmclaughlin3@comcast.net | LB250-G | Breaker | Breaker | 50 |  | 2 Pole | Leviton | Residence |  | 2025-05-28 | 2025-05-28 | 33 Turner St |  | Norfolk | MA | 2056 | Cooktop immediately trips breaker even if cooktop is not turned on. Can not get GFCI breaker to hold. | Meile | KM6375 |  | Dwelling Kitchen | Kitchen electric cooktop | Yes | No | No | No |  | https://www.formstack.com/admin/download/file/18064836611 | Chrome 136.0.0.0 / Windows | 73.126.60.81 | 1348938724 | 42.0648, -71.2504
2025-05-30 08:26 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-05-28 | 2025-05-26 | 660 Main St. |  | Worcester | MA |  | Apt 114¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240WDM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/18066418918 | Chrome 136.0.0.0 / Windows | 66.189.80.15 | 1349054186 | 42.2555, -71.7719
2025-05-30 08:28 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2025-05-29 | 2025-05-27 | 660 Main St. |  | Worcester | MA |  | Apt 116¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/18066424405 | Chrome 136.0.0.0 / Windows | 66.189.80.15 | 1349054620 | 42.2555, -71.7719
2025-05-30 09:07 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2024-12-04 | 2024-12-06 | 660 Main St. |  | Worcester | MA |  | Apt 607¦¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/18066552489 | Chrome 136.0.0.0 / Windows | 66.189.80.15 | 1349064036 | 42.2555, -71.7719
2025-05-30 09:11 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2024-12-04 | 2024-12-06 | 660 Main St. |  | Worcester | MA |  | Apt 507¦¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/18066567006 | Chrome 136.0.0.0 / Windows | 66.189.80.15 | 1349065119 | 42.2555, -71.7719
2025-05-30 09:14 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2024-12-04 | 2024-12-06 | 660 Main St. |  | Worcester | MA |  | Apt 407¦¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/18066581557 | Chrome 136.0.0.0 / Windows | 66.189.80.15 | 1349066225 | 42.2555, -71.7719
2025-05-30 09:19 | Sean | Matthies | 23034 | 1667 Central St. |  | Worcester | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2024-12-04 | 2024-12-06 | 660 Main St. |  | Worcester | MA |  | Apt 307¦¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | NA | Apartment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/18066600411 | Chrome 136.0.0.0 / Windows | 66.189.80.15 | 1349067564 | 42.2555, -71.7719
2025-05-30 09:21 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Pole | Schneider Electric | Residence |  | 2024-12-06 | 2024-12-04 | 660 Main St. |  | Worcester | MA |  | Apt 207¦¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Aprtment | Kitchen | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/18066607584 | Chrome 136.0.0.0 / Windows | 66.189.80.15 | 1349068069 | 42.2555, -71.7719
2025-05-30 15:38 | Cal | Harvey | 14426 | 3 Oxbow Road | Unit B | Raynham | MA | 2767 | 5086500650 | Assistant Project Manager | cal.harvey@thorndikedevelopment.com | BRN250GF | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2025-05-30 | 2025-05-30 |  |  |  | MA |  | Range causing breaker to trip | GE | GRS600AVFS |  | Townhome | Kitchen, laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/18069043215 | Chrome 136.0.0.0 / Windows | 71.162.115.107 | 1349204729 | 42.5945, -71.3571
2025-05-30 19:26 | James | McCormack | 53625 | 196 High St | Unit 2 | Ipswich | MA | 1938 | 9782388250 | Owner | jim@upwire-electric.com | LB230-GFR | Breaker | Magnetic | 30 |  | 2 Pole | Leviton | Residence |  | 2025-05-30 | 2025-05-30 | 36 N Ridge |  | Ipswich | MA | 1938 | When dryer runs with wet clothes the GFCI breaker trips | Electrolux | ELFE7437AG0 |  | Single Family Home | Laundry Room | No | No | No | No |  | https://www.formstack.com/admin/download/file/18070048673 | Chrome 137.0.0.0 / Windows | 173.48.201.48 | 1349268158 | 42.6842, -70.8478
2025-05-31 17:37 | Dany | Gomes | 13423 | 73 stearns street |  | Pawtucket | RI | 2861 | 4016236107 | Electrician | danygomes63@gmail.com | GFTCB220 | Breaker | Circuit breaker | 20 |  | 2 Pole | Eaton | Commercial |  | 2025-05-10 | 2025-05-05 | 399 middle sttreet |  | Weymouth | MA | 2189 | installed the required GFCI per 210.8 B 14 ,for two commercial washers . Washers are tripping GFCI when it goes thru cycle.¦¦¦¦¦¦ | Wascomat | WLD745 | Non | Commercial laundromat | Main area - Two washers | Yes | Yes | Yes | Yes |  | https://www.formstack.com/admin/download/file/18072216277 | Chrome Mobile 136.0.7103.91 / iOS | 68.14.158.140 | 1349484146 | 41.886, -71.3457
2025-06-02 11:48 | Cole | Powers | 18122 | 151 Beach Road | Suite 2E | Vineyard Haven | MA | 2568 | 508-696-6400 | President | powerselectric@comcast.net | Eaton BRN120DF | Breaker | Breaker | 20 |  | 1 Pole | Eaton | Residence |  | 2025-05-16 | 2025-05-16 | 45 Edgewood Road |  | Edgartown | MA | 2539 | Circuit would trip periodically after new refrigerator was installed. | Bosch | B36CT80SNS144 | None | Single Family Household | Kitchen refrigerator. | No | No | No | No |  | https://www.formstack.com/admin/download/file/18076931274 | Chrome 136.0.0.0 / Windows | 76.152.41.177 | 1349825206 | 41.3856, -70.5085
2025-06-02 17:17 | Bryan | A Dollard | 23498 | 472 West Broadway 101B | suite 4 | SOUTH BOSTON | MA | 2127 | 7812667291 | president | Bryan@bayelectricalcorp.com | brn250gf | Breaker | plug in | 50 |  | 2 Pole | Eaton | Residence |  | 2025-05-20 | 2025-04-02 | 82 Baxter St 1 &2 |  | SOUTH BOSTON | MA | 2127 | Stove trips gfci breaker 10-15 mins after oven is turned on | LG | LSIL6334FE | 0 | 2 RENTAL APARTMENTS | Kitchen Stoves | No | No | No | No |  | https://www.formstack.com/admin/download/file/18078913432 | Chrome 137.0.0.0 / Windows | 73.234.90.145 | 1349958042 | 42.3399, -71.1245
2025-06-02 17:27 | Bryan | A Dollard | 23498 | 472 West Broadway 101B | suite 4 | SOUTH BOSTON | MA | 2127 | 7812667291 | president | Bryan@bayelectricalcorp.com | brp115df | Breaker | eaton | 15 |  | 1 Pole | Eaton | Residence |  | 2025-05-13 | 2025-04-02 | 472 West B, suite 4 |  | SOUTH BOSTON | MA | 2127 | Both fridges starting tripping the gfci breaker 4 weeks after install. | LG | LRFLC2706S | 0 | 2 RENTAL APARTMENTS | KITCHEN FRIDGE | No | No | No | No |  | https://www.formstack.com/admin/download/file/18078958200 | Chrome 137.0.0.0 / Windows | 73.234.90.145 | 1349961071 | 42.3399, -71.1245
2025-06-03 08:55 | Michael | Peterson | 11718 | 24 Athol Rd |  | Royalston | Ma | 1331 | 978-407-1831 | Owner | mfp425@gmail.com | Siemens | Breaker |  | 50 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F05%2FIMG_2856.jpg&form-id=2&field-id=22&hash=a950229fe33cd7cf0089bb98b0668644228ef22c6f95b7342e042457e1e199c4 | 2025-05-20 | 2025-05-06 | 780 Old Keene Rd |  | Athol | Ma | 1331 | The breaker trips almost every time the oven is used, it does not trip with the cook top only. | Frigidaire | GCF13060BFD |  | Single bedroom apartment | The oven is only circuit, tried two different GFCI breakers with same result. | No | No |  | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F05%2FIMG_2855.jpg&form-id=2&field-id=42&hash=73e12789fd9c110633d22668e6825aa98b5d8cabec45c0d2e2a2e521bbaeadf1 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F05%2FIMG_2846.jpg&form-id=2&field-id=42&hash=15d75a4c0c97c5f0c96a0b38fb5bd0c377241e0f3bde756631641e09b24a5224 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F05%2FIMG_2854.jpg&form-id=2&field-id=42&hash=3f455c66b9d642712263a321ac17f7e4ebaa55cde881f8d16e28060c2ac2f7bb | Michael Peterson | Unknown |  | 1350110396
2025-06-03 08:55 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | 4132430690 | OWNER/VP | JOHN@HENRYSELECTRICINC.COM | SQUARE ""D"" HOMELINE | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence |  | 2025-04-15 | 2025-04-25 | 190 LAUREL STREET |  | LEE | MA | 1238 | Breaker does not hold, kept tripping. | FISHER PAYKEL | DE7027G1 |  | SINGLE FAMILY | LAUNDRY | No | No |  | No |  | JOHN LEPREVOST | Unknown |  | 1350110397
2025-06-03 08:55 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Poles | Schneider Electric | Residence |  | 2025-05-14 | 2025-05-12 | 660 Main St. |  | Worcester | MA |  | Apt 516¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | NA | Apartment | Kitchen | Yes | No |  | No |  | Sean Matthies | Unknown |  | 1350110398
2025-06-03 08:55 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 01238-1641 | 413-243-0690 | OWNER/VP | JOHN@HENRYSELECTRICINC.COM | Q250 | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-05-16 | 2025-05-16 | 189 WEST STREET |  | LENOX | MA | 1240 | Breaker does not hold, kept tripping. | LG | LSES6338N |  | SINGLE FAMILY | KITCHEN | No | No |  | No |  | JOHN LEPREVOST | Unknown |  | 1350110399
2025-06-03 08:55 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Poles | Schneider Electric | Residence |  | 2025-05-07 | 2025-05-05 | 660 Main St. |  | Worcester | MA |  | Apt 616¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | NA | Apartment | Kitchen | Yes | No |  | No |  | Sean Matthies | Unknown |  | 1350110401
2025-06-03 08:55 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Poles | Schneider Electric | Residence |  | 2025-05-07 | 2025-05-05 | 660 Main St. |  | Worcester | MA |  | Apt 616¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | NA | Apartment | Kitchen | Yes | No |  | No |  | Sean Matthies | Unknown |  | 1350110402
2025-06-03 08:55 | Francis | Baudanza | Master 7755 Journeyman 20326 | 328 Great Rd |  | Bedford | MA | 1730 | 781-275-6662 | Pres/owner | baudanza@erols.com | Bosch B36CT80SNS/11 | Breaker |  | 20 |  | 1 Pole | Leviton | Residence |  | 2025-05-16 | 2025-05-15 | 102 South Rd |  | Bedford | MA | 1730 | The breaker would trip after the refrigerator is running for a while. | Bosch | B36CT80SNS/11 |  | single residence | kitchen refrigerator only | No | No |  | No |  | Frank Baudanza | Unknown |  | 1350110403
2025-06-03 08:55 | James | Kostas | LIC#58376-B | 31 Narrows Lane |  | South Yarmouth | MA | 2664 | 617-835-2619 | homeowner | drkostas@completedentalcarema.com | Model #HOM230GFI | Breaker |  | 30 |  | 2 Poles | Schneider Electric | Residence |  | 2025-05-17 | 2025-05-17 | [5 empty] | My newly delivered Speedqueen washer/dryer Model #ATEE9ASP178TW01¦Product Code: SF7007WE¦Serial #250474214¦when it is plugged into the dryer outlet, it trips the circuit breaker. The electrician has come out to make sure all the connections and the outlet and the circuit breaker are not faulty. KAM Appliance came out and confirmed that the unit does not have any defect | Speedqueen | ATEE9ASP178TW01 | None | private home/laundry closet | laundry closet in a bathroom. | Yes | Yes |  | Yes |  | James Kostas | Unknown |  | 1350110404
2025-06-03 08:55 | Mark | Thibault | 14667 | 1 Industrial Way Unit #5 |  | Tyngsboro | Massachusetts | 1879 | 9782265946 | President | mark@stelectrical.net | HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-05-14 | 2025-05-15 | 280 Martins Landing | Unit 203 | North Reading | Massachusetts | 1864 | When warming up the oven. | Whirlpool | WFE515S0JS4 |  | Condo | Kitchen | Yes | No |  | Yes |  | Mark Thibault | Unknown |  | 1350110405
2025-06-03 08:55 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | mass | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Poles | Schneider Electric | Residence |  | 2025-05-15 | 2025-05-13 | 660 Main St. |  | Worcester | mass |  | Apt 216¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | Yes | No |  | No |  | Sean Matthies | Unknown |  | 1350110406
2025-06-03 08:55 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | mass | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Poles | Schneider Electric | Residence |  | 2025-05-15 | 2025-05-13 | 660 Main St. |  | Worcester | mass |  | Apt 316¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | Yes | No |  | No |  | Sean Matthies | Unknown |  | 1350110407
2025-06-03 08:55 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | mass | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Poles | Schneider Electric | Residence |  | 2025-05-15 | 2025-05-13 | 660 Main St. |  | Worcester | mass |  | Apt 416¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | Yes | No |  | No |  | Sean Matthies | Unknown |  | 1350110408
2025-06-03 08:55 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | mass | 2076 | 5082977700 | Foreman | matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Poles | Schneider Electric | Residence |  | 2025-05-15 | 2025-05-13 | 660 Main St. |  | Worcester | mass |  | Apt 516¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | Yes | No |  | No |  | Sean Matthies | Unknown |  | 1350110409
2025-06-03 08:55 | Sean | Matthies | 23034 | 1667 Central St. |  | Stoughton | MA | 2076 | 5082977700 | Foreman | Matthiesnec@gmail.com | HOM240GFIC | Breaker | na | 40 | na | 2 Poles | Schneider Electric | Residence |  | 2025-05-15 | 2025-05-13 | 660 Main St. |  | Worcester | mass |  | Apt 616¦Oven portion cannot be used without tripping breaker. Have contacted GE before and they have stated it is a known issue with their stoves and they cannot fix it. | GE | RAS240DM3WW | na | Apartment | Kitchen | Yes | No |  | No |  | Sean Matthies | Unknown |  | 1350110410
2025-06-03 08:55 | Rami | Daaboul | 53597 | 33 verndale st |  | Brookline | Ma | 2446 | 7816908520 | Electrician | ramidaaboul@gmail.com | Lb250-gf 50 amp 2 - pole | Breaker |  | 50 |  | 2 Poles | Leviton | Residence |  | 2025-04-24 | 2025-04-24 | [5 empty] | Instantaneously when unit is on | Wolf | ir36550/s/t |  | Home | kitchen oven | Yes | No |  | Yes |  | Rami daaboul | Unknown |  | 1350110411
2025-06-03 10:05 | John | Novello | 12791 | 167 Winn St |  | Woburn | MA | 01801-2860 | 9782837348 | Electrician | john.novello@gmail.com | QF250A Siemens | Breaker | QF250A Siemens | 50 |  | 2 Pole | Siemens | Residence |  | 2025-06-03 | 2025-03-11 | 217 Walnut St. |  | Reading | ME |  | Pre-existing oven was re-wired with a 6/3 NM cable with ground and a new 4-wire cord was installed on the oven. Appliance ran uninterrupted until the end of last month. | Maytag | mer7662ww | dedicated circuit | Single family home | Kitchen oven | Yes | No | Yes | Yes | https://www.formstack.com/admin/download/file/18081545845 | https://www.formstack.com/admin/download/file/18081545846 | Firefox 138.0 / Windows | 73.89.12.51 | 1350133807 | 42.481, -71.1563
2025-06-03 10:59 | Mark | Raposo | 20105 | 20 Charles Joseph Drive |  | Dartmouth | MA | 2747 | 5089859555 | master electrician | tiffany@raposoelectricinc.com | QF250A | Breaker | QPF | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/18081845083 | 2025-05-30 | 2025-05-30 | 4 Maxim Road |  | Rochester | MA | 2770 | During the installation of a new overhead service a emergency disconnect was installed which necessitated the use of SER cable. Therefore the existing three wire range receptacle was updated to a four wire type and the breaker was updated to a GFCI type. After the update the breaker tripped instantly upon power up. Troubleshooting confirmed a likely internal connection between the ground and ungrounded conductors inside of the factory wiring. | whirlpool | GR450LXHB | NONE | DWELLING KITCHEN | KITCHEN ¦¦¦¦¦ | No | No | No | No |  | https://www.formstack.com/admin/download/file/18081845097 | Chrome 136.0.0.0 / Windows | 73.126.152.201 | 1350154431 | 41.6339, -70.9406
2025-06-03 14:28 | Christine | Hagist | 60582 | 726 Crane Ave |  | Pittsfield | MA | 1201 | 4134858510 | Electrician | christine.miller@trinity-solar.com | Hom240gfci | Breaker | 2 pole | 40 |  | 2 Pole | Schneider Electric | Residence | https://www.formstack.com/admin/download/file/18083219706 | 2025-06-03 | 2025-06-03 | [5 empty] | Breaker tripped when we tried to turn on oven | GE | JB256DM3BB | None | Single family | Kitchen | No | No | No | No | https://www.formstack.com/admin/download/file/18083219719 | https://www.formstack.com/admin/download/file/18083219720 | Mobile Safari 17.5 / iOS | 174.242.138.214 | 1350242844 | 41.667, -72.5968
2025-06-03 18:48 | ryan | pigott | 56365 | 32 syracuse road |  | Nashua | NH | 3064 | 7815074390 | owner | rpelectrical22@gmail.com | seimens | Breaker | 2 pole 50 | 50 |  | 2 Pole | Siemens | Residence |  | 2025-05-29 | 2025-06-03 | 38 a brentwood road |  | WOBURN | MA | 1801 | oven gets too mid heat and trips gfci | ge spectra | JBP24BY1AD |  | SINGLE FAMILY HOME | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18084551212 | Chrome 134.0.0.0 / Windows | 76.24.76.97 | 1350329464 | 42.724, -71.479
2025-06-05 05:58 | Jason | Curran | 21794 | 117 Channing Road |  | Concord | MA | 1742 | 617-460-1150 | Master Electrician | jasoncurranelectrician@gmail.com | Eaton | Breaker | GFCI 2 pole 50 | 50 |  | 2 Pole | Eaton | Residence |  | 2025-05-22 | 2025-05-22 | 117 Channing Road |  | Concord | MA | 1742 | Range trips off after short periods of sitting. | Bosch | HIS8055U/05 | n/a | Residential | In-law kitchen. | Yes | No | Yes | No |  | https://www.formstack.com/admin/download/file/18090913775 | Chrome 135.0.0.0 / OS X | 71.10.248.177 | 1350761676 | 42.0509, -71.7543
2025-06-05 10:58 | Steven | Rooney | 50969 | 401 South Street |  | Marlborough | MA | 1752 | 5084813299 | Service manager | Steven@Giombettielectric.com | BR 2p50 GFI | Breaker | N/A | 50 |  | 2 Pole | Eaton | Residence |  | 2025-06-04 | 2025-06-04 | 14C unit 04 Mayberry Drive |  | Westborough | ME | 1581 | breaker would not hold with older stove | whirlpool | AER5630BAWO |  | apartment style condo | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18091945277 | Chrome 137.0.0.0 / Windows | 98.118.122.8 | 1350843535 | 42.5301, -71.7553
2025-06-09 17:14 | Cal | Harvey | 14426 | 5 Oxbow Road | Pleasant Street | Raynham | MA | 2767 | 5086500650 | Assistant Project Manager | cal.harvey@thorndikedevelopment.com | BRN250GF | Breaker | BR | 50 |  | 2 Pole | Eaton | Residence |  | 2025-06-09 | 2025-06-09 | [5 empty] | Range, dryer causing breaker to trip | GE | GRF500PVSS |  | Townhome | Kitchen, laundry room | No | No | No | No |  | https://www.formstack.com/admin/download/file/18106631218 | Chrome 136.0.0.0 / Windows | 71.162.115.107 | 1351898455 | 42.5945, -71.3571
2025-06-09 19:02 | Steve | Laurencio | 18079 | PO Box 645 |  | Bedford | MA | 1730 | 978 621-7221 | Electrician | steve@desousaelectric.com | SquareDHomeLine/HOM250GFCICP | Breaker | 0 | 50 |  | 2 Pole | Schneider Electric | Residence |  | 2025-06-09 | 2025-06-06 | 17 Caribou |  | Bedford | MA | 1730 | Stove tripped circuit breaker after a few minutes on baking cycle. | Electrolux/ Frigidaire | FGIH3047VFE |  | Single Family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18107059850 | Chrome 137.0.0.0 / Windows | 100.17.24.219 | 1351927064 | 42.4881, -71.2758
2025-06-09 19:46 | Steve | Laurencio | 18079 | PO Box 645 |  | Bedford | MA | 1730 | 978 621-7221 | Electrician | steve@desousaelectric.com | Siemens QF250A | Breaker | 0 | 50 |  | 2 Pole | Siemens | Residence |  | 2025-06-09 | 2025-06-09 | 56 Throne Hill Rd. |  | Groton | MA | 1450 | Stove tripped circuit breaker on Bake cycle after a few minutes. | General Electric. | JB258RM1SS |  | Single family | Kitchen. | No | No | No | No |  | https://www.formstack.com/admin/download/file/18107195193 | Chrome 137.0.0.0 / Windows | 100.17.24.219 | 1351935877 | 42.4881, -71.2758
2025-06-09 20:00 | Steve | Laurencio | 18079 | PO Box 645 |  | Bedford | MA | 1730 | 978 621-7221 | Electrician | steve@desousaelectric.com | SquareD HOM220GFIC | Breaker | 0 | 20 |  | 2 Pole | Schneider Electric | Residence |  | 2025-01-13 | 2024-12-23 | 31 Kilburn |  | Belmont | MA | 2478 | Induction cooktop tripped circuit breakers when in use. | Wolf | CI152TF/S |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18107239034 | Chrome 137.0.0.0 / Windows | 100.17.24.219 | 1351938740 | 42.4881, -71.2758
2025-06-10 11:48 | Ryan | Barry | 21833 | PO Box 324 |  | Wakefield | MA | 1880 | 781-589-7437 | Master Electrician | kristin@bestsvs.com | LB220-323-00G | Breaker | 0 | 20 |  | 2 Pole | Leviton | Residence |  | 2025-05-27 | 2025-05-27 | 22 Rodgers Road |  | Stoneham | MA | 2180 | When the oven is turned on it trips shortly after intermittently.¦ | Cafe | CTS70DP2N5S1 |  | Oven in Kitchen | Oven in kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18109694628 | Chrome 137.0.0.0 / Windows | 100.0.110.222 | 1352106011 | 42.4945, -71.0715
2025-06-10 16:46 | John | Cabral | 32066 | 69 Callender St. |  | Dorchester | MA | 2124 | 6179082795 | Sole Proprietor | jp4c@hotmail.com | Siemens QFGA2 | Breaker | None | 20 |  | 1 Pole | Siemens | Residence |  | 2025-06-08 | 2025-06-01 | 12 Kinnaird |  | Cambridge | MA | 2139 | Fridge runs about an hour than trips gfci breaker. | Bosh | B36CT80SN |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18111358864 | Chrome 137.0.0.0 / Windows | 174.196.200.201 | 1352217185 | 42.3474, -71.1582
2025-06-10 16:57 | John | Cabral | 32066 | 69 Callender St. |  | Dorchester | MA | 2124 | 6179082795 | Sole Proprietor | jp4c@hotmail.com | Siemens QFGA2 | Breaker | None | 20 |  | 1 Pole | Siemens | Residence |  | 2025-06-08 | 2025-06-01 | 12 Kinnaird |  | Cambridge | MA | 2139 | When you plug in microwave than trips gfci breaker. | Sharp | KB6524PSYG |  | Single family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18111418040 | Chrome 137.0.0.0 / Windows | 174.196.200.201 | 1352221142 | 42.3474, -71.1582
2025-06-10 20:19 | Todd | Stone | 11167 | 83 Darrow Street |  | Quincy | MA | 2169 | 6176997528 | Owner/President | acmestoneelectric@gmail.com | Siemens QF250A | Breaker | 50AMP 2 pole breaker pig tale neutral | 50 |  | 2 Pole | Siemens | Residence |  | 2025-06-02 | 2025-06-09 | 12 May Elm Lane |  | Norwell | MA | 2061 | Once circuit is connected to stove/oven unit it automatically trips. Holds with no load. No neutral or ground bars bonded internally. Oven/stove is a bosch model number HIS8655U. | Bosch | HIS8655U | No | Single family Dwelling | Kitchen Only¦¦I cannot download the video or nameplate photo I took on my phone, ¦Nameplate¦HIS8655U/07 fd 0410 serial 002419¦Type NAINC3x¦UL STD 858¦120/208v - 10.8 kW¦120/240v - 12.8 kW | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/18112174215 | Chrome 136.0.0.0 / OS X | 174.168.140.94 | 1352273098 | 42.2463, -70.9972
2025-06-11 09:32 | Tyler | Daniels | 1971 | 895 Salem St-2A |  | Groveland | MA | 1834 | 9783731393 | Electrician | office@danielsel.com | Eaton | Breaker | NA |  |  | 2 Pole | Eaton | Residence |  | 2025-05-28 | 2025-05-28 | 3 Boston Way Apt 104 |  |  |  |  | Continually tripping | GE | JB645EK9ES |  | Apartment | Kitchen stove | No | No | No | No |  | https://www.formstack.com/admin/download/file/18113833586 | Chrome 137.0.0.0 / Windows | 50.187.12.233 | 1352385880 | 42.3725, -71.1814
2025-06-11 17:52 | Jeff | McLaughlin | 12014 | 3 Ross Circle |  | Assonet | MA | 2702 | 7742977436 | Owner | jmclaughlin3@comcast.net | LB240GF | Breaker | Breaker | 40 |  | 2 Pole | Leviton | Residence |  | 2025-05-28 | 2025-05-28 | 33 Turner St |  | Norfolk | MA | 2056 | Wall oven trips breaker when turned on. Cannot get breaker to hold. | Bosch | HBLP651RUC/01 |  | Dwelling | Kitchen Wall oven | No | No | Yes | No |  | https://www.formstack.com/admin/download/file/18116527505 | Chrome 137.0.0.0 / Windows | 73.126.60.81 | 1352565471 | 42.1237, -71.1787
2025-06-12 12:17 | Thai | Nguyen | 53264 | 10 Ashland Street |  | Quincy | MA | 2169 | 617-309-8804 | President | bostonnguyenelectric@gmail.com | Eaton | Breaker | 40 | 40 |  | 2 Pole | Eaton | Residence |  | 2025-06-10 | 2025-06-12 | 128A Sewall AvenueA |  | Brookline | MA | 2446 | When the Eaton GFCI 40 breaker was installed it kept tripping the Kitchen AID duaL MICROWAVE AND oven. We contacted the KitchenAid manufacturer aND THEY DON'T MAKE The GFCI breaker with the 20 kiklovolts spec yet. This is is a common issue with not KichenAid but many other appliance brands. | KitchenAid | KitchenAid KOCE 500ESS11 Serial no. DA 2002142 | No. | Condominium | Just the kitchen microwave/oven. | No | No | Yes | Yes |  | https://www.formstack.com/admin/download/file/18119521259 | Chrome 136.0.0.0 / OS X | 24.61.62.230 | 1352797950 | 42.2904, -71.0712
2025-06-13 15:25 | Albert | Carbone | 4434 | 67 Maplewood |  | Marlborough | MA | 1752 | 732-780-3779 | Electrician | david.n1tqp@gmail.com | Seimens QF250A | Breaker | GFCI |  |  | 2 Pole | Siemens | Residence |  | 2025-06-13 | 2025-06-13 | [5 empty] | Instantly trips. | GE | Jb655ek4es | Na | Two family | Kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18125459694 | Mobile Safari 18.5 / iOS | 73.47.53.154 | 1353215866 | 42.1139, -72.5508
2025-06-15 14:53 | Jesse | Kuhlman | 21804 | 313 Eastern Avenue | 46-4305562 | Lynn | MA | 1902 | 6178406252 | owner | ervis.kes@gmail.com | Model # HOM240GFIC | Breaker | none | 40 |  | 2 Pole | Schneider Electric | Residence |  | 2025-06-06 | 2025-06-05 | 415A Dedham |  | Newton | MA | 2459 | The breaker tripped about a minute after the oven was on. | Electrolux | EW30IF60ISB | no | single family | kitchen | No | No | No | No |  | https://www.formstack.com/admin/download/file/18129567623 | Chrome 137.0.0.0 / Windows | 209.6.193.104 | 1353543627 | 42.415, -71.0527
2025-06-16 06:45 | Andrew | Gallione | 8490 | 10 Rainbow Terrace | Unit F | Danvers | MA | 1923 | 9789980414 | Manager | andrewg@nstelectric.com | Q120DF | Breaker | Duel Function | 20 |  | 1 Pole | Siemens | Residence |  | 2025-06-10 | 2025-03-10 | 32 Orleans St |  | East Boston | MA | 2128 | Oven tripping AF/GFCI circuit breaker during the pre-heating process. | Electrolux Home Products | FCFG3083ASA |  | Residential | Kitchen appliance | No | No | Yes | Yes | https://www.formstack.com/admin/download/file/18131236583 | https://www.formstack.com/admin/download/file/18131236584 | Chrome Mobile 137.0.7151.107 / iOS | 166.198.21.10 | 1353669164 | 42.2904, -71.0712
2025-06-16 08:54 | Hector | Montanez | 13674 | 4 Meaders Lane |  | Salisbury | MA | 1952 | 9789942695 | Owner, Installer and service technician | Hmelectric@linewire.net | ITE QF250A | Breaker | 2 Pole 50 Amp | 50 |  | 2 Pole | Siemens | Residence | https://www.formstack.com/admin/download/file/18131560448 | 2025-06-02 | 2025-05-14 |  |  | 6 Felton Lane | MA | 1985 | I was Informed by the homeowner that the Range circuit breaker tripped, mainly while using the oven. Since the Install the breaker has tripped several times. I verified all the connections In the main panel, the surface mount receptacle and on the appliance, which everything checked out. During my visit there I turned the oven On and left it On for ten minutes, doing so didn't cause the breaker to trip. The home owner stated the breaker would had tripped in half that time. Please let me know if there's anything else you need for me to do. ¦ | Whirlpool | KSEG700ESS3 |  | Residential Kitchen | Dedicated circuit to Kitchen range. | No | Yes | No | No |  | https://www.formstack.com/admin/download/file/18131560464 | Chrome 137.0.0.0 / Windows | 73.123.157.201 | 1353693389 | 42.8539, -70.9397
2025-06-17 | Albert | Pierucci | 14951B |  |  | Randolph |  |  | 7814432511 | Journeyman | alpierucci22@gmail.com | Leviton 50 amp 2 pole gfci breaker, LB250-G | Breaker |  | 50 |  | 2 Poles | Leviton | Residence |  | 2025-05-14 | 2025-05-14 | 33 foley beach RD |  | Hingham | MA | 2018 | Direct trip when put on to power up the range | Signature kitchen suite | SKSCV3002S |  | Kitchen | Only kitchen | No | Yes |  | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F06%2FIMG_1926.png&form-id=2&field-id=42&hash=11dc5a6bae410763da40b7a7f5d9ceb60081825f16abe64405957e2d31df64e0 | Albert Pierucci | Unknown |  | 1360878483
2025-06-17 | Mark | Thibault | 14667 |  |  | Tyngsboro |  |  | 9782265946 | President | mark@stelectrical.net | Schneider Electric | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-05-26 | 2025-05-27 | 6305 Peters Farm Way |  | Westborough | MA | 1581 | When warming up the oven | Whirlpool | WFE535S0LS3 |  | Condo | Kitchen | Yes | No |  | Yes |  | Mark Thibault | Unknown |  | 1360878484
2025-06-18 | Michael | Gannon | 40499e |  |  | Boston |  |  | 617 2936429 | Electrician | gannonm317@gmail.com | GE | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-05-27 | 2025-05-27 | 167 Nehoiden rd |  | newton | MA | 2468 | breaker would not hold when turned on kept tripping | wolf | C136560T/S | none | single family home | induction cooktop in kitchen | No | Yes |  | No |  | Michael Gannon | Unknown |  | 1360878481
2025-06-18 | Scott | Stevens | A16505 |  |  | Worcester |  |  | 5088299889 | Electrician | wireguyscott@gmail.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-20 | 23 Deer Path | Unit 7 | Maynard | MA | 1754 | The GFCI breaker trips when the convection portion of the oven is activated. | GE | PHS930BP | N/A | Multi unit townhouse | Kitchen | No | No |  | No |  | Scott Stevens | Unknown |  | 1360878482
2025-06-19 | Cole | Powers | 18122 |  |  | Vineyard Haven |  |  | 5086966400 ext. 101 | President | powerselectric@comcast.net | QO240GFI | Breaker | Circuit Breaker | 40 | 40 | 2 Poles | Schneider Electric | Residence |  | 2025-06-13 | 2025-01-04 | 20 Jennie Lane |  | Edgartown | Massachusetts | 2539 | The oven tripped the breaker. | Bosch | HBLP651LUC/09 | No | Single-Family House | Kitchen | No | No |  | No |  | Cole Powers | Unknown |  | 1360878479
2025-06-20 | Patrick | JOYCE | 20627-A |  |  | PRINCETON |  |  | 9784231582 | OWNER | PMJELECTRIC@GMAIL.COM | SIEMANS QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-06-07 | 2025-02-04 | 56 Morency St Unit 93 |  | Natick | Ma | 1760 | When the oven is turned to pre heat the breaker tripped. Also occurs periodically when the broiler is turned on. Breaker has been replaced with a new 2-pole 50-amp GFCI breaker and problem still occurs. | FRIGIDAIRE GALLEREY | LGEF3043KFK |  | Condo | Kitchen stove | No | No |  | No |  | Patrick M Joyce | Unknown |  | 1360878477
2025-06-20 | Nathan | Ploughman | 2207A1 |  |  | Walpole |  |  | 8603775199 | Project Executive | nploughman@baldhillbuilders.com | Eaton GFTCB250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-03 | 2025-03-11 | 1599 Columbus Ave |  | Roxbury | MA | 2119 | When oven heats up over 350 degrees, the GFCI Trips. This is happening consistently with the GFCI breakers installed above in the 65 residential units. | Whirlpool | WFES3030RS | None | Kitchen | 65 unit multifamily project. All 65 units kitchen ovens have consistent issue as outlined within. | Yes | No |  | Yes |  | Nathan Ploughman | Unknown |  | 1360878478
2025-06-24 | Steve | Laurencio | 18079 |  |  | Bedford |  |  | 978 621-7221 | Electrican | steve@desousaelectric.com | QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-06-17 | 2025-06-03 | 19 Chicory |  | Westford | Ma | 1886 | Oven Tripped GFCI on baking setting. | Frigidaire | GCF13060BFC | No | Single family | Kitchen | No | No |  | No |  | Steve Laurencio | Unknown |  | 1360878475
2025-06-24 | Steve | Laurencio | 18079 |  |  | Bedford |  |  | 978 621-7221 | Electrician | steve@desousaelectric.com | Q230GF | Breaker |  | 30 |  | 2 Poles | Siemens | Residence |  | 2025-06-24 | 2025-06-21 | 37 Pickman Rd. |  | Bedford | Ma | 1730 | Oven tripped on baking setting. | Thermador | MED301RWS/05 | no | Single family | Kitchen oven. | No | No |  | No |  | Steve Laurencio | Unknown |  | 1360878476
2025-06-25 | Gilligan | Alan | 1126-96 |  |  | Quincy |  |  | 6172932562 | Owner | alangilliganelectric@hotmail.com | Siemens ak45eool. A50 | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-06-20 | 2025-06-20 | Garage | 6. Henry's lane | Norwell | Ma | 2161 | Breaker trips instantly when connected to cooktop. | Wolf | C1365c | No | Single family | Kitchen | No | No |  | No |  | Alan gilligan | Unknown |  | 1360878474
2025-06-26 | Philips | Electric | Philip Mendonca |  |  | Arlington |  |  | 6178885434 | Electrician | philipselectric@gmail.com | sqaure d QO250GFIC | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-06-26 | 2025-05-24 | 7 Hadley Rd, |  | Lexington | MA | 2420 | tripping breaker after stove is running | Bosch | h118057u/06 |  | kitchen | kitchen | No | No |  | No |  | pm | Unknown |  | 1360878473
2025-06-30 | Cal | Harvey | 14426 |  |  | Raynham |  |  | 7816974950 | Assistant Project Manager | cal.harvey@thorndikedevelopment.com | BRN250GF | Breaker | BR | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2024-11-12 | [5 empty] | Range causes breaker to trip repeatedly | General Electric | GE CafÃ© Electric Range CHS900P2MS1 |  | Townhome | Kitchen | No | No |  | No |  | Cal Harvey | Unknown |  | 1360878471
2025-06-30 | Ryan | LaBrache | 22040A |  |  | Watertown |  |  | 617-538-4851 | Owner | ryan@lampasonabloomer.com | QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-06-19 | 2025-06-17 | 62 Fayerweather St |  | Cambridge | MA | 2138 | Breaker would trip instantly when running the stove | AGA | AEL361IN |  | single family | Kitchen | No | Yes |  | No |  | Ryan LaBrache | Unknown |  | 1360878472
2025-07-01 | Qui | Phan | 56163-B | 24 Palmer Street |  | Quincy | MA | 2169 | 6176526431 | Journeyman Electrician | qpphan87@gmail.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_5388.webp&form-id=2&field-id=22&hash=0c12bc9d557882bafaf094e7b35c6999b16f7f626d456a6ffc81f62ceb509d24 | 2025-06-24 | 2025-04-02 | 192 Mason Terrace |  | Brookline | MA | 2446 | United States | The moment the stove was installed with the bonded tab (ground and nuetral) removed and plugged in, it tripped the Siemens Type BR GFCI 50amp 2-pole breaker. There are no shorts and/or ground faults after testing with a multimeter. | Cafe Smart Appliances | CHS900P4MW2 | None | Kitchen | Only stove that is on a dedicated circuit that was affected. | No | Yes | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_5385.jpeg&form-id=2&field-id=42&hash=e2bbdbb775625c505a0646b68d056ef06ef9db078c7129ca22b094026b5c429b | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Qui Phu Phan
2025-07-02 | Cal | Harvey | 14426 | 21 Oxbow Road |  | Raynham | Massachusetts | 2767 | 5086500650 | Assistant Project Manager | cal.harvey@thorndikedevelopment.com | BRN250GF | Breaker | BR | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-02 | 2025-06-02 | [6 empty] | Range causing breaker to trip repeatedly | General Electric | GRF500PVSS |  | Townhome | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Cal Harvey
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 242 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 242 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 241 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 241 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 240 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 240 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 239 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 239 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 237 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 237 | Yes | No | No | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 236 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 236 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 235 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 235 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 234 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 234 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-25 | 2025-04-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 233 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 233 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 232 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 232 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-09 | 2025-06-09 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 231 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 231 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-18 | 2025-06-18 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 230 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 230 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 229 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 229 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 228 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 228 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 227 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 227 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-31 | 2025-03-31 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 225 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 225 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 223 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 223 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 221 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 221 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 220 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 220 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-14 | 2025-03-14 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 219 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 219 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-27 | 2025-06-27 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 134 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 134 | Yes | No | No | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-02 | Daniel | Greenberg | 54913 B | 06 Metacomet Rd | Norfolk Ave. | West Bridgewater | MA | 2379 | 7812647746 | Site Supervisor | Dgreenberg@stonebridgehomesinc.com | DP-4075 | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2Fthumbnail_IMG_4447.jpg&form-id=2&field-id=22&hash=025db6964c0a56689bd9bdc7e89aa4c7e562f32e9b3d1b37ee4a169ffb8833ba | 2025-06-27 | 2025-07-22 | [6 empty] | Every time the oven is turned on, the breaker trips. | Frigidaire | GCRE306CBFD | none | Single Family Home | Kitchen only | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2Fthumbnail_IMG_0404.jpg&form-id=2&field-id=42&hash=1ba77c8dcc924b1b84df2df56ca187152b090da37e41829143ea6a00f37ca983 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Daniel M. Greenberg
2025-07-02 | Douglas | Lynch | 11933 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-09 | 2025-04-09 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 133 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 133 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-03 | 2025-06-03 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 342 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 342 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 341 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 341 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 340 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 340 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 339 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 339 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 337 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 337 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 336 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 336 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 336 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 336 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 335 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WOES5030L2 |  | Apartment building | Kitchen in unit 335 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 334 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 334 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 333 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 333 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 332 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 332 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 331 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 331 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 330 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 330 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 329 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 329 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 328 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 328 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-05-01 | 2025-05-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 327 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 327 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-05-16 | 2025-05-16 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 325 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 325 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-17 | 2025-04-17 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 323 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 323 | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 321 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 321 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-09 | 2025-06-09 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 320 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 320 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-03 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-31 | 2025-05-31 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 319 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 319 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-04 | Peter | Henault | 34546E | 30 Bay Road |  | Eastham | 2651 | MA | 5082370278 | Owner | petesadds@gmail.com | Square D. QO250GFCI | Breaker |  | 50 | 240 | 2 Poles | Industrial | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2Fimage.jpg&form-id=2&field-id=22&hash=5d6df8961f93ca98bc04d2331ca7adb6824453d8772eca7f5dd65137fbf29fe8 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2Fimage1.jpg&form-id=2&field-id=22&hash=f0622ae0ddf042f8fed4ee7d525e2b602f921c6e1fff3f49e7927a11199f9a28 | 2025-07-02 | 2025-06-13 | 65 Harmes Way | 65 Harmes Way |  | North Eastham | MA | United States | The stove once plug in traps the GFCI breaker. | Viking | VIR53626BSSBB00 | None | Home residence | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2Fimage2.jpg&form-id=2&field-id=42&hash=ca924139af27d58f4854769b93a9ac4ee6341646b29e19072cbdc0b57c4853fb | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Peter Henault
2025-07-06 | Timothy | Pytal | E39163 | 86 Bayview Street |  | Chatham | MA | 2633 | 2018882865 | Homeowner | Timothy.Pytal@gmail.com | Legrand / 1597TRW | Receptacle |  | 15 |  | 1 Pole | Legrand | Residence |  | 2025-06-06 | 2025-05-06 | [6 empty] | The GFI outlet trips when the refrigerator compressor starts. The manufacturer sent a technician who confirmed the fridge works properly and identified the issue as the GFI outlet. | Thermador | T36IB905SP / 39 | None | Single Family House | Only the kitchen room affected where the refrigerator is located. | No | Yes | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FInstall.pdf&form-id=2&field-id=42&hash=ea3919400d70f3cec983655bb490e2dbe668f0c86c3f907be3027fa6ba453c5e , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FNameplate.pdf&form-id=2&field-id=42&hash=028f035cba997992384fb2fd9f9fc6422d7335aefd1d1adfc4fac7d05d713ff0 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Timothy Pytal
2025-07-07 | Scott | Haynes | E39328 | 18 Maddie Way |  | Bellingham | MA | 2019 | 5089226557 | Owner | scottmhaynes@comcast.net | QF250AP | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-07-03 | 2025-07-02 | 13 Patrick Road |  | Hopedale | Ma | 1747 | United States | GFI trips every time you preheat the oven. | Frigidaire | 6CFI3060BFD |  | Single Family | Kitchen | No | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FRange-B.jpeg&form-id=2&field-id=42&hash=eaad840818c9664d6f86179a3e911f76e02896889ad8daac4a01b408d074f11b , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FRange-A.jpeg&form-id=2&field-id=42&hash=22d1332c818751adfeb969b79a3c9897883028dd4f7dbfd7f834ea1bacd592a3 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Scott M Haynes
2025-07-07 | Curtis | Capra | 57632-b | 59 pond view dr |  | Centerville | Ma | 2632 | 7742050160 | Electrician | curtiscapra@gmail.com | Q230gf | Breaker |  | 30 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2Fimage3.jpg&form-id=2&field-id=22&hash=35c2cbe7815de0433e86a5fd448e7f92809becc90d502d269f3731af5112d936 | 2025-05-29 | 2025-05-28 | 101 Southgate dr |  | Hyannis | Ma | 2601 | United States | Installed Gfci breaker per code, Gfci holds on dry cycle for about 30 mins then trips, had KAM appliances out several times to check dryer wasn’t able to find anything wrong with dryer or cord , I also changed the breaker with another new Gfci and had same results. | Maytag | Md3906690 |  | Residential | Mud room/laundry just the dryer circuit. | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2Fimage4.jpg&form-id=2&field-id=42&hash=d2493e19cc691748effb77780f7d4011b8e1593de893085e2f024e13ff4af733 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Curtis capra
2025-07-08 | Michael | Giombetti | A13678 / Giombetti Electric, Inc. | 401 SOUTH STREET | Marlboro | Marlborough MA 01752 | MA | 1752 | 5084813299 | President | Mike@giombettielectric.com | GE THQL2140GFT | Breaker |  | 40 |  | 2 Poles | ABB | Residence |  | 2025-07-03 | 2025-07-03 | 1610 Worcester Road | Apartment 248 | Framingham | MA | 1702 |  | The breaker will trip while using the oven. | GE | JB258RT4SS | None | Apartment | Kitchen Stove | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_7409.jpg&form-id=2&field-id=42&hash=e88b44fa78e33b5a3dbea815958deac5234894697898c8d98cda7d4d3c2e4a9c | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Michael A Giombetti
2025-07-09 | Jonathan | Tomasi | 100858 | 65 avco road |  | haverhill | ma | 1835 | 9782043941 | foreman/supervisor | jtomasi92@yahoo.com | qbgfep2020 | Breaker |  | 20 |  | 2 Poles | Eaton | Industrial |  | 2025-07-07 | 2025-07-01 | 117 water street |  | lawrence | massachusetts | 1841 | United States | Circuit breaker trips immediately when unit is plugged into the receptacle. Circuit breaker holds and remains energized when no equipment load in plugged in. Transformer for controls in the machine are powered by a transformer which is bonded to the frame which I believe may be causing the issue. | Rational | icombi pro20 | no other equioment on circuit | production kitchen | production kitchen | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jonathan Tomasi
2025-07-09 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 430 was tripping the old breaker (BRN230GF), we replaced breaker to an Eaton BR230 and a ground leakage test to confirm breaker functionality | Whirlpool | WOES5030L2 |  | Apartment building | Kitchen in unit 430 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-09 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 425 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 425 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-09 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 429 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 429 | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-09 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 425 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 425 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-09 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 423 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 423 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-09 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 421 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 421 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-09 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 420 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 420 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-09 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-20 | 2025-06-20 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 419 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 419 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-09 | Daniel | Henderson | 14075 | 1 Tyson Rd |  | South Easton | MA | 2375 | 5083699986 | Owner | dan@danielhendersonelectric.com | Thql1120df | Breaker |  | 20 |  | 1 Pole | Schneider Electric | Residence |  | 2025-07-05 | 2025-07-01 | 1264 beacon st unit 5 |  | Brookline | MA | 2446 | United States | Dryer trips constantly after 10 minutes | Miele | Wxd160 | No | Multi family | Laundry closet in hallway | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_8523.jpeg&form-id=2&field-id=42&hash=cda61e44c64e4468a286123a0f16a237f9f8178d0462207a44a0c8b961bf7782 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_85241.jpeg&form-id=2&field-id=42&hash=bfa6ff5d426ba30d109b5217765b505a8d5eec8fa161f6113eca43bd93b81519 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Daniel Henderson
2025-07-09 | Daniel | Henderson | 14075 | 1 Tyson Rd |  | South Easton | MA | 2375 | 5083699986 | Owner | dan@danielhendersonelectric.com | Ge thql1120df | Breaker |  | 20 |  | 1 Pole | Schneider Electric | Residence |  | 2025-07-02 | 2025-06-01 | 1264 beacon st unit 5 |  | Brookline | MA | 2446 | United States | Washer trips consistantly after 10 minutes. | Miele | Txd160wp | No | Multi family | Laundry closet in hallway | No | No | No | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_8522.jpeg&form-id=2&field-id=42&hash=380dcf814f9778624caea3f6ba14a467f9cc2302d373af8fb49c1038ca5d01d9 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_8524.jpeg&form-id=2&field-id=42&hash=c6faa75f0560596a9cb966fc83dd13156fd0b3564b0b1edc0bd889e37cfc13e2 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Daniel Henderson
2025-07-10 | John | Sousa | 12911B | 8 Warren Street |  | Cambridge | MA | 2141 | 6178687734 | Electrician | john@maelectric.net | Siemens | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-06-26 | 2025-06-25 | Kitchen | 11Blackstone Unit #9 | Cambridge | MA | 2139 |  | Like all other ovens this keeps tripping on GFCI breaker every one we try. | GE | PTs9200SN3SS |  | Kitchen | The is so stupid | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Sousa
2025-07-10 | John | Sousa | 12911B | 8 Warren Street |  | Cambridge | MA | 2141 | 6178687734 | Electrician | john@maelectric.net | Siemens | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-06-26 | 2025-06-25 | Kitchen | 11Blackstone Unit #9 | Cambridge | MA | 2139 |  | Like all other ovens this keeps tripping on GFCI breaker every one we try. | GE | PTs9200SN3SS |  | Kitchen | Kitchen oven GFCI keeps tripping | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Sousa
2025-07-10 | John | Sousa | 12911B | 8 Warren Street |  | Cambridge | MA | 2141 | 6178687734 | Electrician | john@maelectric.net | Siemens | Breaker |  | 50 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_5333.heic_.pdf&form-id=2&field-id=22&hash=f38d3a80c6708991af9053222bd7c9584542e81912b1e2203bcf52f53531e895 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_5335.heic_.pdf&form-id=2&field-id=22&hash=a1252017b262c96a4359efd7e1fef4333dcfa9b89343f9f28536be1177408a11 | 2025-06-26 | 2025-06-25 | Kitchen | 11Blackstone Unit #9 | Cambridge | MA | 2139 |  | Like all other ovens this keeps tripping on GFCI breaker every one we try. | GE | PTs9200SN3SS |  | Kitchen | Kitchen oven GFCI keeps tripping | Yes | Yes | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_5335.heic_1.pdf&form-id=2&field-id=42&hash=5b28c580b4c38b2cb40892f307d32b0b1bf80be0f8d024dce98cec70c51a4b45 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_5333.heic_1.pdf&form-id=2&field-id=42&hash=4bcbc54b0b0ae8ca430bbdbd3a23ba80166fcd947b42ad8d15f0587b302b9934 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Sousa
2025-07-11 | Matthew | Holt | 2230 | 1 State Tree CIR | Breed Ave Unit F | Londonderry | New Hampshire | 3053 | 6037656746 | PM | mattholtsed@gmail.com | GFTCB250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-03 | 2025-07-10 | 100 Chestnut St |  | Ashland | Ma | 1721 | United States | Range Tripping Breaker | Whirlpool | WEE515S0LS3 |  | Apartment Unit #100-409 | Kitchen | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Matthew Holt
2025-07-11 | Matthew | Holt | 2230 | 1 State Tree CIR | Breed Ave Unit F | Londonderry | New Hampshire | 3053 | 6037656746 | PM | mattholtsed@gmail.com | GFTCB250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-03 | 2025-07-10 | 100 Chestnut St |  | Ashland | Ma | 1721 | United States | Range Tripping Breaker | Whirlpool | WEE515S0LS3 |  | Apartment Unit #100-407 | KItchen | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Matthew Holt
2025-07-11 | Matthew | Holt | 2230 | 1 State Tree CIR | Breed Ave Unit F | Londonderry | New Hampshire | 3053 | 6037656746 | PM | mattholtsed@gmail.com | GFTCB250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-03 | 2025-07-10 | 100 Chestnut St |  | Ashland | Ma | 1721 | United States | Range Tripping Breaker | Whirlpool | WEE515S0LS3 |  | Apartment Unit #100-214 | Kitchen | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Matthew Holt
2025-07-11 | Matthew | Holt | 2230 | 1 State Tree CIR | Breed Ave Unit F | Londonderry | New Hampshire | 3053 | 6037656746 | PM | mattholtsed@gmail.com | GFTCB250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-03 | 2025-07-10 | 100 Chestnut St |  | Ashland | Ma | 1721 | United States | Range Tripping Breaker | Whirlpool | WEE515S0LS3 |  | Apartment Unit #100-203 | Kitchen | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Matthew Holt
2025-07-11 | Matthew | Holt | 2230 | 1 State Tree CIR | Breed Ave Unit F | Londonderry | New Hampshire | 3053 | 6037656746 | PM | mattholtsed@gmail.com | Eaton GRTCB250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-03 | 2025-07-10 | 100 Chestnut St |  | Ashland | Ma | 1721 |  | Range tripping GFCI | Whirlpool | WEE515S0LS3 |  | Apartment Unit #100-201 | Kitchen | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Matthew Holt
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-17 | 2025-06-17 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 541 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WCE77USOHS01 |  | Apartment building | Kitchen in unit 541 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-26 | 2025-03-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 540 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 540 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-05-18 | 2025-05-18 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 539 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 539 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-23 | 2025-06-23 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 537 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 537 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-23 | 2025-06-23 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 536 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 536 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 535 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WOES5030L2 |  | Apartment building | Kitchen in unit 535 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-05-16 | 2025-05-16 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 534 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 534 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-14 | 2025-03-14 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 533 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 533 | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-23 | 2025-06-23 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 532 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 532 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 531 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 531 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-23 | 2025-06-23 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 530 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 530 | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-05-18 | 2025-05-18 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 529 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 529 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-23 | 2025-06-23 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 528 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 528 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-05-19 | 2025-05-19 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 527 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 527 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 525 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 525 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-23 | 2025-06-23 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 523 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 523 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-05-18 | 2025-05-18 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 521 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 521 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-05-18 | 2025-05-18 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 520 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 520 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-20 | 2025-06-20 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 519 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 519 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 442 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 442 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 437 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 437 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 436 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 436 | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-06-17 | 2025-06-17 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 435 was tripping the old breaker (BRN230GF), we replaced breaker to an Eaton BR230 and a ground leakage test to confirm breaker functionality | Whirlpool | WOES5030L2 |  | Apartment building | Kitchen in unit 435 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Jonathan | Tomasi | 100858 | 65 avco road |  | haverhill | ma | 1835 | 9783725877 | foreman/supervisor | jtomasi92@yahoo.com | qbgfep2020 | Breaker |  | 20 |  | 2 Poles | Eaton | Industrial |  | 2025-07-03 | 2025-07-03 | 117 water street |  | lawrence | massachusetts | 1841 | United States | Circuit breaker trips immediately when unit is plugged into the receptacle. Circuit breaker holds and remains energized when no equipment load is plugged in. Transformer for controls in the machine is bonded to the frame to generate 120v which I believe may be the reason for tripping. | rational | icombi pro20 | none | production kitchen | production kitchen | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | jonathan tomasi
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-06-18 | 2025-06-18 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 434 was tripping the old breaker (BRN230GF), we replaced breaker to an Eaton BR230 and a ground leakage test to confirm breaker functionality | Whirlpool | WEP560LHW2 |  | Apartment building | Kitchen in unit 434 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Jonathan | Tomasi | 100858 | 65 avco road |  | haverhill | ma | 1835 | 9782043941 | foreman / supervisor | jtomasi92@yahoo.com | qbgfep2020 | Breaker |  | 20 |  | 2 Poles | Eaton | Industrial |  | 2025-07-03 | 2025-07-03 | 117 water street |  | lawrence | massachusetts | 1841 | United States | Circuit breaker trips immediately when unit is plugged into the receptacle. Circuit breaker holds and remains energized when no equipment load is plugged in. Transformer for controls in the machine is bonded to the frame to generate 120v which I believe may be the reason for tripping. | rational | icombi pro20 | none | production kitchen | production kitchen | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | jonathan tomasi
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-27 | 2025-06-27 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 433 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 433 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Jonathan | Tomasi | 100858 | 65 avco road |  | haverhill | ma | 1835 | 9783725877 | foreman/ supervisor | jtomasi92@yahoo.com | qbgfep2020 | Breaker |  | 20 |  | 2 Poles | Eaton | Industrial |  | 2025-07-03 | 2025-07-03 | 117 water street |  | lawrence | massachusetts | 1841 | United States | Circuit breaker trips immediately when unit is plugged into the receptacle. Circuit breaker holds and remains energized when no equipment load is plugged in. Transformer for controls in the machine is bonded to the frame to generate 120v which I believe may be the reason for tripping. | rational | icombi pro20 | none | production kitchen | production kitchen | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | jonathan tomasi
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 432 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 432 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Jonathan | Tomasi | 100858 | 65 avco road |  | haverhill | ma | 1835 | 9783725877 | foreman/supervisor | jtomasi92@yahoo.com | qbgfep2020 | Breaker |  | 20 |  | 2 Poles | Eaton | Industrial |  | 2025-07-03 | 2025-07-03 | 117 water street |  | lawrence | massachusetts | 1841 | United States | Circuit breaker trips immediately when unit is plugged into the receptacle. Circuit breaker holds and remains energized when no equipment load is plugged in. Transformer for controls in the machine is bonded to the frame to generate 120v which I believe may be the reason for tripping. | rational | icombi pro 20 | none | production kitchen | production kitchen | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | jonathan tomasi
2025-07-11 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 431 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 431 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-11 | Jonathan | Tomasi | 100858 | 65 avco road |  | haverhill | ma | 1835 | 9783725877 | foreman/ supervisor | jtomasi92@yahoo.com | qbgfep2020 | Breaker |  | 20 |  | 2 Poles | Eaton | Industrial |  | 2025-07-03 | 2025-07-03 | 117 water street |  | lawrence | massachusetts | 1841 | United States | Circuit breaker trips immediately when unit is plugged into the receptacle. Circuit breaker holds and remains energized when no equipment load is plugged in. Transformer for controls in the machine is bonded to the frame to generate 120v which I believe may be the reason for tripping. | rational | icombi pro 20 | none | industrial kitchen | production kitchen | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | jonathan tomasi
2025-07-12 | Lukasz | Smugarzewski | 53580 | 22 Adeline st |  | Hampstead | NH | 3841 | 7816326274 | Electrician | Smugarzewski@gmail.com | Eaton | Breaker |  | 20 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | [6 empty] | Breaker trips when appliance is turned on. | Wolf | SPO30TE/S/TH |  | Single family home | Kitchen island appliance. | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Lukasz Smugarzewski
2025-07-14 | Greg | Mastroianni | 22544-A | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 413-739-3835 | Supervisor | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 347 Central St. APT 1 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15&#039; from the electrical panel. Install a new 4 wire receptacle and 40 amp breaker. Power up electric stove the breaker is working. Turn on heating elements for and it runs for about 30 seconds and the trips the gfci breaker. Tried this multiple times and each time it trips around 30-60 seconds from the heating elements being turned on. | Kenmore | RAS2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number.jpg&form-id=2&field-id=42&hash=ed732134094d513832a9dae80208fd3cf4822f6846a258b5208a3f7ed32c94dc | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-14 | Paul | Earnest | 57714-B | 117 Union Street | Unit 1 Front | Westfield | Ma | 1085 | 4134541513 | Lead Foreman/Journeyman | paul@electricalexperts.com | Leviton LB230-G | Breaker |  | 30 |  | 2 Poles | Leviton | Residence |  | 2025-07-08 | 2025-07-08 | 83 Adams Road |  | Haydenville | Ma | 1039 | United States | Instant trip on multiple breaker attempts | Kitchenaid | KCIG550JBL | None | Home | Cooktop for kitchen counter | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Paul Earnest
2025-07-15 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 347 Central St. APT 4 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RAS2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number3.jpg&form-id=2&field-id=42&hash=c52ce73ed56216d18b9cc0b59f4ae1b6c5f35ede0f4f35d88ad4aaf3e942cc7a | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-15 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 347 Central St. APT 3 |  | Springfield |  | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RAS2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number2.jpg&form-id=2&field-id=42&hash=29aa30724ef0005d67ea1c6129f4348fcac7bb3658b4afdaa3a633f810d24ef4 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-15 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 347 Central St. APT 2 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RAS2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number1.jpg&form-id=2&field-id=42&hash=892141e8bd2612ce5a94a99a1011962b766daade7a2ec377d6e51ba227d14b19 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-16 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 353 Central St. APT 16 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number15.jpg&form-id=2&field-id=42&hash=d395e1e88d0520a04d4091a5889f8ea9d514ee55b309eabd0b737fb3ff91dd82 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-16 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 353 Central St. APT 15 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number14.jpg&form-id=2&field-id=42&hash=430a7b6d37d01d160de00a403a84348399802467df165d4685c8742ba545c3fb | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-16 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 353 Central St. APT 14 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number13.jpg&form-id=2&field-id=42&hash=5a1027ff1606e243b9d79af87162d1bc5b03d8b3e92e43864babf722598f7b85 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-16 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 353 Central St. APT 13 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number12.jpg&form-id=2&field-id=42&hash=ec6f5b31540f68f950455e64d502a06e377a9da4155901fdd943724eb505a3f8 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-16 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 351 Central St. APT 12 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number11.jpg&form-id=2&field-id=42&hash=e31e40d69b8f3082733ea60e5088ff0a1a9b75146f096ad356d293b94d8d3a0f | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-16 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 351 Central St. APT 10 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number10.jpg&form-id=2&field-id=42&hash=1519a6a7d6515c808fd9a25e3d4d2b045ac91e234bc8543ed8707413e788f96a | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-16 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 351 Central St. APT 10 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number9.jpg&form-id=2&field-id=42&hash=dced27aaed522ec5c5838b52aceb35396ed18bef9d8393477ef4a7a6b62c69f0 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-16 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 351 Central St. APT 9 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number8.jpg&form-id=2&field-id=42&hash=34bd99b2638d61a8a7e4801c6ff978695dd4db11ab5a6ec14d3ece67a6f7d391 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-16 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 349 Central St. APT 8 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number7.jpg&form-id=2&field-id=42&hash=ece360d2640fcd177adbf4199320e566a7f561ff74c7954395e7079d543aac19 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-16 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 349 Central St. APT 7 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number6.jpg&form-id=2&field-id=42&hash=4a7d351dc67db5d465ff4207ac121a4f32b545563406d3379d8abf0b52bf818b | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-16 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 349 Central St. APT 6 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number5.jpg&form-id=2&field-id=42&hash=a343f19dddafc91dc1df61f708b84f31eb4911e23220792e210bf044bf057b93 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-16 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 349 Central St. APT 5 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number4.jpg&form-id=2&field-id=42&hash=1a82e49fdf66e3796298e8542f2b653fc25266a946ab21dae681183c90ce0c44 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-16 | John | Vespa | 17144 | 250 Milton St LL007 |  | Dedham | MA | 2026 | 6173251151 | Owner | Vespa@johnvespaelectrical.com | QPF2 | Breaker |  | 20 |  | 2 Poles | Siemens | Residence |  | 2024-10-31 | 2024-06-28 | 126 Westbourne Terrace |  | Brookline | MA | 2446 | United States | Installed wall oven with 2 pole 20A GFCI Siemens breaker, nuisance tripping occurred first in October 2024 and continued afterwards, final replacement to standard breaker on July 22nd 2025. | GE | PTS7000BN4TS |  | single family | kitchen oven circuit | No | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John Vespa
2025-07-16 | Eric | Caldon | 21306A | 100 Deanville Rd |  | Attleboro | MA | 2703 | 7742296409 | owner/electrician | Ecaldonmidstate@gmail.com | Cutler Hammer BR | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-12 | 2025-05-09 | kitchen | 19 Ledge Hill Lane | Rehoboth | MA |  |  | Range will not turn on | Viking | VDR74828BDG01 | 0 | single family | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2F19-Ledge-Hill-oven.jpg&form-id=2&field-id=42&hash=bfa27fbb449abd6ac0851aeaf4aad9d97087c54078d1ebace615eb68128233fa | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Eric Caldon
2025-07-16 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-27 | 2025-06-27 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 101 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 101 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 367 Central St. APT 44 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number43.jpg&form-id=2&field-id=42&hash=675419a5c2b6fecd27b0c113153062af3d56f2c73a8a090fa5faf9551a5e6638 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | QF240A | Breaker |  | 40 |  | 1 Pole | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 367 Central St. APT 43 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240V | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 367 Central St. APT 42 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 367 Central St. APT 41 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | QF240A | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number42.jpg&form-id=2&field-id=42&hash=6e3365b6a625acc95472052cad03f25882dcd19b78da0e24f3732432849d7d54 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 365 Central St. APT 40 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number41.jpg&form-id=2&field-id=42&hash=af5bf6db0c4c61469a9f1532d987c36de4af0d8a04521aca62d72dceb13e4da0 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number39.jpg&form-id=2&field-id=22&hash=58d9966808ede23d40f9cb7184d8574c579ccf04eb8c532558aa96caeac8aa68 | 2025-05-23 | 2025-05-23 | 365 Central St. APT 39 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number40.jpg&form-id=2&field-id=42&hash=fe24251af4468b49141fdcdb18bb87a5cf017dc3dbd6c88d4f3b1cf9388e8c5d | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 365 Central St. APT 38 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number38.jpg&form-id=2&field-id=42&hash=c1c1cf31ce18ed499d9e8962c02f1f8958906f5bc5d6b9b10396fbe5526985d3 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 365 Central St. APT 37 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number37.jpg&form-id=2&field-id=42&hash=76e48ac6a5443eabb1fbd4dacc3caf4617d1db1aa93d1e30a7c5dadeb3cd3b75 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 363 Central St. APT 36 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number36.jpg&form-id=2&field-id=42&hash=20f80bcc721800baab15eab6cd1f73cb879639a00f986376f9478f7cbec97291 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 363 Central St. APT 35 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number35.jpg&form-id=2&field-id=42&hash=4e8505dccf33217bb7e9a9229221c5f6c055954e2f80506fe3465ede4b5e80fc | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 363 Central St. APT 34 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number34.jpg&form-id=2&field-id=42&hash=95b6d90d6de6b2abb43a812039b83df1fe5102ae143e87f5364c54c0d12b2d38 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 363 Central St. APT 33 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number33.jpg&form-id=2&field-id=42&hash=865252d2b19761acbe5eb8e6d801e614f975c2b6369a1de61cc2fabe3125b842 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number31.jpg&form-id=2&field-id=22&hash=4feac1109d8e37d4e47eccee7847a6afc1dc8c9aff9685d90c8b0867c12a5c1e | 2025-05-23 | 2025-05-23 | 361 Central St. APT 32 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number32.jpg&form-id=2&field-id=42&hash=1a5d7c6286c20ac397f5de283f774b3b1c82adb47d42ed1ffcb94b1ea18e6486 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 361 Central St. APT 31 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number30.jpg&form-id=2&field-id=42&hash=c7295815245d1ed259944c1bb167f51c38d23ed86ddcc43b1f9496c11bf45688 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 361 Central St. APT 30 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number29.jpg&form-id=2&field-id=42&hash=d9568186d0e6d1ffa3b92af6a107598fc41b12580dded3d125300cc9c933e4fe | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 361 Central St. APT 29 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number28.jpg&form-id=2&field-id=42&hash=517e3221b2cf7d20ada3fc7e9be67429f99ef00318caf656b8030342eaa1ea72 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 359 Central St. APT 28 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number27.jpg&form-id=2&field-id=42&hash=e641c1d80cc4cb13e70e5414433c502fa47d47114119ea6e9b2c58a6b764956f | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 359 Central St. APT 27 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number26.jpg&form-id=2&field-id=42&hash=fe9c757ed3a77c1df3ee61844b1bbced63b7e1aa86167f9d0a48ac9d9a405bd2 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 359 Central St. APT 26 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number25.jpg&form-id=2&field-id=42&hash=84ca619b0858ffc9b309f468f31a4fe644e88e99414272f322e5607e0792a967 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 359 Central St. APT 25 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number24.jpg&form-id=2&field-id=42&hash=095e7ea4cc2a423636ccc8ce45cb9e02e99163f64ec011d83a8b5e3aede17a6a | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 357 Central St. APT 24 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number23.jpg&form-id=2&field-id=42&hash=ea5667cc171921f0c28242b9b8e49da100197cc12cc8d13fe4d92a0491040a16 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 357 Central St. APT 23 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number22.jpg&form-id=2&field-id=42&hash=12c56596e5ac87b056b1824c69cd28619ca89df8b343715b8435be61eb08a321 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 357 Central St. APT 22 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number21.jpg&form-id=2&field-id=42&hash=af01d711c4054cb7d6620ff25243c7af1a83896931f8328add96c5943ebc3920 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | GMastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 357 Central St. APT 21 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number20.jpg&form-id=2&field-id=42&hash=a488dc6aedf6fed9ad180a70f22684e6443a44eccf0a92137a5be61a9cc32f4e | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 355 Central St. APT 20 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number19.jpg&form-id=2&field-id=42&hash=71a4de3b22e94a8470d080ef760d47ff152b255da3ab9138ac9a61fb8bd47584 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 355 Central St. APT 19 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number18.jpg&form-id=2&field-id=42&hash=43b7d0e214c1a2c2b8a64227bd83ecd50ee6878007bf39705725b33b989e651a | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | steven | Marchand | 56386 | 72 Rolfe Avenue |  | Shrewsbury | Massachusetts | 1545 | 5085606344 | Electrician | s.marchand86@yahoo.com | THQL2140GFT2P | Breaker |  | 40 |  | 2 Poles | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 39 | Groton Harvard Road | Ayer | Massachusetts | 1432 | United States | TRips breaker while stove is being used everytime no matter what the operation is set to on appliance | BOSCH | HIS8055U |  | Single Family Home | isolated to appliance itself nothing else is affected | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Steven Marchand
2025-07-17 | steven | Marchand | 56386 | 72 Rolfe Avenue |  | Shrewsbury | Massachusetts | 1545 | 5085606344 | Electrician | s.marchand86@yahoo.com | THQL2140GFT2P | Breaker |  | 40 |  | 2 Poles | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 39 | Groton Harvard Road | Ayer | Massachusetts | 1432 | United States | TRips breaker while stove is being used everytime no matter what the operation is set to on appliance | BOSCH | HIS8055U |  | Single Family Home | isolated to appliance itself nothing else is affected | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Steven Marchand
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 355 Central St. APT 18 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number17.jpg&form-id=2&field-id=42&hash=7342eae96e605b027bd4060876801286c4ef93a90460398faf9297ef4be96282 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-17 | Greg | Mastroianni | 14144-B | 100 Memorial Ave. |  | West Springfield | MA | 1089 | 4137393835 | Foreman | gmastroianni@goodlesselectric.com | Siemens QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-05-23 | 2025-05-23 | 355 Central St. APT 17 |  | Springfield | MA | 1105 | United States | Installed brand new dedicated 8/3 romex apx 15’ from the electrical panel. Installed a new 4 wire receptacle and 40 amp 2 pole GFCI breaker. Powered up the electric stove and the circuit works, as soon as the heating elements are turned on it runs for around 30 seconds and then trips the gfci breaker. We tried this multiple times and each time it trips within 30-60 seconds from the heating elements being turned on. | Kenmore | RSA2000M1WW | None | Apartment | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FCentral-Housing-Stove-Model-Number16.jpg&form-id=2&field-id=42&hash=fba9a47f1c0e5858685488a07c0c1f203944a9d5b0cb05fa720569f0ea69a846 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Greg Mastroianni
2025-07-18 | Leonard | Silvaggio | A10579 | 50 Mount Vernon St | Unit 2 | North Reading | MA | 1864 | 6177191956 | Electrician | lsilvaggio@wireworkselectrical.com | Seimans | Breaker |  | 60 |  | 2 Poles | Siemens | Residence |  | 2025-07-18 | 2025-07-18 | 28 Atlantic Ave | Unit 423 | North Reading | MA | 1864 | United States | Range trips the GFI breaker. Checked all wiring and owner replaced the range. | Bosch | Scout Ceran | No | Condo | Kitchen range | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Leonard Silvaggio
2025-07-19 | Gabriel | Silva | 61251-B | 315 Charger Street |  | Revere | MA | 2151 | 6174617825 | Electrician | gboliveirasilva0@gmail.com | Siemens | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-07-15 | 2025-07-21 | 32 high street |  | Charlestown | MA | 2129 | United States | Range often tripping the gfci breaker | Thermador | PRI36LBHU |  | Residencial | Kitchen | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Gabriel Silva
2025-07-20 | Sean | Matthies | 8262a1 | 31 Norman Ave. |  | West Bridgewater | MA | 2379 | 7814929520 | Owner Sean Matthies Construction Services LLC | matthieselectrician@gmail.com | BRN240GF | Breaker |  | 40 |  | 2 Poles | Eaton | Residence |  | 2025-07-18 | 2025-07-04 | 1000 Blue Hill Ave |  | Milton | MA |  |  | Oven will intermittently trip while customer is attempting to cook. | Frigidaire | gcwm2767ade | na | Dwelling | kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Sean Matthies
2025-07-20 | Sean | Matthies | 8261a1 | 31 Norman Ave. |  | West Bridgewater | MA | 2379 | 7814929520 | Owner Sean Matthies Construction Services LLC | matthieselectrician@gmail.com | BRN250GF | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-18 | 2025-07-04 | 1000 Blue Hill Ave |  | Milton | MA |  |  | Cooktop will intermittently trip while customer is attempting to cook | LG | LCE3610SB | na | dwelling | kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Sean Matthies
2025-07-21 | Manuel | Andino | 52474-B | 15 Shurtleff Road |  | Eastham | MA | 2642 | 7747222397 | Electrician | maniandino@icloud.com | M2401150481 | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-07-02 | 2024-07-23 | [6 empty] | The oven is a basic 4-coil electric range/oven, and when the oven gets up to the preset temperature, it causes the GFCI breaker to shut off. The oven is relatively new. | Amana | AEP222VAW5 |  | Family home, two story. | Main floor kitchen. | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Manuel Andino
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-06-19 | 2025-06-19 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 527 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WOES5030L2 |  | Apartment building | Kitchen in unit 527 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-06-18 | 2025-06-18 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 541 was tripping the old breaker (BRN230GF), we replaced breaker to an Eaton BR230 and a ground leakage test to confirm breaker functionality | Whirlpool | WOES5030L2 |  | Apartment building | Kitchen in unit 541 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-23 | 2025-06-23 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 544 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 544 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 543 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 543 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-23 | 2025-06-23 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 517 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 517 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-20 | 2025-06-20 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 515 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 515 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-20 | 2025-06-20 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 514 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 514 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-20 | 2025-06-20 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 513 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 513 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-23 | 2025-06-23 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 512 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 512 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-20 | 2025-06-20 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 511 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 511 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-23 | 2025-06-23 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 509 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 509 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 508 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 508 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-19 | 2025-06-19 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 507 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 507 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-19 | 2025-06-19 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 506 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 506 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-19 | 2025-06-19 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 505 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 505 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-20 | 2025-06-20 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 504 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 504 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-19 | 2025-06-19 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 503 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 503 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-19 | 2025-06-19 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 502 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 502 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-19 | 2025-06-19 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 501 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 501 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 444 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Stove in unit 444 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 443 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 443 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 417 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 417 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 415 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 415 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-17 | 2025-06-17 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 414 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 414 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 412 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-24 | 2025-06-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 411 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 411 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 409 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 409 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-09 | 2025-06-09 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 408 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 408 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-03 | 2025-06-03 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 407 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 407 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 406 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 406 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 405 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 405 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 404 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 404 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 403 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Stove in unit 403 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 402 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 402 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-05-25 | 2025-05-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 401 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 401 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-03 | 2025-06-03 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 344 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 344 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 317 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 317 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 315 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 315 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 314 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 314 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 313 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 313 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 312 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 312 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 311 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 311 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 309 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 309 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 308 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 308 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 307 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 307 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 306 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Stove in unit 306 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 306 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 306 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 305 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 305 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 304 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 304 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 303 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 303 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 302 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 302 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-25 | 2025-06-25 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 301 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 301 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 244 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 244 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 243 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 243 | Yes | No | No | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 217 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 217 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 215 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 215 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 214 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 214 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 213 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 213 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 212 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 212 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 211 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 211 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 209 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 209 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 208 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 208 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 207 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 207 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 206 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 206 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-18 | 2025-06-18 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 205 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 205 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 204 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 204 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 203 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 203 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-26 | 2025-06-26 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 202 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 202 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-30 | 2025-06-30 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 201 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 201 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-18 | 2025-06-18 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 144 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 144 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-17 | 2025-06-17 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 117 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 117 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-17 | 2025-06-17 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 115 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 115 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-27 | 2025-06-27 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 113 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 113 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-27 | 2025-06-27 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 111 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 111 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-27 | 2025-06-27 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 109 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 109 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-27 | 2025-06-27 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 108 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 108 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-17 | 2025-06-17 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 106 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 106 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-10 | 2025-06-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 105 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 105 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-27 | 2025-06-27 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 104 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 104 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-27 | 2025-06-27 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 103 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 103 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-27 | 2025-07-27 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 103 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 103 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-21 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-27 | 2025-06-27 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 102 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 102 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-22 | Nicole | Hollenbeck | 38955e | 31 Sunset Drive |  | Dudley | MA | 1571 | 5085810986 | Home Owner | nhollenbeck05@gmail.com | CH-BR 240GFCI | Breaker |  | 15 |  | 2 Poles | ABB | Residence |  | 2025-07-18 | 2025-05-29 | [6 empty] | When starting to preheat the oven, it will trip the circuit, and all power is lost. We have to reset the breaker and try again. This has happened many times. The oven will heat up multiple times, and when it reaches the max temperature, it blows a circuit. This has been going on for over a month now. | Whirlpool 30 Inch electric range with steam clean | WFES3330RZ |  | Primary residence and in-law apartment | The kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Nicole Hollenbeck
2025-07-22 | Richard | Chase | 21093-A | 16 | Fermanagh St. | Haverhill | Massachusetts | 1835 | 7815890262 | Owner/Electrician | Richard@ChaseElectricNE.com | QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-07-19 | 2025-04-08 | 25 Hamilton Ave. |  | Haverhill | Massachusetts | 1830 |  | Circuit trips when oven cycles up. Tested for overload and fault current and found none. | Whirlpool | WEE515S0LB3 | None | Two family home | Dedicated range circuit for the kitchen at 25 Hamilton Ave. | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Richard Chase, Jr.
2025-07-22 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor | castlecp@hotmail.com | Semiens 20-amp dual-function | Breaker |  | 20 |  | 1 Pole | Siemens | Residence |  | 2025-07-18 | 2025-03-07 | 55 Foster St. |  | Littleton | MA | 1460 | United States | Installed a new 20-amp dual-function breaker on a new Freezer. It continues to trip. | Fisher & Paykel | RS1884FLJKI |  | Single family. | Kitchen. | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark S. VanMolle
2025-07-22 | Mark | VanMolle | 13527 | PO Box 1534 |  | Littleton | MA | 1460 | 978-337-6541 | Contractor | castlecp@hotmail.com | Seimens | Breaker |  | 20 |  | 1 Pole | Siemens | Residence |  | 2025-07-18 | 2025-03-07 | 55 Foster St. |  | Littleton | MA | 1460 |  | Installed a new 20-amp dual-function breaker on a new dishwasher. It continues to trip. | Miele | G7366SCVI |  | Single family. | Kitchen. | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark S. VanMolle
2025-07-22 | Brian | Bradley | 20351-A | 266 Sudbury Street |  | Marlborough | MA | 1752 | (978) 212-8014 | Owner/Electrician | bbelectric.permits@gmail.com | Siemens QF260A | Breaker | None | 60 | N/A | 2 Poles | Siemens | Residence |  | 2025-07-21 | 2025-07-19 | 65 Whittemore Street |  | Concord | MA | 1742 | United States | Manufacturer recommends not using a GFCI breaker when wiring their saunas. GFCI breaker will remain on for about five minutes while sauna is operating and then trips. | HUUM Hive 9kW Heater | HUUM9KVA |  | Single Family Home | Sauna is the only thing that trips. | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Brian M Bradley
2025-07-22 | ELIEZER GILBERTO | DA CRUZ | 23664-A | 8 Meridian St |  | Melrose | MA | 2176 | 8578800574 | Master Electrician | master@cfcelectric.com | BCCI30 | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-01-10 | 2025-07-07 | 91 Boston Rock Road |  | Melrose | MA | 2176 | United States | As soon as I turn the breaker on, it holds. However, the moment I turn on the range, the breaker trips immediately. | Big Chill | BCCI30 |  | Single family | Just the range in the kitchen. | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Eliezer Gilberto da Cruz
2025-07-24 | Andy | Courtade | 39574e | 11 1st ave |  | Bellingham | Massachusetts | 2019 | 5088162001 | Contractor | ezek1@verizon.net | Square D Home Line | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-05-01 | 2025-05-01 | 473 Auburn St |  | Newton | Massachusetts | 2466 | United States | Manufacturer instructions sent that the GFCI will not work with appliance | Wolf | CI365T/5 |  | Kitchen | Kitchen | No | No | No | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Andy Courtade
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-01 | 2025-07-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 548 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 548 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 450 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 450 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 448 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 448 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-01 | 2025-07-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 551 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 551 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 15 |  | 2 Poles | Eaton | Residence |  | 2025-07-24 | 2025-07-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 550 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 550 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-01 | 2025-07-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 549 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 549 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-01 | 2025-07-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 548 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 548 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-01 | 2025-07-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 547 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 547 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-01 | 2025-07-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 546 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 546 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-01 | 2025-07-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 545 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 545 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 451 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 451 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 450 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 450 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 449 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 449 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 448 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 448 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 447 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 447 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 446 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 446 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 445 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 445 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-16 | 2025-07-16 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 413 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 413 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 351 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 351 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 350 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 350 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 349 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 349 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 348 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 348 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 347 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 347 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 346 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 346 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 345 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 345 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-17 | 2025-07-17 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 343 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 343 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 251 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 251 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 250 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 250 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 249 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 249 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 248 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 248 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 247 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 247 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 246 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 246 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 245 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 245 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-11 | 2025-07-11 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 151 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 151 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-11 | 2025-07-11 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 150 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 150 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 149 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 149 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 148 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 148 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 147 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 147 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933 | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 146 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WOES5030L2 |  | Apartment building | Kitchen in unit 146 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 145 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 145 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-17 | 2025-07-17 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 143 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 143 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-17 | 2025-07-17 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 114 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 114 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-07-17 | 2025-07-17 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 112 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WOES5030L2 |  | Apartment building | Kitchen in unit 112 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-17 | 2025-07-17 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 107 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 107 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-03 | 2025-07-03 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 439 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 439 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 15 |  | 2 Poles | Eaton | Residence |  | 2025-06-20 | 2025-06-20 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 542 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 542 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-06-20 | 2025-06-20 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 441 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WOES5030L2 |  | Apartment building | Kitchen in unit 441 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-03 | 2025-07-03 | 95 Maple St. |  | Stoneham |  |  |  | Stove in unit 440 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 440 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-16 | 2025-07-16 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 428 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 428 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-16 | 2025-07-16 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 427 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 427 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-15 | 2025-07-15 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 142 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 142 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-01 | 2025-07-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 141 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 141 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-01 | 2025-07-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 140 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 140 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-24 | 2025-07-24 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 139 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 139 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-01 | 2025-07-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 137 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 137 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-01 | 2025-07-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 136 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 136 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-01 | 2025-07-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 135 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 135 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-01 | 2025-07-01 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 132 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 132 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-03 | 2025-07-03 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 563 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 563 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-03 | 2025-07-03 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 562 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 562 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-03 | 2025-07-03 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 561 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 561 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-03 | 2025-07-03 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 560 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 560 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-16 | 2025-07-16 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 559 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 559 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-03 | 2025-07-03 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 558 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 558 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-02 | 2025-07-02 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 557 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 557 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-02 | 2025-07-02 | 95 Maple St. |  | Stoneham | MA | 2180 | United States | Stove in unit 556 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 556 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-02 | 2025-07-02 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 555 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 555 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-02 | 2025-07-02 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 554 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 554 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-02 | 2025-07-02 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 553 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 553 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-02 | 2025-07-02 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 552 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 552 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-07 | 2025-07-07 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 463 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 463 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-07 | 2025-07-07 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 462 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 462 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-07 | 2025-07-07 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 461 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 461 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 460 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 460 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 459 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 459 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 458 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 458 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 457 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 457 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 456 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Stove in unit 456 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 455 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 455 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 454 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 454 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 453 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 453 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-08 | 2025-07-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 452 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 452 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-08 | 2025-03-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 363 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 363 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-08 | 2025-03-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 362 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 362 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-08 | 2025-03-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 361 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 361 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-08 | 2025-03-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 360 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 360 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-08 | 2025-03-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 359 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 359 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-08 | 2025-03-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 358 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 358 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-08 | 2025-03-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 357 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 357 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-08 | 2025-03-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 356 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 356 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-08 | 2025-03-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 355 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 355 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-08 | 2025-03-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 354 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 354 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-08 | 2025-03-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 353 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 353 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-08 | 2025-03-08 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 352 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 352 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-06-09 | 2025-06-09 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 256 was tripping the old breaker (BRN230GF), we replaced breaker to an Eaton BR230 and a ground leakage test to confirm breaker functionality - please disregard previous submission with 50A breaker, it was sent in error | Whirlpool | WEP560LHW2 |  | Apartment building | Kitchen in unit 256 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 263 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 263 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 262 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 262 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 261 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 261 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 260 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 260 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 259 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 259 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 258 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 258 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 257 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 257 | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 256 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 256 | Yes | No | No | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 254 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 255 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 253 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 253 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 252 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 252 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 163 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 163 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Kitchen in unit 162 | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 162 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 161 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 161 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 160 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 160 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 159 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 159 | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 158 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 158 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 157 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 157 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 156 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 156 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 155 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 155 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 154 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 154 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 153 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 153 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-24 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | 7819320707 | President | faith@danddnet.com | Eaton BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-10 | 2025-07-10 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 152 was tripping the old breaker (BRN250GF), we replaced breaker to an Eaton BR250 and a ground leakage test to confirm breaker functionality | Whirlpool | WEE515SOL53 |  | Apartment building | Kitchen in unit 152 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-07-25 | James | McCormack | 22340A | 196 High St | Unit 2 | Ipswich | Massachusetts | 1938 | 9784710544 | Owner | jim@upwire-electric.com | QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-07-25 | 2025-07-25 | 12 Cedar St |  | Lexington | MA | 2421 | United States | Whenever the induction range is turned on the breaker trips | AGA | AEL361IN |  | Single Family Home | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | James McCormack
2025-07-25 | Robert | Mahoney | 14526 | 18 Surrey Dr. | Surrey Drive | Lakeville | MA | 2347 | 617-719-7532 | Owner | bobmahoneyelectric@comcast.net | QF 250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FSiemens-50-amp-gfi-breaker.pdf&form-id=2&field-id=22&hash=6b2b27b021e15e180d179fe31ca10449dde9169f8cda53ae797db4c7ec00aea4 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FSiemens-50-amp-gfi-breaker1.pdf&form-id=2&field-id=22&hash=38bce3d5a276ca728148f73069e77b66b9e23b67e4a6c413a51ec30e5c468a42 | 2025-04-01 | 2025-03-27 | 18 Surrey Dr. | Surrey Drive |  | MA | 2347 | United States | Turn on cooktop, breaker immediately trips | Wolf | CI365T/S |  | Single family home | Kitchen | No | No | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2Fwolf-cooktop-specs.pdf&form-id=2&field-id=42&hash=cd26c79c79d1622b240d703aaf98468ed5f0d88b0d2e0245bd518fbeae81be09 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FWolf-cooktop.pdf&form-id=2&field-id=42&hash=d7d9cf727c231753182959724a469e8b797c8951dcea26fa0dbc92db75b9da06 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Robert Mahoney
2025-07-28 | Chris | Coviello | 9858 A | 168 Water St. |  | Saugus, | Ma. | 1906 | 617-799-3974 | Electrician | chriscoviello56@gmail.com | AJ6JEOOL. HOOOOZP. 50 Q-R | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-06-28 | 2025-06-28 | 21 McCullough rd |  | Saugus | Ma | 1906 | United States | BREAKER TRIPS IN one to two minutes after stove is turned on to use. | Cafe | CTD70DP2N4S1 | No | Dwelling | Kitchen wall oven | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Chris Coviello
2025-07-28 | CARMELO | OCCHINO | 111487A | 175 Brookline Street |  | Cambridge | MA | 2139 | 6178999952 | PRESIDENT | cocchino@aetnacorp.com | GR THQL2150GFI2 TYPE THQL-GFI HACR CU/AL 120/240V 60HZ | Breaker |  | 50 |  | 2 Poles | ABB | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_0060.jpg&form-id=2&field-id=22&hash=7d7523a75fe035e8f4fc5fe14da5c06b9ddd8a0e4ae3af23d233c9310094bc3d , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_0063.jpg&form-id=2&field-id=22&hash=d80d47a8fd913ce6652734a142bb179094e63911e2fa09279447864a718ca303 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_0061.jpg&form-id=2&field-id=22&hash=b050fe4a25df6d682e0dd765d0d6bf9986cc18cbe9a5117448912ddb1f2147b4 | 2025-07-11 | 2025-07-11 | 7 WOOD STREET |  | WOBURN | MA | 1801 | United States | 2 POLE 50A GFCI BREAKER TRIPS IMMEDIATELY WHEN THE RANGE IS TURNED ON. | FRIGIDARE INDUCTION RANGE | GCF13060BFE | NONE | KITCHEN | RESIDENTIAL KITCHEN | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_0028.jpg&form-id=2&field-id=42&hash=0c60dc107ec2d5036cff5f1b2ce6ebea7e56331f66b54802eee2010c769dd8dd , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_0027.jpg&form-id=2&field-id=42&hash=5045c830233b4e51fb79197aa3f18fdd8e67c447691f7e40a6b7ce2dddf8c21a | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Carmelo Charles Occhino
2025-07-29 | Daniel | Greenberg | 54913B | 36 Metacomet Rd |  | W Bridgewater | Massachusetts | 2375 | 7812647746 | Construction Manager | Dgreenberg@stonebridgehomesinc.com | DP-4075 | Breaker | none | 40 | none | 1 Pole | ABB | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2Fthumbnail_IMG_1486.jpg&form-id=2&field-id=22&hash=ae5c2e4dcf030ad7a2cd7342d97fb346701804333cd4e8381cfd2b22df08ad60 | 2025-07-28 | 2025-07-24 | [6 empty] | Kitchen range trips every time it is turned on. | Frigidaire | GCRE3060BFD | none | Single Family Home | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2Fthumbnail_IMG_1482.jpg&form-id=2&field-id=42&hash=a4e0d8ce1d7da7f0a36732a76f9bb088e59d2f7bf0e894ced4144900444d59b5 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2Fthumbnail_IMG_1483.jpg&form-id=2&field-id=42&hash=9e7bb9921451476358e08aec61bdc59654c06a53854541360a3b6869281a9b44 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2Fthumbnail_IMG_14861.jpg&form-id=2&field-id=42&hash=2155c835d16fb67c488b48fcffd4b7e6f0e4fd8a45dd642a08046bcb209b913f | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Daniel Greenberg
2025-07-29 | David | Balkcom | A18026 | 210 Essex St, Ste 5 | Ste 5 | WHITMAN | MA | 2382 | 7812480575 | President | dj@djelectricma.com | Square D | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-07-18 | 2025-07-18 | [6 empty] | Random trip when installed | GE Cafe | CHS900P@M9S1 | none | Kitchen | Kitchen range trips randomly | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | David Balkcom Jr
2025-07-29 | Francois | Charlotin | 36586E | 303 Cambridge St | Apt 1 | Fall River | MA | 2721 | 6175935553 | Electrican | fcharlotinjr@aol.com | Square D homeline | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-07-25 | 2025-07-25 | 36 Appleton | Apt 1 | Malden | MA | 2148 | United States | GFCI trips when oven is connected. | MayTag | WL0L90L98.A |  | Kitchen oven | The kitchen oven is a dedicated circuit. | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Francois Charlotin Jr
2025-07-31 | Giombetti | Electric, Inc. | A13678 | 401 SOUTH STREET | 401 South Street | Marlborough | MA | 1752 | 508-481-3299 | President | mike@giombettielectric.com | Eaton CHN240GF | Breaker |  | 40 |  | 2 Poles | Eaton | Residence |  | 2025-07-29 | 2025-07-29 | 29 Pleasant Street | Apartment C-5 | Marlborough | MA | 1752 | United States | Breaker trips while using the burners or the oven | Premier | ECK2400P01 | None | Apartment | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_7443.jpeg&form-id=2&field-id=42&hash=c0467e7b90e467ac84032416cc1cf02733cb37763f9b436d3c889590dfe9e355 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_7441.jpeg&form-id=2&field-id=42&hash=9447d2ca13ea184e2df62dc45d9f831624aaa7e684f5a5ed388f9e980d6fe515 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_7440.jpeg&form-id=2&field-id=42&hash=bd580a909a61381e47f52a24f63f1be4794d9c676581f01033bf6ae1dbe50a96 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F07%2FIMG_7442.jpeg&form-id=2&field-id=42&hash=1ea0c9fc30312eee7470a666e8caa6af58e121a22720dfdf4a3631ef05624d4e | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Michael A Giombetti
2025-08-03 21:17 | Tyler | Hopkins | 58471-b | 280 | Berkley st | Taunton | MA | 2780 | United States | 5088449818 | office@hopkinselectric-ma.com | whirlpool WFE525S0JZ0 | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-07-31 | 2025-07-30 | 6 Ginley Road | Berkley st | Walpole | MA | 2081 | United States | The GFI breaker works fine while the stove top is on and while the oven is preheating. As soon as the oven preheats, it trips the breaker instantly. | Whirlpool | WFE525S0JZ0 |  | single family home kitchen | The range is the only affected item. | No | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_6508.jpg&form-id=2&field-id=42&hash=cd31356e480a4b9afd7d86bf47f29872ff7adce709eba470c73d956abc7d24c4 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Hopkins
2025-08-04 21:19 | Edward | McCurbin | 36962E | 196 Dana Ave |  | Hyde Park | MA | 2136 | United States | 617.438.1050 | Mccurbineg@gmail.com | M2503061228 | Breaker |  | 50 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FBreaker-for-stove.docx&form-id=2&field-id=22&hash=f6f79f02e3b69ba03672334b9b72aba8f8a59e7819b467deb9d9dc118a22f3f0 | 2025-08-01 | 2025-08-01 | 354 Beacon St. |  | Boston | MA | 2116 | United States | Turned the electric stove on and the breaker tripped. | Avanti | DER20P3S |  | Condominium | The stove in the kitchen is is affected by the trip. | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Edward McCurbin
2025-08-05 08:48 | JHONATAN | CARDOSO | 23778A | 78 WALKER RD | 78 WALKER RD | SHIRLEY | MA | 1464 | United States | 8572371619 | JCELECTRICALMA@GMAIL.COM | THQL2150GFT2A | Breaker |  | 50 |  | 2 Poles | ABB | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_3353.jpeg&form-id=2&field-id=22&hash=e169f2bd4ef0ec169e6a2d5a2effeb4836f3346329b497d6e4787446675f596c | 2025-08-01 | 2025-07-27 |  | 187 WOODWARD ST | NEWTON | MA | 2468 | United States | THE COOKTOP DOESN&#039;T WORK WITH GFCI BREAKER, MANUFACTURE RECOMMENDS REGULAR BREAKER. | WOLF | C36560T/S |  | KITCHEN | KITCHEN | Yes | Yes | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_3356.jpeg&form-id=2&field-id=42&hash=608c0556870a58c30ba14c3c6fefbed2de53134ed9100146fd5ae91ca0206cec | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | JHONATAN CARDOSO
2025-08-06 07:01 | James | Comeau | E39174 | 31 Pine Grove St |  | Milton | MA | 2186 | United States | 6172726291 | Jcomeau0@gmail.com | Siemens QPF2N | Breaker |  | 20 |  | 1 Pole | Siemens | Residence |  | 2025-03-08 | 2025-03-01 | 108 Lincoln Ave |  | Quincy | MA | 2170 | United States | This breaker is continually tripping for no apparent reason. It trips every 6-10 days. This is an entirely new installation. New circuit, materials, panel, etc. | Bosch | B36CT80SNS | Dedicated outlet | Kitchen | Kitchen only | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | James Comeau
2025-08-06 07:20 | James | Comeau | E39174 | 31 Pine Grove St |  | Milton | MA | 2186 | United States | 6172726291 | Jcomeau0@gmail.com | Siemens QPGAH2 | Breaker |  | 20 |  | 1 Pole | Siemens | Residence |  | 2025-05-09 | 2025-05-01 | 108 Lincoln Ave |  | Quincy | MA | 2170 | United States | This breaker is continually tripping for no apparent reason. It trips every 6-10 days. This is an entirely new installation. New circuit, materials, panel, etc. | Bosch | B36CT80SNS | Dedicated outlet | Kitchen | Kitchen only | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | James Comeau
2025-08-08 12:26 | James | Frazier | 22574A | 20 Richardson St | 2 | Wakefield | MA | 1880 | United States | 7817991502 | jfrazier281@gmail.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-07 | 2025-08-07 | 71 Summer st |  | Saugus | MA |  | United States | When electric stove is turned on. Breaker nuisance trips. | Fridgidaire | LFEF3017LBD | None | Single family kitchen | Kitchen electric stove. | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | James Frazier
2025-08-11 12:22 | Michael | Campaniello | 23649-A | 2 Gay Road |  | Brookfield | MA | 1506 | United States | 7742000856 | office@robertandmikeselectric.com | Miele/ KM7745FL | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-08-11 | 2025-08-11 | 120 Seaver Street | Unit C301 | Brookline | MA | 2445 | United States | The GFCI breaker trips instantly as soon as power use is attempted at oven appliance. Burn off test was attempted and once GFCI was reinstalled the same tripping issue occured. | Miele | KM 7745 FL |  | Condo Kitchen | Residential kitchen. | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Michael Campaniello
2025-08-12 08:42 | Andrew | crowe | 24989-b | 331 Forest st |  | rockland | Massachusetts | 2370 | United States | 7817186460 | Andrew@crowe-electric.com | brn250gf | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-08-06 | 2025-07-03 | 3 east st |  | marshfield | ma | 2050 | United States | Reinstall the breaker and let it run for about 10 minutes. We left the house and we got a call back that the breaker tripped again. We came back. It runs for about two minutes and then trips right away. We split the neutrals and grounds up in the stove and it still doesn&#039;t work. We also installed a new line so it&#039;s not a bad line. | Samsung stove | na | nothing | single famley | It&#039;s a very old electric stove. There&#039;s no model number on it or anything like that. | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Andrew Crowe
2025-08-12 10:04 | Daniel | Greenberg | 54913B | 09 Narragansett |  | W. Bridgewater | MA | 2379 | United States | 7812647746 | Dgreenberg@stonebridgehomesinc.com | DP-4075 | Breaker | - | 40 | - | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FbREAKER.jpg&form-id=2&field-id=22&hash=428c1c2b30db9ffb31ff979135e7fde084d782be8d35180006aaa6c1d68e6007 | 2025-08-08 | 2025-08-05 | [6 empty] | Oven / range breaker trips whenever it is used. | Frigidaire | VF51960188 | - | Single Family Home | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FRange.jpg&form-id=2&field-id=42&hash=a7df4de3c846a8d08cbb76bdb1758b38e1760edbd070e44095ff33a806b8563e , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FRange-2.jpg&form-id=2&field-id=42&hash=f46c984d1368250827b7fccf907fa4b12725a12134b402431b07cd70963e2ae7 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Daniel M. Greenberg
2025-08-12 16:06 | Douglas | Lynch | 11933A | 10 Everberg Rd. |  | Woburn | MA | 1801 | United States | 7819320707 | faith@danddnet.com | Eaton BR230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-08-05 | 2025-08-05 | 95 Maple St. |  | Stoneham | MA | 2180 |  | Stove in unit 149 was tripping the old breaker (BRN230GF), we replaced breaker to an Eaton BR230 and a ground leakage test to confirm breaker functionality | Whirlpool | WED560LHW2 |  | Apartment building | Kitchen in unit 149 | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Lynch
2025-08-13 11:28 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | 2339 | United States | 781-953-4023 | starbro@verizon.net | GE THQOLDF20 | Breaker |  | 20 |  | 1 Pole | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Unit 106 |  | Quincy | MA | 2169 | United States | Refrigerator nuisance tripping | GE | GWE19JMLXFES |  | Condo | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-13 13:03 | Nick | McElroy | 670A1 | 381 Old Falmouth Rd. | Suite #32 | MARSTONS MILLS | MA | 2648 | United States | 5085664489 | Nick@capecodelectrician.com | Eaton | Breaker |  | 30 |  | 2 Poles | Eaton | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_7915.jpeg&form-id=2&field-id=22&hash=19ecae52af07a711bc9d3df83cceb966468d877734ec5283e295e9eca5aa28d2 | 2025-06-25 | 2024-08-09 | 159 south street | Suite #32 | Yarmouth | MA | 2664 | United States | nuisance tripping of breaker when stove burners were turned on | Wolf | DF366 |  | Home | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_7914.jpeg&form-id=2&field-id=42&hash=653ee853777c03c4d2300c825360b335cb2d3d4a3c24a61e23321f466e01c99c | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Nick McElroy
2025-08-13 13:54 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | 2339 | United States | 781-953-4023 | starbro@verizon.net | GE THQOL1120DF | Breaker |  | 20 |  | 1 Pole | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Unit 106 |  | Quincy | MA | 2169 | United States | Washing machine nuisance tripping | Bosch | WQB245AXUC/01 |  | Condo | Laundry closet | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-13 14:47 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | 2339 | United States | 781-953-4023 | starbro@verizon.net | GE THQL30DF | Breaker |  | 30 |  | 2 Poles | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Unit 106 |  | Quincy | MA | 2169 | United States | Dryer nuisance tripping | Bosch / BSH Home Appliances | WQB245AXUC/01 |  | Condo | Laundry closet | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-13 15:17 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | Quincy | United States | 781-953-4023 | starbro@verizon.net | GE THQOL1120DF | Breaker |  | 20 |  | 1 Pole | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Unit 201 |  | Quincy | MA | 2169 | United States | Washing machine nuisance tripping | Bosch | WQB245AXUC/01 |  | Condo | Laundry room | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-13 15:30 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | 2169 | United States | 781-953-4023 | starbro@verizon.net | GE THQL2150 GFCI | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Unit 201 |  | Quincy | MA | 2169 | United States | Electric range nuisance tripping | Bosch | WGB246AXUC/11 |  | Condo | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-13 15:38 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | 2169 | United States | 781-953-4023 | starbro@verizon.net | GE THQL1120DF | Breaker |  | 20 |  | 1 Pole | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Suite 207 |  | Quincy | MA | 2169 | United States | Refrigerator nuisance tripping | LG | LRFCS25D35/00 |  | Condo | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-13 15:46 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | 2339 | United States | 781-953-4023 | starbro@verizon.net | GE THQL2150 GFCI | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Unit 207 |  | Quincy | MA | 2169 | United States | Electric oven nuisance tripping | LG | LSEL6335FE/01 |  | Condo | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-13 15:51 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | 2339 | United States | 781-953-4023 | starbro@verizon.net | GE THQL1120DF | Breaker |  | 20 |  | 1 Pole | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Unit 207 |  | Quincy | MA | 2169 | United States | Microwave nuisance tripping | LG | MVEL2033F/00 |  | Condo | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-13 15:57 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | 2339 | United States | 781-953-4023 | starbro@verizon.net | GE THQL2150 GFCI | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Unit 208 |  | Quincy | MA | 2169 | United States | Electric oven nuisance tripping | Frigidaire | FCRE3083ASF |  | Condo | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-13 17:54 | Daniel | Savoie | E40678 | 10 Crescent St. |  | Wilmington | ma | 1887 | United States | 9782653987 | savoiedan7@gmail.com | siemans Q120DFN | Breaker | Leviton GFTR1-W | 20 | 15 | 1 Pole | Siemens | Residence |  | 2022-04-01 | 2022-03-25 | 3 Stevens St. |  | Chelmsford | MA | 1824 | United States | I installed a 20amp Siemans dual-function circuit breaker during a kitchen remodel to serve 2 countertop receptacles and the fridge. Shortly after the homeowner let me know that the circuit breaker was randomly tripping and causing his fridge to lose power. I then replaced the breaker with another of the same type/manufacturer. This did not resolve the problem. I then removed the breaker and installed a 20amp Siemans arc-fault breaker and a GFCI receptacle in the countertop with no improvement. I than plugged the fridge into a nearby AFCI only receptacle in an adjacent room which stopped the tripping issue. At that time I advised the homeowner that the problem was internal to the fridge and an internal GFCI issue. I further advised him that there was nothing more I could do that would help him without violating the code and that he should take the issue up with the fridge manufacturer. He contacted Samsung and was advised that they do not recommend GFCI protection on that model. I did not hear back from him until recently when he called me indicating that he was hoping to sell the house and wanted to see if I could help resolve the issue and having recently heard of this option I went ahead and removed the GFCI protection from the fridge while maintaining AFCI protection only for the fridge and AFCI/GFCI protection for the countertop receptacles | Samsung | RF28T5001SR/AA | 2 countertop receptacles | single family | Kitchen | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Daniel Savoie
2025-08-14 13:27 | Andrew | Harland | 21030A | PO Box 94 |  | Littleton | MA | 01460-0094 | United States | 9784868154 | andy@harlandelectric.com | Siemens/QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-07-24 | 2025-07-21 | 362 King St. |  | Littleton | MA | 1432 | United States | Customer needed existing range to be connected to new 4 wire receptacle. Electrician installed 2 pole 50 GFCI breaker. Breaker has tripped multiple times on GFCI protection. Electrician checked circuit wiring, no issues. Checked appliance to ensure no continuity phase to phase or each phase to ground- no issue found. Electrician installed standard 50A breaker, tested appliance, which worked as it should. Reinstalled GFCI breaker, which tripped. Due to no issues found with circuit wiring or appliance wiring, Electrician removed GFCI breaker and installed a non GFCI 2 pole 50A breaker. system normal at this time. | Frigidaire | FCRE3052BSE |  | Single family dwelling | Kitchen range | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2F362-King-St-littleton-range-name-plate.jpg&form-id=2&field-id=42&hash=68903aec77689b5c7511e4b8e130a22470b1639ac1cc8fbd802938a11c378e16 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Andrew Harland
2025-08-14 13:55 | Andrew | Harland | 21030A | PO Box 94 |  | Littleton | MA | 1460 | United States | 978-486-8154 | andy@harlandelectric.com | Siemens/QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-07-25 | 2025-02-03 | 1 Harvard Rd |  | Ayer | MA | 1432 | United States | Customer purchased new induction range. Electrician installed 50A circuit wiring and installed 2 pole 50 GFCI breaker. Range preheats to 150 degrees and then the breaker trips. Electrician checked circuit wiring, no issues. Checked appliance to ensure no continuity phase to phase or each phase to ground- no issue found. Electrician installed standard 50A breaker, tested appliance, which worked as it should. Reinstalled GFCI breaker, which tripped at approx. 150 degrees on preheat. Due to no issues found with circuit wiring or appliance wiring, Electrician removed GFCI breaker and installed a non GFCI 2 pole 50A breaker. system normal at this time. | General Electric | PHS930YPBFS |  | Single family | Kitchen range circuit only | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2F1-Harvard-Rd.-name-plate-for-trip-report.jpg&form-id=2&field-id=42&hash=c27264fe88f7138b37fc1cc56701a43993a2100b3fdd57903cd0882f3422d79b | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Andrew Harland
2025-08-15 08:09 | Giombetti | Electric, Inc. | A13678 | 401 SOUTH STREET |  | Marlborough | MA | 1752 | United States | 5084813299 | Mike@giombettielectric.com | SqD HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-08-14 | 2025-08-14 | 109 Broadmeadow Road | Apartment A3 | Marlborough | MA | 1752 | United States | Breaker trips when using the oven or burners | GE | J B256R T3SS | None | Apartment | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_20250815_075054.jpg&form-id=2&field-id=42&hash=4acef6a3232ba5697d31f9ba0428ea4b427d99e12ea253f841d8b6d9ca91ed4e , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_20250815_075032.jpg&form-id=2&field-id=42&hash=0d42035705f91c5daec73378925f149b08b0d84eda6545e210b9b72ab6ecaf06 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_20250815_075026.jpg&form-id=2&field-id=42&hash=c36def4a251f5bf9f3fb294c638bacf2023fcac2853ee88d650d70af9774137f , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_20250815_075021.jpg&form-id=2&field-id=42&hash=c03d68b0b206500e8a36a7e5fae4f03d9eaff27cc2ba1b68da042fe78de9220f | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Michael A Giombetti
2025-08-16 19:54 | Antonio F | Grieco | 17555A | PO Box 517 | 14 Towne Rd | Middleton | MA | 1949 | United States | 617-293-6555 | tony@griecoelectric.com | siemens | Breaker |  | 50 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2F170-Greystone-Ln-Sudbury-Manuel.pdf&form-id=2&field-id=22&hash=24b535db8e15ae7f7a8e8b48d4e1780dd5c135946f0a25bb1e57492a78806cdd | 2025-08-08 | 2025-08-01 | 170 Greystone Lane |  | Sudbury | MA | 1776 | United States | The Manufactures specifications states that the Bulestar Range Must be on a Non-GFI protected dedicated outlet. | BuleStar | BSDF488BCPLT |  | Single Family and Kitchen Range | Electric Range | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Antonio F Grieco
2025-08-18 16:20 | Noah | Gomes | 54-500B | 35 Hawthorne Street |  | Fairhaven | MA | 2743 | United States | 5082642531 | ndgomes.ec@gmail.com | BRN230GFCS | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-08-14 | 2025-08-14 | [6 empty] | Kitchen aid cooktop is a straight 240 volt equipment, holds no neutral, this gfi breaker will never work on this type of equipment using 240v without a neutral. | Kitchenaid | KCIG550jbl01 |  | Kitchen | Kitchen | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Noah D. Gomes
2025-08-18 20:53 | Steven | Blais | 55870B | 178 Dodge St |  | Beverly | MA | 1915 | United States | 9784067228 | sblais590@gmail.com | QO250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-07-12 | 2025-07-12 | 16 Wheatland St |  | Salem | MA | 1970 | United States | The range tripped the GFCI breaker within one minute of turning on | General Electric | JBP23DR3WW | none | Single Family | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Steven Blais
2025-08-18 20:59 | Andrew | Harland | 21030A | PO Box 94 | PO Box 94 | Littleton | MA | 1460 | United States | 9784868154 | andy@harlandelectric.com | GE Industrial THQL2140GFT | Breaker |  | 40 |  | 2 Poles | ABB | Residence |  | 2025-07-01 | 2025-06-27 | 48 Lee Drive |  | Concord | MA | 1742 | United States | Customer purchased new induction cooktop. Electrician installed installed 2 pole 40 GFCI breaker on existing cooktop circuit. When cooktop is in use, breaker trips frequently. Electrician checked circuit wiring, no issues. Checked appliance to ensure no continuity phase to phase or each phase to ground- no issue found. Electrician installed standard 40A breaker, tested appliance, which worked as it should. Reinstalled GFCI breaker, which tripped. Due to no issues found with circuit wiring or appliance wiring, Electrician removed GFCI breaker and installed a non GFCI 2 pole 40A breaker. System normal at this time. | Frigidaire | FFEH3054USE |  | Single family dwelling | Kitchen appliance | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2F48-Lee-Drive-Concord-trip-report-nameplate.jpg&form-id=2&field-id=42&hash=d69c768cd0115012ab49d394b08434364356868cd2eded3201b40e9ae895784c | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Andrew Harland
2025-08-19 06:35 | David | DEGRAZIA | 17119A | PO BOX 299 | COUNTY RD | E. Freetown | MA | 2717 | United States | 5085420179 | DEGR47@COMCAST.NET | BROAN | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-07-31 | 2025-07-16 | 242 COUNTY RD |  | E FREETOWN | MA | 2717 | United States | WHEN APPLIANCE IS TURNED ON CIRCUTIS ARE TRIPPED SHORTLY THERE AFTER ON GOIN PROBLEM | WHIRLPOOL | WFE550SOLZ | NA | KITCHEN | KITCHEN | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | DAVID DEGRAZIA
2025-08-19 06:50 | David | DeGrazia | 17119A | PO Box 299 | COUNTY RD | E Freetown | MA | 2717 | United States | 5085420179 | DEGR47@COMCAST.NET | BROAN | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-07-31 | 2025-07-17 | 242 COUNTY RD |  | E FREETOWN | MA | 2717 | United States | when appliance is turned on circuits are tripped shortly there after this is an on going problem | whirlpool | WED501LW0 | NA | LAUNDRY ROOM | LAUNDRY ROOM | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | DAVID DEGRAZIA
2025-08-19 06:51 | David | DeGrazia | 17119A | PO Box 299 | COUNTY RD | E Freetown | MA | 2717 | United States | 5085420179 | DEGR47@COMCAST.NET | BROAN | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-07-31 | 2025-07-17 | 242 COUNTY RD |  | E FREETOWN | MA | 2717 | United States | when appliance is turned on circuits are tripped shortly there after this is an on going problem | whirlpool | WED501LW0 | NA | LAUNDRY ROOM | LAUNDRY ROOM | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | DAVID DEGRAZIA
2025-08-19 06:58 | David | DeGrazia | 17119A | PO Box 299 |  | E. Freetown | MA | 2717 | United States | 5085420179 | DEGR47@COMCAST.NET | broan | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-07-31 | 2025-07-16 | 242 County Rd |  | E. Freetown | MA | 2717 | United States | when appliance is turned on tripping occurs this is an on going problem | Whirlpool | WFE550SOLZ | na | kitchen | kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | David DeGrazia
2025-08-19 09:05 | Anthony | Triolo | 54913B | 11 Hayford trail |  | Hanson | Massachusetts | 2341 | United States | 5088136244 | Atrioloelectric@gmail.com | HOM240GFIC | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_8143.png&form-id=2&field-id=22&hash=c28c0aa64efa7469f96aa5610955964e5258c8cd8850e1af665d15fa297776ef | 2025-08-16 | 2025-08-16 | [6 empty] | Electric stove trips when HOM240GFIC is installed | Frigidaire | GCRE3060BFD |  | Condo | Kitchen | No | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_8144.png&form-id=2&field-id=42&hash=716ba443c86392e397367317d1af7d1b28642433c3b024552635a346998199a5 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Anthony Triolo
2025-08-19 11:23 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 781-293-5701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 1 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIDGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 13:07 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET |  | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIDGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 13:10 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 3 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIDGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 13:14 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 4 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIDGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 13:21 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 5 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 13:28 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 6 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 13:32 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 7 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 13:36 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 8 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 13:39 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 9 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 13:42 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 10 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 13:49 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 11 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 13:52 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 12 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 13:56 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 13 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 13:59 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 14 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 14:00 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 15 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-19 16:24 | James | McCormack | 53625B | 196 High St | Unit 2 | Ipswich | Massachusetts | 1938 | United States | 9784710544 | jim@upwire-electric.com | Q120DFN | Breaker |  | 15 |  | 1 Pole | Siemens | Residence |  | 2025-08-18 | 2025-08-14 | 1 Bushnell |  | Lexington | MA | 2421 | United States | Fridge will run for about 15 minutes and then the circuit breaker trips. | Bosch | KCB36CAUS1 | None | Single Family Home | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | James McCormack
2025-08-20 06:14 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 16 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:16 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 17 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:19 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 18 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:21 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 19 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:24 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 20 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:26 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 21 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:28 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 22 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:31 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 23 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:34 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 24 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:36 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 25 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:39 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 26 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:41 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 27 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:43 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 28 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:46 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 29 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 06:48 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 30 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:09 | Anthony | Triolo | 54913-B | 220 High Street |  | Taunton | MA | 2764 | United States | 5088136244 | atrioloelectric@gmail.com | AD-910 | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_2954.jpeg&form-id=2&field-id=22&hash=27dade10aff8ec4df5f49af8bb44299b974d222b0a74bd808375773d044e33e1 | 2025-08-19 | 2025-08-19 | [6 empty] | Brand new installation, new range trips GFCI when oven is used. | Frigidaire | GCRE3060BFD |  | Residential | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_2953.jpeg&form-id=2&field-id=42&hash=25963d7907acc4592965ccd3bd927eb9a02e0c6619081c425800ea106cc77629 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Anthony Triolo
2025-08-20 10:16 | Anthony | Triolo | 54913-B | 9 Hayford Trail |  | Hanson | MA | 2341 | United States | 5088136244 | atrioloelectric@gmail.com | AD-910 | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_29541.jpeg&form-id=2&field-id=22&hash=23623c7080a869518e06ce605bf93374b174f00163f24c1c37de339f5ad893a6 | 2025-08-19 | 2025-08-19 | [6 empty] | Brand new installation, new range trips GFCI when oven is used. | Frigidaire | GCRE3060BFD |  | Residential | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_29531.jpeg&form-id=2&field-id=42&hash=eb35b1356cb9a8cc318e8628b911c0f703af89caff292a47ebedaed01cf1d6bc | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Anthony Triolo
2025-08-20 10:22 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 31 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:25 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 32 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:27 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 33 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:29 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 34 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:31 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 35 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:33 | Christopher | Stevens | 20655A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 36 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:35 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 37 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:36 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 38 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:39 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 39 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:41 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 40 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:43 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 41 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:45 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 42 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:47 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 43 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:49 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 44 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:52 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 45 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:54 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 46 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:57 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 47 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 10:59 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 48 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 11:01 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 49 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 11:02 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-18 | 2025-08-18 | 245 ESSEX STREET | UNIT 50 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-08-20 13:27 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | 2339 | United States | 781-953-4023 | starbro@verizon.net | GE THQOL1120DF | Breaker |  | 20 |  | 1 Pole | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Unit 301 |  | Quincy | MA | 2169 | United States | Bidet toilet nuisance tripping | Gijgit | GWF1418SSM1WW |  | Condo | Bathroom | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-20 13:36 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | 2339 | United States | 781-953-4023 | starbro@verizon.net | GE THQL2150 GFCI | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Unit 301 |  | Quincy | MA | 2169 | United States | Electric oven nuisance tripping | GE | PHS930YPBFS |  | Condo | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-20 13:42 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | 2339 | United States | 781-953-4023 | starbro@verizon.net | GE THQL2150 GFCI | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Unit 306 |  | Quincy | MA | 2169 | United States | Electric range nuisance tripping | Whirlpool | WFES330RZO |  | Condo | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-20 13:48 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | 2339 | United States | 781-953-4023 | starbro@verizon.net | GE THQOL20DF | Breaker |  | 20 |  | 1 Pole | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Unit 307 |  | Quincy | MA | 2169 | United States | Microwave nuisance tripping | Frigidaire | FMOS1846BWA |  | Condo | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-20 13:56 | John | Stark | 8602A | 25 Pond Street, Suite 7 |  | Hanover | MA | 2339 | United States | 781-953-4023 | starbro@verizon.net | GE THQL50 GFCI | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-07-01 | 2025-07-01 | 64 Willard Street, Unit 307 |  | Quincy | MA | 2169 | United States | Electric oven nuisance tripping | Frigidaire | CRE3062AWC |  | Condo | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John M Stark
2025-08-21 10:10 | Daniel | Greenberg | 54913B | 10 Narragansett Dr |  | W Bridgewater | Massachusetts | 2379 | United States | 7812647746 | Dgreenberg@stonebridgehomesinc.com | DP-4075 | Breaker | - | 40 | - | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FbREAKER1.jpg&form-id=2&field-id=22&hash=aaa3061be974325afb0b326ce6da262fe6c354578b473e477fb3fefdfdfbefd6 | 2025-08-21 | 2025-08-20 | 10 Narragansett Dr |  | W Bridgewater | Massachusetts | 2379 | United States | When range is turned on, the breaker will trip. | Frigidaire | VF51960188 | - | Single Family | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FRange1.jpg&form-id=2&field-id=42&hash=fa3d658aa5f2be72a04e42809f58eb9f61b287cb212dc7fece7bea0bb95e67ec , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FRange-21.jpg&form-id=2&field-id=42&hash=37803e2bd5331ffa51c1bc3df0ec2d58eda3424dfb22228fa50ef1a8723cb076 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Daniel Greenberg
2025-08-21 12:47 | Welch | Electrical Systems, Inc. | 17139A | 190 Pleasant Street |  | Rockland | MA | 2370 | United States | 781-878-6001 | wwelch@welchelectricalsystems.com | QO 250 | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-07-11 | 2025-06-13 | 55 Summer Street |  | Cohasset | MA | 2025 | United States | The stove in the kitchen tripped three to four times when the stove was turned on in July 2025. Tried to reset multiple times and changed the breaker. Neither resolved the issue. | AGA | AEL481INABBLK | None - The stove is on a separate circuit. | Single family residence | The kitchen in a single family residence. The manufacturer suggested submitting this form. | No | No | No | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | William Welch
2025-08-22 14:44 | Gustavo | Simoes | 23674A | 12 welles way |  | Chilmark | Massachussetts | 2535 | United States | 774 563 4988 | jbsimoes2@gmail.com | GFTCB250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-08-22 | 2025-08-21 | 47 Kings highway |  | Chilmark | MA | 2535 | United States | Breaker constantly trips overnight and sometimes while in use. | Harmony Liberty | PRI36LBHU |  | Single Family Dwelling | Kitchen | No | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | GSS
2025-08-26 11:41 | Gustavo | Simoes | 23674-a | 8 N line rd |  | Edgartown | Ma | 2539 | United States | 5083382341 | gsselectricmv@gmail.com | LB120DFT | Breaker |  | 20 |  | 1 Pole | Leviton | Residence |  | 2025-08-25 | 2025-08-23 | 426 Bigelow rd |  | Vineyard Haven | MA | 2568 | United States | Fridge (subzero) trips | Sub Zero | CL4850UFD/0 | N/A | single dwelling | kitchen fridge | No | Yes | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Gustavo Simoes
2025-08-26 15:30 | Timothy | Kent | 23633A | 220 Foster rd |  | Tewksbury | Massachusetts | 1876 | United States | 9786042857 | tkent@netrinc.com | BRN250GF | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2024-11-21 | 2024-10-04 | 11 Great Woods Terrace |  | Lynn | Massachusetts | 1904 | United States | we conducted a service upgrade and had to replace the range line to make it code compliant. We installed a GFCI 50A breaker as required by State code and since then the breaker keeps tripping when the customer uses there stove. we have tested and inspected all the connections from the range to the panel and we have change out the breaker twice now. still having same problem. | General Electric | JB3000R1WW |  | Single Family | The Kitchen range. | No | Yes | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Timothy Kent
2025-08-28 14:55 | Francisco | Toste | E34419 | 86 addington | None | Brookline | MA | 2445 | United States | 5084007384 | tosteelectric@gmail.com | Gftcb250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-08-28 | 2025-08-21 | [6 empty] | Heated oven with standard 50 Amp breaker, then install 50 GFCI trips about minute later. | Wolf | DO3050PE/S/P |  | 2 family | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2F20250828_145323.jpg&form-id=2&field-id=42&hash=d7061f0c2c16110a0faa7fcc63e135eb7cab6db20cdb3e09c2f990ee9be4af83 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Francisco A Toste
2025-08-29 07:31 | Chris | Polny | 11660B | 325 Hopping Brook |  | Holliston | MA | 1746 | United States | 7742178986 | christopherpolny@rodenhiser.com | Square D Homeline HOMGFCIP | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-08-13 | 2025-08-13 | 264 Seminloe Ave |  | Waltham | MA | 2451 | United States | Multiple nuisance tripping for the Range | Frigidaire | GCRE3038AFG | None | Dwelling | Only the range | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Chris Polny
2025-08-29 08:51 | Chris | Polny | 11660B | 325 Hopping Brook |  | Holliston | MA | 1746 | United States | 7742178986 | christopherpolny@rodenhiser.com | Eaton BRN240GF | Breaker |  | 40 |  | 2 Poles | Eaton | Residence |  | 2025-06-03 | 2024-09-09 | 35 Elliot St |  | Sherborn | MA | 1770 | United States | Trips overnight when not in use | LG | WCEP6423 | None | Dwelling | Wall oven / microwave only | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Chris Polny
2025-08-30 13:59 | David | Ferreira | 23573A | 3 Pine Hill Ave |  | Chelmsford | MA | 1824 | United States | 9789684144 | davidferreira96@hotmail.com | Eaton BRN240GF | Breaker |  | 40 |  | 2 Poles | Eaton | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_8762.png&form-id=2&field-id=22&hash=2893aecca337d2946c7bc35e6d1f08824b7bdd77268e76a29d5dc1cd383dba84 | 2025-08-05 | 2023-11-29 | 43 monmouth st |  | boston | ma | 2128 | United States | 3 family house got remodeled back in 2023, stayed vacant till late 2025. Once occupied, tenant complained that it keeps tripping when they use the stove part. We tried a different breaker, brand new out of the box, and same problems occurs. We troubleshot, but everything seems to be in order. Then we processed to remove it from a gfci breaker to a regular breaker. | WHIRLPOOL | WFE535S0L72 |  | APARTMENT | Kitchen, trips when baking things in the oven. | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F08%2FIMG_87621.png&form-id=2&field-id=42&hash=bda540f1b15f51ba576ce2739cf9cea77427ffde8282dd591903a195436aa41c | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | David Ferreira
2025-09-02 10:38 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | United States | 4132430690 | OWNER/VP | JOHN@HENRYSELECTRICINC.COM | EATON / BR250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-06 | 2025-06-06 | 49 MAIN RAOD |  | TYRINGHAM | MA | 1264 | United States | BREAKER DOES NOT HOLD, KEPT TRIPPING. | LG | LSIL6336FE |  | SINGLE FAMILY | KITCHEN | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | JOHN LEPREVOST | 2025-09-02
2025-09-02 11:26 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET |  | LEE | MA | 1238 | United States | 4132430690 | OWNER/VP | JOHN@HENRYSELECTRICINC.COM | SQUARE QO | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence |  | 2025-08-29 | 2025-04-17 | 1425 PLEASANT STREET |  | SOUTH LEE | MA | 1260 | United States | BREAKER DOES NOT HOLD, KEPT TRIPPING. | CAFE | CHS950P2MS1 |  | SINGLE FAMILY | KITCHEN | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | JOHN LEPREVOST | 2025-09-02
2025-09-03 08:30 | Brian | Bradley | 20351A | 118 Forest Ave |  | Hudson | MA | 1749 | United States | (978) 212-8014 | Owner/Electrician | bbelectric.permits@gmail.com | M2408220580 | Breaker |  | 60 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F337c7d0468a8271f464e626177e6248cf33502ea-1.jpg&form-id=2&field-id=22&hash=d271ad0c64843e1f83446f213a58a43d5e7ee41c6aa0959c609227d72b6c47a6 | 2025-08-29 | 2025-08-27 | 102 Oak Trail |  | Bolton | MA | 1740 | United States | When operating the new range GFCI breaker trips. Occurs every time the range attempt to heat. | Thermador | PRD486WDHU | None | Single Family - Residential | Kitchen | Yes | No | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F337c7d0468a8271f464e626177e6248cf33502ea-2.jpg&form-id=2&field-id=42&hash=e1a2f5bfd97ea13390f433d752302f2bd750a99a21e86629bb2a975650b2b224 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F337c7d0468a8271f464e626177e6248cf33502ea-3.jpg&form-id=2&field-id=42&hash=567ab2632cc81b80e913fb481dbe5f8b940c342de5802b984e8306a95d9ef8d8 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Brian Bradley | 2025-09-03
2025-09-03 10:22 | Jonathan | Harris | 21234A | 6 Granite Rd | Unit #6 | Kingston | NH | 3848 | United States | 603-301-5112 | President/ Master Electrician | ashley@lifestyleselectric.com | QOB350GFI | Breaker |  | 50 |  | 3 Poles | Schneider Electric | Commercial |  | 2025-08-23 | 2025-08-24 | 430 Boston Rd |  | Billerica | MA | 1821 | United States | GFCI Breaker continuously tripping pizza oven. | Doyon | PIZ6 | N/A | Mangia Mangia Italian Kitchen | Kitchen | No | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jonathan Harris | 2025-09-03
2025-09-03 11:34 | John | Vespa | A17144 | 250 Milton St LL007 |  | Dedham | MA | 2026 | United States | 617 325 1151 | Owner | Vespa@johnvespaelectrical.com | BRN240GF | Breaker |  | 40 |  | 2 Poles | Eaton | Commercial |  | 2025-07-02 | 2025-06-26 | 455 Arborway |  | Jamaica Plain | MA | 2130 | United States | Breaker continuously nuisance tripping, not compatible with range unit. | ZLine | RASZ-WM-60-G |  | Church | kitchen range | No | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John Vespa | 2025-09-03
2025-09-03 11:36 | John | Vespa | A17144 | 250 Milton St LL007 |  | Dedham | MA | 2026 | United States | 617 325 1151 | Owner | Vespa@johnvespaelectrical.com | BRN240GF | Breaker |  | 40 |  | 2 Poles | Eaton | Commercial |  | 2025-07-02 | 2025-06-26 | 455 Arborway |  | Jamaica Plain | MA | 2130 | United States | Breaker continuously nuisance tripping, not compatible with range unit. | Thermador | prd606weg |  | Church | kitchen range | No | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John Vespa | 2025-09-03
2025-09-03 15:04 | Mark | VanMolle | A-13527 | PO Box 1534 |  | Littleton | MA | 1460 | United States | 978-337-6541 | Contractor | castlecp@hotmail.com | QF260 | Breaker |  | 60 |  | 2 Poles | Siemens | Residence |  | 2025-08-01 | 2025-08-01 | 95 Highland St. |  | Dunstable | MA | 1827 | United States | Installed a new 2-pole 60-amp GFCI breaker on a new range. It continuously trips. | Kitchen Aid | KSDB900ESS |  | Single Family. | Kitchen. | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark VanMolle | 2025-09-03
2025-09-03 19:23 | Joseph F | Brennion | 50066 | 5 Lee Cir |  | Hudson | MA | 1749 | United States | (774) 245-7628 | Electrician | jfbrennionelectric@gmail.com | Siemens | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-09-02 | 2025-08-20 | 805 Farm Road |  | Marlborough | MA | 1752 | United States | Every time the range is turned on after 3-4 minutes the breaker trips and the range never gets hot | Whirlpool | Accubake |  | Single family | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Joseph F Brennion | 2025-09-03
2025-09-04 06:26 | Jesse | Kuhlman | 21804-A | 313 Eastern Avenue |  | Lynn | MA | 1902 | United States | 617.741.5043 | Owner | Ervis.Bushi@callkuhlman.com | HOM250GFICP | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-08-29 | 2025-08-29 | 120 Beacon St |  | Boston | Massachusetts | 2116 | United States | Breaker would not hold when both cooktop and oven were put on. | Wolf Appliance | IR30450/S/T |  | Apartment | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jesse Kuhlman | 2025-09-04
2025-09-04 07:33 | DAN | WHITELEY INC | 22453A | 52 COTTAGE ST |  | EASTHAMPTON | MA | 1027 | United States | 4135271440 | PRESIDENT | WHITELEYELECTRIC@AOL.COM | BRN230GF | Breaker |  | 30 |  | 2 Poles | Eaton | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FScreenshot-2025-09-04-at-7.26.56-AM.png&form-id=2&field-id=22&hash=990644bf7e9aee22c1b89828ef601d9380fac708a1f34b2914bc96380851e7e7 | 2025-08-29 | 2025-06-11 | 61 GREEN AVE |  | BELCHERTOWN | MA | 1007 | United States | NUSANCE TRIPPING | GE APPLIANCE | PTD70EBPT1DG | NONE | DWELLING | DRYER | Yes | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FScreenshot-2025-09-04-at-7.26.56-AM1.png&form-id=2&field-id=42&hash=52937331597d29a53c0001889dfad125288386e92be3bd64828fb0d324cc5cc6 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | DANIEL S WHITELEY | 2025-09-04
2025-09-04 14:17 | Francis | Baudanza | Master 7755 Journeyman 20326 | 5 Hilltop Dr |  | Bedford | MA | 1730 | United States | 781-275-6662 | President | baudanza@erols.com | Siemens 2 pole 40 amp gfci | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-09-03 | 2025-06-05 | 37 Mitchell Grant Way |  | Bedford | MA | 1730 |  | When the oven is used it trips the gfci breaker | Kenmore | 790.9641 |  | kitchen | the kitchen stove | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Francis Baudanza | 2025-09-04
2025-09-04 15:03 | Brian | Bradley | 20351A - 29707E - 8069A1 | 266 | Sudbury St | Marlborough | MA | 1752 | United States | 978-212-8014 | Owner | bbelectric.permits@gmail.com | Siemens QF260A | Breaker | None | 30 |  | 1 Pole | Siemens | Residence |  | 2025-08-28 | 2025-08-23 | Lincoln MA 01733 - Basement - Indoor Sauna | 19 Oak Meadow Rd | Lincoln | MA | 1773 |  | Manufacturer recommends not using a GFCI breaker when wiring their saunas. GFCI breaker will remain on for about five minutes while sauna is operating and then trips. | HUUM Hive 6kW Heater | HUUM6KVA | n/a | Single family home | Sauna is the only thing that trips. | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Brian Bradley | 2025-09-04
2025-09-04 21:29 | Jesse | Kuhlman | 21804-A | 313 Eastern Avenue |  | Lynn | MA | 1902 | United States | 6177415043 | owner | Ervis.Bushi@callkuhlman.com | US2:QF250AP | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-09-04 | 2025-09-04 | 37 Wachusett St. Unit 3 |  | Boston | Massachusetts | 2130 | United States | Breaker would trip after oven was on for about 2 minutes | Frigidaire | GCFI3060BFD |  | Apartment | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jesse Kuhlman | 2025-09-04
2025-09-04 21:42 | Jesse | Kuhlman | 21804-A | 313 Eastern Avenue |  | Lynn | MA | 1902 | United States | 6177415043 | Owner | Ervis.Bushi@callkuhlman.com | HOM250GFICP | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-09-04 | 2025-09-04 | 37 Wachusett St. Unit 1 |  | Boston | Massachusetts | 2130 | United States | Breaker would trip when oven would be on for about 2 minutes. | Frigidaire | GCFI3060BFD |  | Apartment | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jesse Kuhlman | 2025-09-04
2025-09-05 09:41 | Mark | Thibault | A14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-08-22 | 2025-08-23 | 2 Winslow Lane Unit 205 |  | Grafton | Massachusetts | 1536 | United States | When warming up the oven. | Whirlpool | WFES3530RS0 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark J Thibault | 2025-09-05
2025-09-05 09:44 | Mark | Thibault | A14667 | 1 Industrial Way Unit #5 |  | Tyngsboro | Massachusetts | 1879 | United States | 6034906301 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-08-28 | 2025-08-29 | 4 Stratton Drive Unit 205 |  | Woburn | Massachusetts | 1801 | United States | When warming up the oven. | Whirlpool | WFES3530RS0 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark J Thibault | 2025-09-05
2025-09-08 10:07 | Joseph | Giacalone | 1035A1 | #451-#455 Essex Street |  | Beverly | MA | 1915 | United States | 978-879-6850 | Project Manager | joseph@giacalonegc.com | Part No. 2097W | Breaker | Part No. 2097W | 20 |  | 1 Pole | Legrand | Residence |  | 2025-05-30 | 2025-04-30 | [6 empty] | In all 5 Town homes located at 451-455, all 5 ovens are rendered unusable, as they trip almost immediately. | Frigidaire | GCRE3060BD, GCRE3060BF |  | Townhouse | In all 5 Town homes located at 451-455, all 5 ovens are rendered unusable, as they trip almost immediately. | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Joseph Giacalone | 2025-09-08
2025-09-08 10:14 | Liniker | Goncalves | 22803A | 26 Buckhill rd | 222 Turnpike Rd | 26 Buckhill rd | Northborough | MA | United States | 8578884280 | President | liniker@lgelectric-inc.com | Leviton LB230-G | Breaker |  | 30 |  | 2 Poles | Leviton | Residence |  | 2025-08-15 | 2025-08-12 | 281 Franklin st |  |  | Boston | MA |  | When dryer kicks on, it trips the breaker. | LG | WKE100H_A / WKG101H_A |  | Building | 201 202 203 301 302 303 401 402 403 501 502 503 601 602 603 | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Liniker G | 2025-09-08
2025-09-09 08:42 | Philippe | Thibeault | 22128 | 276 Lexington st |  | Newton | Ma | 2456 | United States | 9788156009 | Owner | cmkillion@yahoo.com | Square d | Breaker |  | 20 |  | 1 Pole | ABB | Residence |  | 2025-09-04 | 2025-09-02 | [6 empty] | Thermidor hood trips when fan turns on | Thermador | Hood |  | Single gamily | When exhaust turns on | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Philippe Thibeault | 2025-09-09
2025-09-09 09:41 | James | McCormack | 22340 A | 196 High St | Unit 2 | Ipswich | f0c26795-e510-e311-ba31-d43d7e4e88b2 | 1938 | United States | 9782388250 | Owner | jim@upwire-electric.com | Siemens | Breaker |  | 15 |  | 1 Pole | Siemens | Residence |  | 2025-09-07 | 2025-08-22 | 1 Bushnell Dr |  | Lexington | MA | 2421 | United States | After time breaker will trip, nothing notable triggers it | Bosch | B36CT80SNS | None | Single Family Home | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | James McCormack | 2025-09-09
2025-09-09 10:00 | James | McCormack | 53625 B | 196 High St | Unit 2 | Ipswich | f0c26795-e510-e311-ba31-d43d7e4e88b2 | 1938 | United States | 9782388250 | Owner | jim@upwire-electric.com | Q115DF | Breaker |  | 15 |  | 1 Pole | Siemens | Residence |  | 2025-09-07 | 2025-08-14 | 1 Bushnell Dr |  | Lexington | MA | 2421 | United States | Breaker trips after some time, no apparent trigger | Miele | G 5008 SCU |  | Single Family Home | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | James McCormack | 2025-09-09
2025-09-09 10:11 | James | McCormack | 53625 B | 196 High St | Unit 2 | Ipswich | f0c26795-e510-e311-ba31-d43d7e4e88b2 | 1938 | United States | 9782388250 | Owner | jim@upwire-electric.com | Q120DF | Breaker |  | 20 |  | 1 Pole | Siemens | Residence |  | 2025-09-06 | 2025-09-02 | 12 Livingston |  | Newbury | MA | 1951 | United States | Breaker trips for no apparent reason after a period of time | Fisher & Paykel | RS3684WRUVE1 | NONE | Single Family Home | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | James McCormack | 2025-09-09
2025-09-09 11:43 | William | Morrissey | 53986 | 100 Malden St |  | Revere | MA | 2151 | United States | 7815603354 | Electrician | wmorrissey@hotmail.com | HOM230GFIC | Breaker |  | 30 |  | 2 Poles | Schneider Electric | Residence |  | 2025-09-03 | 2025-09-03 | 9 Penniman st |  | Brookline | MA |  |  | Breaker tripping during initial startup. | GE | PFD87ESSV0W | None | Single Family | Laundry Room | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | William Morrissey | 2025-09-09
2025-09-09 13:29 | STEVE | GILBERT | A21845 | PO 534 |  | Pepperell | MA | 1463 | United States | 9788358921 | OWNER | sgilbert74@msn.com | THQL2130GF | Breaker |  | 30 |  | 2 Poles | ABB | Residence |  | 2025-06-25 | 2025-08-28 | 308 CONCORD RD |  | SUDBURY | MA | 1776 |  | HAD PROBLEMS AND WE TRIED A NEW BREAKER/ APPLIANCE COMPANY TRIED NEW BOARD AND SAME RESULSTS | FISHER AND PAYKEL | OR36SDI6X1 |  | SINGLE FAM | KITCHEN OVEN | No | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | STEVEN GILBERT | 2025-09-09
2025-09-09 13:55 | Mark | Roussel | A21100 | 33 old forge Ln |  | Sudbury | MA | 1776 | United States | 9784438888 | Electrician/owner | Baseball78@verizon.net | ABB GE THQL2150GFT2P | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-09-08 | 2025-09-08 |  | 118 Peakham Rd | Sudbury | MA | 1776 | United States | At initial installation GFCI holds fine - 30 seconds after charger is plugged into car charge port the GFCI consistently pops (Same problem occurs with a replacement GFCI breaker) | ABB GE | Grissl-E-Duo | nothing | residential 2 car gargage | The only area affected by this trip is garage (specifically the dedicated circuit to the car charger) | No | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2Fnameplate.jpg&form-id=2&field-id=42&hash=933b9fa5fdbfb186a84a0e3bcb2c96c4a5aa31b8ba708112fe7d2000192943d2 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark R Roussel | 2025-09-10
2025-09-10 10:24 | Daniel | Greenberg | 54913B | 25 Metacomet Rd |  | West Bridgewater | MA | 2379 | United States | 508-230-2300 | Construction Manager | Dgreenberg@stonebridgehomesinc.com | DP-4075 | Breaker | - | 40 | - | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FbREAKER.jpg&form-id=2&field-id=22&hash=af0593c959accc543bb39fdc78c477b2ab696c816b8a4965e86272fd6dccc9c6 | 2025-09-04 | 2025-09-02 | [6 empty] | Range trips whenever its turned on. | Whirlpool | VF51960188 | - | Single Family Home | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FRange.jpg&form-id=2&field-id=42&hash=214a5a587826e152229f2336033f54995e0b6f20ec645b84173c8dd11c2496a7 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FRange-2.jpg&form-id=2&field-id=42&hash=6dcf6d7afd26414648f513502425691c93d817b09c230ab2352edb3203b6a37d | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Daniel Greenberg | 2025-09-10
2025-09-10 11:05 | Jesse | Kuhlman | 21804-A | 313 Eastern Avenue |  | Lynn | MA | 1902 | United States | 6178406252 | Owner | Ervis.Bushi@callkuhlman.com | Q120DF | Breaker | Q120DF | 20 | 20 | 1 Pole | Siemens | Residence |  | 2025-09-10 | 2025-09-05 | 119 W 3d St. Unit A |  | South Boston | Massachusetts | 2155 | United States | Customer bought a Washer and a Dryer made by Miele. They both trip at the end of the cycle. | Miele | Dryer 11619650, Washer 11614070 Type HW21 | no | Apartment | Laundry closet. Dedicated circuits. | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jesse Kuhlman | 2025-09-10
2025-09-10 11:30 | Joseph | MacDonald | B-14940 | 49 Sargent st |  | Quincy | Ma | 2169 | United States | 6178750103 | Electrician | jmacdonald1225@gmail.com | Eaton GFTCB230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-09-06 | 2025-09-06 | 369 Pond st |  | Rockland | Ma | 2370 | United States | Dryer 30amp 2 pole GFI breaker trips as soon as the equipment is plugged into receptacle | LG | WKEX200H*A | None | Single family house | Dryer receptacle in bathroom is the only breaker/equipment is affected. | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Joseph MacDonald | 2025-09-06
2025-09-10 13:24 | Cole | Powers | 36860 | 151 Beach Rd | #4549 | Vineyard Haven | Massachusetts | 2568 | United States | 5086966400 ext.101 | President/Master Electrician | powerselectric@comcast.net | QO250GF | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-09-01 | 2025-01-04 | 20 Jennie Lane |  | Edgartown | Massachusetts | 2539 | United States | When the induction cooktop is turned on and is in use, the GFCI breaker trips. | Bosch | NITP660UC/1 | None | Residential | The induction cooktop is in the central kitchen/cooking area of the house. | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Cole Powers | 2025-09-10
2025-09-10 14:16 | Mark | Flores | 52255b | 97 Groveland Ave |  | South Weymouth | MA | 2190 | United States | 7816643215 | President | Mark@MAFElectrician.com | HOM250GFICP | Breaker |  | 30 |  | 2 Poles | Schneider Electric | Residence |  | 2025-09-10 | 2025-08-15 | 160 Edward Foster Rd |  | Scituate | MA | 2066 | United States | Wolf Dual Fuel Range/oven. Trips while on High Temp, Had appliance man out to go through Range, and all checked out OK. Heating Elements where they should be both OHM wise and installation wise. | Wolf | DF366 | None | Single Family Dwelling | Kitchen , kitchen area , place to cook | No | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark A Flores | 2025-09-10
2025-09-10 16:52 | Giombetti | Electric, Inc. | A13678 | 401 SOUTH STREET |  | Marlborough | MA | 1752 | United States | 5084813299 | President | Mike@giombettielectric.com | CHN240GF | Breaker |  | 40 |  | 2 Poles | Eaton | Residence |  | 2025-09-10 | 2025-09-10 | 29 Pleasant Street | Apartment A5 | Marlborough | MA | 1752 | United States | The GFCI breaker trips after about 1 minute of using the stove | Hop Point General Electric | RAS240DM1WW | None | Apartment | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F1000002106.jpg&form-id=2&field-id=42&hash=a7cfa4a7615dea508d032a0d49b9c7e5b97a7abdedbd81dcf8fb5f8c0e2f6b11 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F1000002108.jpg&form-id=2&field-id=42&hash=a6b26e82e3ad87529d6d7ff3d101be8dca63fd51ea2720dce694c6b4d3dff424 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F1000002109.jpg&form-id=2&field-id=42&hash=ada62c1b914173e02d53908a72c01fb9d4c46033e31a6fad66abd3ebb91b6706 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F1000002110.jpg&form-id=2&field-id=42&hash=44372b3aff9d1859ef60f5e57bd2576629afcd90bff3cc2db858968e4f144069 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F1000002107.jpg&form-id=2&field-id=42&hash=f7792d6f6f25fa41e2f341d3bad1658226ccf32cc6cddaf96c08e61856cdc054 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F20250910_103233.jpg&form-id=2&field-id=42&hash=e09e6c0d205d839cd545ed1b645dab71f8ee69c733f419e58cb288bec9770ebf | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Michael A Giombetti | 2025-09-10
2025-09-11 12:30 | Michael | Raymond | A21550 | 24 Trumbull Ave |  | Haverhill | MA | 1832 | United States | 9788072065 | Owner | michael@mgrelectrical.net | HOM230GFIC | Breaker |  | 30 |  | 2 Poles | Schneider Electric | Residence |  | 2025-09-11 | 2025-06-01 | 4 Coventry Lane |  | Andover | MA | 1810 | United States | Customer complaint that the Wall oven trips the GFCI intermittently when the oven is in use and when the oven is not in use. We responded to make certain that that we had no circuit integrity issues. We disconnected the Appliance and the circuit from the GFCI breaker tested the cable with a meter to verify that we had good dielectric strength on the insulated conductors to ground confirmed that we had no cable issues. Reconnected the appliance and ran the appliance through different functions over the course of a full day and found the breaker to be tripping intermittently. Disconnected the equipment grounding conductor at the panel board and found leakage voltage to the equipment grounding conductor of 35 to 69 V. reconnected the equipment grounding conductor at the panelboard. pulled the appliance out of its location. Disconnected the equipment, grounding conductor at the Appliance whip. Verified that we had 35 to 69 V leaking to the chassis of the cabinet, therefore leaking to the equipment conductor. Reconnected the appliance and re-installed into the wall cavity. Customer has complained that the equipment continues to trip. Recommended that the customer call the manufacturer to have a manufacturers rep troubleshoot, the appliance. The appliance manufacturer sent out a form letter stating that the Appliance was incompatible with a GFCI protected circuit and broadly recommended that we ask the AHJ for permission to remove the GFCI protection. I refused to remove the GFCI protection as I consider leaking voltage to the chassis cabinet and unsafe condition. The last line of The third paragraph of the “Emergency Amendment to Mass. Electrical Code (527 CMR 12.00)” states that “Importantly, the amended language disallows the elimination of required GFCI protection in instances where malfunctioning appliances are deservedly causing GFCI protective devices to discontinue power” I believe this appliance as designed is faulty. I further stated that the GFCI breaker is be behaving exactly as it was designed. When asked by the customer how many volts were acceptable to leak to the chassis of the cabinet, I answered zero. I Explained that the equipment grounding conductor is not designed as a return path for any circuit and that it is for incident fault current only. I recommended that he go back to the manufacturer and demand a proper remedy and a rework of their internal circuit design within their appliance so that is compatible with a GFCI protected circuit. I will not install a non GFCI breaker and place this family in harms way because of a manufacturers design flaw. On a side note, I personally have lost hundreds of hours and have lost tens of thousands of dollars troubleshooting inferior products that have had no R&amp;D done in the lab, before dumping their garbage on us in the field only to be made to look like a clowns in our customers eyes. Manufacturers of appliances, electrical equipment and code making panels need to get on the same page. This is ridiculous and an embarrassment. Signed Michael G. Raymond. Call me if you want to have a spirited conversation. | Wolfe | CONAPPWM | None | Single family | Kitchen wall oven. | No | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Michael G Raymond | 2025-09-11
2025-09-11 21:37 | Stephen | Cappadona | 54255 | 128 Essex Street |  | Marlborough | MA | 1752 | United States | 5083970009 | Electrician | scapelectric@gmail.com | Square d QO | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-09-02 | 2025-09-01 |  | 12 bruce st |  | Grafton | Ma | United States | When the oven starts to pre heat the breakers shuts off | Frigidaire | Gallery GCFE3060BF |  | House | Kitchen oven | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Stephen cappadona | 2025-09-11
2025-09-15 10:22 | Tyler | Daniels | 1971 | 895 | Salem Street-2A | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | Eaton | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-09-08 | 2025-09-08 | 3 Boston Way | Salem Street-2A | Newburyport | MA | 1950 | United States | Continual tripping | Stove | JB645EK9ES |  | Residential | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels | 2025-09-15
2025-09-15 10:25 | Tyler | Daniels | 1971 | 895 | Salem Street-2A | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | Eaton | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-09-08 | 2025-09-15 | 3 Boston Way |  | Newburyport | MA | 1950 |  | Stove continually tripping | GE | JB645EKE9ES |  | Residential | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels | 2025-09-15
2025-09-15 11:12 | STEVEN | GIBERT | A21845 | PO 534 | PO 534 | Pepperell | MA | 1463 | United States | 9788358921 | OWNER | sgilbert74@msn.com | HOM250GFICI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-08-30 | 2025-08-07 | PO 534 | 5 WESTAVAL | Pepperell | MA | CONCORD | United States | GFCI TRIPS EVERYTIME THE DURRING BAKE | KENMORE | 790.942 |  | SINGLE FAM | KITCHEN OVEN | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Steven Gilbert | 2025-09-15
2025-09-15 11:20 | Mark | Thibault | A14667 | 1 Industrial Way Unit #5 |  | Tyngsboro | Massachusetts | 1879 | United States | 6034906301 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-09-05 | 2025-09-06 | 5 Goodwin Drive | Woburn |  | Massachusetts | 1801 | United States | When warming up the oven | Whirlpool | WFE5350LS3 |  | Townhouse | Kitchen | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark J Thibault | 2025-09-15
2025-09-16 07:26 | Mark | Dumais DUMAIS ELECTRIC, Inc. | 12170 A | 8 Newport Street |  | Methuen | MA | 1844 | United States | 978-683-9438 | President / Owner | mdumais@dumaiselectric.com | Siemens Q120DFN | Breaker | Combination Arc Fault / GFCI | 20 |  | 1 Pole | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FRiccio-Appliance-Report.pdf&form-id=2&field-id=22&hash=ec4832372af397f53effa70431b59d2607b825712158c648b0bb07dd10385bc7 | 2025-09-10 | 2025-08-12 | 9 Bradstreet Road | 8 Newport Street | North Andover | MA | 1845 | United States | During a certain cycle in the refrigerator operation the GFCI breaker trips. This happens several times in a 24 hour period. | Bosch | B36CT80SNS/45 | None | Kitchen | Kitchen Refrigerator ONLY | No | Yes | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FFridge-Rough.jpg&form-id=2&field-id=42&hash=fb9e36be929cf695d44bcd0466747c2e1993b5124e98acf6904cfc707ba4e8dd , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FFridge-Name-Plate.jpg&form-id=2&field-id=42&hash=ca88f50ec53ee806a1173defa36181678f04241e4442c1578e90f519a6db2389 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark A Dumais | 2025-09-16
2025-09-16 17:01 | Mark | Raposo | 20105 A | 141S Main Street |  | Assonet | MA | 2702 | United States | 5089859555 | Master electrician | tiffany@raposoelectricinc.com | BRN250GF | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-09-10 | 2025-09-10 | 1605 Village Rd West |  | Norwood | MA | 2062 | United States | Resident stated that the breaker would trip every time they attempted to used / turn on the oven on the range. | Whirlpool | WFE320M0JS0 | N/A | Townhouse | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Raposo | 2025-09-16
2025-09-17 07:47 | Jake | Carlan | 1971 | 895 | Salem Street-2A | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | X010918290 | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-08-03 | 2025-09-16 | 33 Woodcock Ave Unit 13 |  | Haverhill | MA | 1832 | United States | continous tripping on stove when stove preheats | Whirlpool | WFC31580JB3 | none | Apartment | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jake Carlan | 2025-09-17
2025-09-17 11:34 | Joseph | OBrien | 20729 | 12 Oakwood | 12 Oakwood rd | Wilmington | MA | 1887 | United States | 7818444606 | Owner/Electrician | jpobrienelectric@verizon.net | Model # R92-GFTR1-0KW | Receptacle |  | 15 |  | 1 Pole | Leviton | Residence |  | 2025-09-02 | 2025-09-04 | 5 Junction Rd | 12 Oakwood rd | Wilmington | Ma | North Reading | United States | - Portable ac unit tripped gfci outlet. Tried other gfci outlets in garage which the ac unit also tripped. - Installed dedicate 20amp 120volt circuit to garage. - Installed single outlet for ac unit. - Label no gfci protection, ac unit only. | Midea | map14hs1TBL | none | Single family | Garage | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Joseph OBrien | 2025-09-17
2025-09-17 11:54 | Eric | Caldon | 21306a | 100 Deanville Rd |  | Attleboro | MA | 2703 | United States | 7742296409 | owner | Ecaldonmidstate@gmail.com | Cutler hammer | Breaker |  | 50 |  | 2 Poles | Eaton | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F28-HAmmond-appliance.jpg&form-id=2&field-id=22&hash=ac1960023074961e3fcbf2fe8be7c36e4128f58a8425437f29022dedaef80917 | 2025-09-09 | 2025-06-15 | Residence | 28 Hammond St | Attleboro | MA | Seekonk | United States | Convention oven is tripping | Thermador | POD301RW/06 |  | Kitchen | The oven breaker trips when in use | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F28-HAmmond-appliance1.jpg&form-id=2&field-id=42&hash=873329df30b801440710b409a35260cbb63a8fb8f9b8500e4a4a4faa460c3b71 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Eric Caldon | 2025-09-17
2025-09-17 12:01 | Eric | Caldon | 21306a | 100 Deanville Rd |  | Attleboro | MA | 2703 | United States | 7742296409 | owner | Ecaldonmidstate@gmail.com | Cutler HAmmer | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-09-12 | 2025-06-01 | 34 Hammond St |  | Seekonk | MA | 2703 | United States | The clothes dryer keeps tripping when in use | Samsung | DVE5075300C/A3 | none | laundry room | laundry room | Yes | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F34-Hammond.jpg&form-id=2&field-id=42&hash=cc15d6a344e5e35f78f22c8595942be628b84e92b5a5b396cdc6b331dd28a783 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Eric Caldon | 2025-09-17
2025-09-18 07:25 | DAN | WHITELEY | 22453A | 52 COTTAGE ST |  | EASTHAMPTON | MA | 1027 | United States | 4135271440 | PRESIDENT | WHITELEYELECTRIC@AOL.COM | EATON BRN230GF | Breaker | GFCI | 30 |  | 2 Poles | Eaton | Residence |  | 2025-09-10 | 2025-08-29 | 197 NORTH ST |  | BELCHERTOWN | MA | 1007 | United States | NUISANCE TRIPPING | ELECTROLUX | BLTE7300AWM | NONE | DWELLING | LAUNDRY ROOM | Yes | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | DANIEL S WHITELEY | 2025-09-18
2025-09-18 07:33 | DAN | WHITELEY | 22453A | 52 COTTAGE ST |  | EASTHAMPTON | MA | 1027 | United States | 4135271440 | PRESIDENT | WHITELEYELECTRIC@AOL.COM | EATON BRN240GF | Breaker |  | 40 |  | 2 Poles | Eaton | Residence |  | 2025-09-10 | 2025-08-28 | 197 NORTH ST |  | BELCHERETOWN | MA | 1007 | United States | NUISANCE TRIPPING | FRIGIDAIRE | FCF13082BSA | NONE | DWELLING | KITCHEN RANGE | Yes | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | DANIEL S WHITELEY | 2025-09-18
2025-09-18 09:57 | Tyler | Daniels | 1971 | 895 | Salem Street-2A | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | BRP120F | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-06-07 | 2025-07-31 | 3 Wainwright | Unit 410 | Winchester | MA | 1890 |  | Continuous tripping | GE | JGSS66SELSS |  | Apartment | kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels | 2025-07-31
2025-09-18 13:37 | Steven | Rooney | E50969 | 401 South Street |  | Marlborough | MA | 1752 | United States | 5084813299 | service manager | Steven@Giombettielectric.com | GFTCB250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-09-12 | 2025-08-16 | kitchen | 4 Townline Road | Franklin | MA | 2038 | United States | tripped well pre-heating wall oven | Wolf Appliance | CONAPPWM |  | Kitchen | wall oven | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Steven Rooney | 2025-09-18
2025-09-19 11:03 | Mark | Thibault | A14667 | 1 Industrial Way Unit #5 |  | Tyngsboro | Massachusetts | 1879 | United States | 6034906301 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-09-18 | 2025-09-19 | 2 Winslow Lane Unit 109 |  | Grafton | MA | 1536 | United States | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault | 2025-09-19
2025-09-19 12:00 | Scott | McLoud | 33374E | 419 Summer st | n/a | East Bridgewater | MA | 2333 | United States | 6179300708 | Division Manager | scott.mcloud@callkuhlman.com | Square D, Homeline | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-09-04 | 2025-08-28 | 71 Brookside Ave |  | Brockton | MA | 2301 | United States | GFCI circuit breaker tripping during oven pre-heat | GE | JBS360DMWW |  | Single family | Kitchen Electric range | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Scott McLoud | 2024-09-05
2025-09-19 13:52 | Robert W | Pasquariella Jr DEI Systems, LLC | 33599E | 35 Hunewill Ave |  | Medford | Massachusetts | 2155 | United States | 617-719-8953 | Project Manager DEI Systems, LLC | rpasquariella@deisystems.com | NK Technologies AGU1-SDT-120-DEN-005-FL | Relay/Contactor |  | 50 |  | 3 Poles | Siemens | Commercial |  | 2025-09-11 | 2025-09-05 | 94 Shirley St |  | Boston | MA | 2119 | United States | We were hired to wire a commercial kitchen in a existing commercial building with electric fryers under the hood which require shunt trip &amp; GFCI protection. This product is one of the only options when GFCI is required with shunt trip breakers relays that use the shunt trip to trip breaker when a ground fault is detected. We installed on the fryers and after a little time during use, they trip. We reset checked everything, didn&#039;t find any issues. Left, they tripped again so we removed the GFCI relays and works without any issue. | Henny Penny | 500CFA |  | Commercial Kitchen | Kitchen | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Robert W Pasquariella Jr | 2025-09-19
2025-09-22 13:19 | Andrew | Harland | 21030A | Harland Electric | PO Box 94 | Littleton, MA | MASSACHUSETTS | 1460 | United States | 9784868154 | President | andy@harlandelectric.com | Eaton BRN250GF | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-09-22 | 2025-09-17 | 42 Highland Ave |  | Ayer | MASSACHUSETTS | 1432 | United States | Range circuit was upgraded in conjunction with service upgrade. Range is an existing appliance approx. 5 years old. Stove top works with no issue. When oven is set to &quot;Bake&quot;, the GFCI trips at 115 degrees. Replaced breaker with standard 2 pole 50A breaker, range works as it should. Informed the customer that the appliance should be checked by an appliance company. | Bosch | HES7282U/06 |  | single family | kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F42-Highland.jpg&form-id=2&field-id=42&hash=30cd9af152cff04f47bef39151b2a1d7b70fe2d86d2c05235e602e6d5904d484 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Andrew Harland | 2025-09-22
2025-09-22 15:49 | John | Tamasi | A 12321 | 6 Easy Street |  | Windham | New Hampshire | 3087 | United States | 603-247-6135 | electrician | johntamasi@yahoo.com | Siemens Model number Q120DFP | Breaker |  | 20 |  | 1 Pole | Siemens | Residence |  | 2025-09-09 | 2025-09-09 |  | 480 Washington Street | Brookline | Massachuettes |  | United States | It tripped 1st time. Checked wiring to fridge plug all clear. Changed breaker held for day tripped. Check line going to fridge all clear. Changed to new breaker again. Held of day then tripped over night. Replaced braker with standard breaker. Haven&#039;t had any problems since then. | Bosch | B36CT80SNS/44 | none | home | Just Fridge in kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John Tamasi | 2025-09-22
2025-09-23 14:17 | Kenneth | Sparrow | 20580A | 151 Mystic Ave #2 |  | Medford | MA | 2155 | United States | 6174601251 | Service/Installation Manager | stephen@gibbonselectric.com | GE thql2150gft2p | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-08-06 | 2025-07-31 |  | 7 Lowell St | Cambridge | MA | 2138 | United States | Breaker tripping when oven is being used Home owner had to reset it almost every time used the oven | Wolf Appliance Inc. | IR36550/s/t Serial #18910263 | no | single family | Kitchen stove outlet | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Stephen McAllister | 2025-09-23
2025-09-23 22:28 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 601 | Cambridge | MA | 2140 | United States | 6179089677 | Electrician | vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dk9ww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero | 2025-09-23
2025-09-23 22:33 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 602 | Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dk5ww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero | 2025-09-23
2025-09-23 22:35 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 603 | Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dkbww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero | 2025-09-23
2025-09-23 22:38 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 604 | Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dkbww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero | 2025-09-23
2025-09-23 22:41 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 605 | Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dkbww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero | 2025-09-23
2025-09-23 22:45 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 606 | Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | grf400v1ww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero | 2025-09-23
2025-09-23 22:56 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 608 | Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jk53000dnzww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero | 2025-09-23
2025-09-24 07:14 | Tyler | Daniels | 1971 | 895 | Salem Street-2A | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | Siemens | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-08-23 | 2025-09-23 | 25 Victor | Unit 19 | Haverhill | MA | 1832 |  | Stove continually tripping while heating | GE | PHP9030ST3SS |  | Apartment | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels | 2025-09-23
2025-09-24 14:35 | Francois | Charlotin | 36586E | 303 Cambridge St | Apt 1 | Fall River | MA | 2721 | United States | 6175935553 | Electrican | fcharlotinjr@aol.com | SIEMENS ???? Q?F Class A 40°C | Breaker |  | 50 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F20250924_141241.jpg&form-id=2&field-id=22&hash=04b00c14b370f89030c2db18400df3264fe32f8f4ffb9c0aada1b8bd5cfb2ed9 | 2025-09-23 | 2025-09-23 | 30 Messenger St |  | Boston | Ma | 2126 | United States | The breaker was installed on a dedicated 3-wire circuit for an LG oven per directions. The breaker would instantly trip once turned on. | LG | LWC3063ST | None | Single family house | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2F20250923_105720.jpg&form-id=2&field-id=42&hash=f877971807489ba426dba81a74fe3bdf9a116d5dbff7ec19c84b914d18b348b2 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Francois Charlotin Jr | 2025-09-25
2025-09-24 20:56 | Vanessa | Romero |  | 432 Rindge Ave | 501 | Cambridge | MA | 2140 | United States | 6179089677 | Electrician | vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dkbww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero | 2025-09-24
2025-09-25 07:28 | Robert | Mahoney |  | 18 Surrey Dr. | Surrey Drive | Lakeville, MA | MA | 2347 | United States | 6177197532 | Owner | bobmahoneyelectric@comcast.net | QF 250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FSiemens-50-amp-gfi-breaker.pdf&form-id=2&field-id=22&hash=465b68a5148a03c382ded38e1d3fa385c52fbba7f2839c324852f4a6fd1de1a6 | 2025-08-29 | 2025-08-29 | 14 Cogswell Ave. #1 |  | Cambridge | Massachusetts | 2140 | United States | Turn on stove &amp; breaker immediately trips | Frigidaire | FFEH24UW |  | Condominium | Kitchen | No | No | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FDiana-Goldfarb-Frigidaire-picture-of-stove-specs.pdf&form-id=2&field-id=42&hash=c9e401b913f01332ae350cf8d6c9301cd2f5243955e6c479f7cd732705184e75 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Robert Mahoney | 2025-09-26
2025-09-25 10:48 | Nick | Curcuru |  | 451 Essex Street | Unit #1 | Beverly | MA | 1915 | United States | 978-283-2299 | Electrican | nickc@royspittleelectric.com | QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-09-01 | 2025-08-01 | [6 empty] | After 90 seconds of the oven turning on, the GFCI 50 Amp breaker trips. This is occurring in all 5 units of the property. | Frigidaire | GCRE3060BFC | No | Apartment | Kitchen is only room affected by trip as the problem is exclusive to the oven. | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Nick Curcuru | 2025-09-25
2025-09-25 10:53 | Nick | Curcuru |  | 451 Essex Street | Unit #2 | Beverly | MA | 1915 | United States | 978-283-2299 | Electrican | nickc@royspittleelectric.com | QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-09-01 | 2025-08-01 | [6 empty] | After 90 seconds of the oven turning on, the GFCI 50 Amp breaker trips. This is occurring in all 5 units of the property. | Frigidaire | GCRE3060BFC | No | Apartment | Kitchen is only room affected by trip as the problem is exclusive to the oven. | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Nick Curcuu | 2025-09-25
2025-09-25 10:57 | Nick | Curcuru |  | 451 Essex Street | Unit #3 | Beverly | MA | 1915 | United States | 978-283-2299 | Electrican | nickc@royspittleelectric.com | QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-09-01 | 2025-08-01 | [6 empty] | After 90 seconds of the oven turning on, the GFCI 50 Amp breaker trips. This is occurring in all 5 units of the property. | Frigidaire | GCRE3060BFC |  | Apartment | Kitchen is only room affected by trip as the problem is exclusive to the oven | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Nick Curcuru | 2025-09-25
2025-09-25 11:01 | Nick | Curcuru |  | 451 Essex Street | Unit #4 | Beverly | MA | 1915 | United States | 978-283-2299 | Electrican | nickc@royspittleelectric.com | QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-09-01 | 2025-08-01 | [6 empty] | After 90 seconds of the oven turning on, the GFCI 50 Amp breaker trips. This is occurring in all 5 units of the property. | Frigidaire | GCRE3060BFC |  | Apartment | Kitchen is only room affected by trip as the problem is exclusive to the oven | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Nick Curcuru | 2025-09-25
2025-09-25 11:04 | Nick | Curcuru |  | 541 Essex Street | Unit #5 | Beverly | MA | 1915 | United States | 978-283-2299 | Electrican | nickc@royspittleelectric.com | QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-09-01 | 2025-08-01 | [6 empty] | After 90 seconds of the oven turning on, the GFCI 50 Amp breaker trips. This is occurring in all 5 units of the property. | Frigidaire | GCRE3060BFC |  | Apartment | Kitchen is only room affected by trip as the problem is exclusive to the oven. | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Nick Curcuru | 2025-09-25
2025-09-25 11:24 | Mark | Thibault |  | 1 Industrial Way Unit #5 |  | Tyngsboro | Massachusetts | 1879 | United States | 6034906301 | President | mark@stelectrical.net | Schneider HOM50GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-09-23 | 2025-09-24 | 6203 Peters Farm Way |  | Westborough | MA | 1581 | United States | When warming up the oven | Whirlpool | WFE535S0LS3 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault | 2025-09-25
2025-09-25 13:03 | Vanessa | Romero |  | 432 Rindge Ave | 607 | Cambridge | MA | 2140 | United States | 6179089677 | Electrician | vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dkbww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero | 2025-09-25
2025-09-25 13:08 | Vanessa | Romero |  | 432 Rindge Ave | 502 | Cambridge | MA | 2140 | United States | 6179089677 | Electrician | vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dk9ww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero | 2025-09-25
2025-09-26 08:04 | Tyler | Daniels |  | 895 | Salem Street-2A | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | BRP120DF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-06-06 | 2025-07-31 | 3 Wainwright | Unit 407 | Winchester | MA | 1890 |  | Kitchen stove continous tripping | GE | JGSS66SEL5SS |  | Apartment | Kitchen stove | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels | 2025-07-31
2025-09-26 08:31 | Tyler | Daniels |  | 895 | Salem Street-2A | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | Q120DF | Breaker |  | 20 |  | 1 Pole | Siemens | Residence |  | 2025-08-28 | 2025-09-25 | 25 River St | Unit 205 | Winchester | MA | 1890 |  | Stove continous tripping | LG | LSGL5833F/00 |  | Apartment | Kitchen stove | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels | 2025-09-25
2025-09-26 14:21 | Robert W | Pasquariella Jr DEI Systems, LLC |  | 35 Hunewill Ave |  | Medford | Massachusetts | 2155 | United States | 617-719-8953 | Project Manager DEI Systems, LLC | rpasquariella@deisystems.com | EATON BRN250GF 50A 2-Pole 120/240V GFCI Circuit Breaker | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-08-25 | 2025-07-22 | 125 Essex St |  | Swampscott | MA | 1907 | United States | This is brand new 114 unit multi-res 5 floor building that we were the electrical contractor and performed all electrical work. We have had several nuisance trip calls and they are not even close to full capacity in the building, several units still need to be rented. We try swapping with new GFCI breakers, still happens, install standard breaker and the problem goes away. | GE | GRF500PVSS Stainless Steel |  | Multi-Residential | The kitchen electric ranges. | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Robert W Pasquariella Jr. | 2025-09-26
2025-09-29 09:37 | Thomas | Gallagher |  | 16 west street |  | Northborough | MA | 1532 | United States | 508-330-0872 | Electrical contractor | gallagherelectric@verizon.net | Square d Homeline s1 120/240v 60hz | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-09-25 | 2025-09-11 | 27 Abbottswood way |  | Sudbury | MA | 1776 |  | immediate trip when oven is put into cooking mode | Wolf | do3050tm/s/t | no | single family | Kitchen oven | Yes | No | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FIMG_0764.jpg&form-id=2&field-id=42&hash=a59a1c75aba4fb06a7eb4489f2875a2b7af8f62dba910572895bad0f333dc42c | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Thomas Gallagher | 2025-09-29
2025-09-29 09:54 | Thomas | Gallagher |  | 16 West street |  | Northborough | MA | 1532 | United States | 508-330-0872 | Electrical contractor | gallagherelectric@verizon.net | Type Hom s1 120/240 | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-09-19 | 2025-09-05 | 27 Abbottswood way |  | Sudbury | MA | 1776 | United States | trips immediately when breaker is engaged | Wolf | c1365t/s | none | single family | Kitchen | Yes | No | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FIMG_0758.jpg&form-id=2&field-id=42&hash=3503ee393186dd9c8363d8178b331470fd776c2681efea8e3573dd4940ba6df0 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Thomas Gallagher | 2025-09-29
2025-09-30 10:09 | Timothy | Entwistle |  | PO Box 910 |  | Essex | MA | 1929 | United States | 9782703185 | Electrician | ryan@covenantllc.com | BRN230GF | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-08-15 | 2025-07-10 | 374 Essex Street |  | Salem | MA | 1970 | United States | Customer reported multiple occurrences of dryer tripping inexplicably mid-cycle during normal operation. No overload tripping has occurred since changing to non-GFCI breaker. Neutral/ground separation for 4-wire configuration was confirmed. Nuisance tripping of GFCI by appliance was determined to be the cause of this unwanted tripping. | Kenmore | 796.8138 | None. Dedicated dryer. Recent wiring. | Laundry room. | Dedicated 4 prong 30A dryer receptacle in newly renovated laundry room on second floor of space. | No | Yes | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FIMG_3087.jpeg&form-id=2&field-id=42&hash=3b4a8c9a997734a360e9c4047617027033c1c2d5566f1f5d38bc9e447f4d3df3 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FIMG_3088.jpeg&form-id=2&field-id=42&hash=2fafd0e291b25dbb4453e00a2f4693fd011d8373fcba9f0f304b444eb7a692c9 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FIMG_0020.jpeg&form-id=2&field-id=42&hash=1ee0e570e1531c065c74c6260b2bf205b748d67f23e9ae83a84932b95fa967dd | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Timothy Ryan Entwistle | 2025-09-30
2025-09-30 10:47 | Timothy | Entwistle |  | PO Box 910 |  | Essex | MA | 1929 | United States | 9782703185 | Electrician | ryan@covenantllc.com | BRN230GF | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-08-19 | 2025-07-24 | 113 Old Essex Road |  | Manchester | MA | 1944 | United States | Customer reported multiple occurrences of dryer tripping without reasonable cause during normal operation. No overload tripping has occurred since changing to non-GFCI breaker. Neutral/ground separation for 4-wire configuration was confirmed. Nuisance tripping of GFCI by appliance was determined to be the cause for this unwanted tripping. | LG | WKEX200HWA | none. Dedicated dryer circuit. | Single Family Residence. | Laundry closet in second floor. | No | Yes | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FIMG_0028.jpeg&form-id=2&field-id=42&hash=8d54aa81c1d0ff944bba9b41970599057b4452d002190ccd34799f099203b629 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FIMG_0027.jpeg&form-id=2&field-id=42&hash=2916b9d1dda304e004e53ddd681c92cc7c3cd0d419e3321dbdcbbf969b630b54 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FIMG_00201.jpeg&form-id=2&field-id=42&hash=35188ec5ae3cd893ccf8da93b5a7203823e43b4edd5201cc2b5cf7c9aec7ea8b | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Timothy Ryan Entwistle | 2025-09-30
2025-09-30 12:06 | Anthony | Triolo |  | 22 Howland Trail |  | Hanson | MA | 2341 | United States | 5088136244 | Electrical Contractor | atrioloelectric@gmail.com | AD-910 | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FIMG_2954.jpeg&form-id=2&field-id=22&hash=db8d837ac2825ff6921bd73881c4b28232898c37a09cecf12c87c21ec17f68d7 | 2025-09-30 | 2025-09-30 | [6 empty] | Tripping instantly. Stove doesn’t work with GFCI. No faults License #54913-B | Electrolux | GCFE3060BFF |  | Duplex | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FIMG_1766.jpeg&form-id=2&field-id=42&hash=710688ea4b0524e5517abf720d09ac2ec3d568e0e4f3eb43d7b2f2d7a1b32399 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F09%2FIMG_1767.jpeg&form-id=2&field-id=42&hash=965ad05e5d5aef9f4f1761e2e58f0fe4222762b042f5e2045e9d28b2bdeada5c | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Anthony Triolo | 2025-09-30
2025-10-01 11:23 | Philippe | Thibeault | #####A | 10076 | Horizon dr | 1 | Springhill fl | 34608 | United States | 9788156009 | Master | cmkillion@yahoo.com | Siemens | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-09-27 | 2025-09-27 |  | 38 mill st |  | Pepperell | Ma | United States | Switched wire out to 3 wire 4 prong plug once plug Range in trips other wise it holds | Ge | 126869 |  | 3 family | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Philippe Thibeault
2025-10-01 13:51 | Jason | Rocca | #####A | 76 Ramah Cir N. |  | Agawam | MA | 1001 | United States | 4132629182 | President | j@jrs2electric.com | CH BRN230GF | Breaker |  | 30 |  | 2 Poles | Eaton | Commercial |  | 2025-08-21 | 2025-08-07 | 25 Allen Park | Unit 200 A&B, 265 A&B, 81 A&B, 299 A&B, 400 A&B, 500 A&B, 55 A&B | Springfield | MA | 1118 | United States | Unable to use equipment, breaker trips immediately 14 total breakers | GE | PTS700LSN3SS | no | Apartment building | kitchen | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jason Rocca
2025-10-01 16:36 | Joseph | Penney | #####A | 3 Daniel Drive |  | Stoneham | MA | 2180 | United States | 6175900558 | PROJECT MANAGER | joejr@penneyelec.com | QF250AP | Breaker |  | 50 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_5057.jpeg&form-id=2&field-id=22&hash=45a897ae679bfeb35b91b0565ce6715116f6ab1a25cb67e60db80c904f9249e9 | 2025-10-01 | 2025-09-01 | 32 Garden Road |  | Stoneham | MA | 2180 | United States | Trips upon oven startup. | Electrolux Home Products Inc | PCFI3670AF | NONE | KITCHEN | KITCHEN | Yes | No | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_50571.jpeg&form-id=2&field-id=42&hash=5ac20d59061896baf6829f75a7dfdc22395be41628b7503e9d1c4c12885cc211 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Joseph Penney
2025-10-03 05:33 | lauro | Tonani | 53437b | 7 Mildred Road |  | Burlington | MA | 1803 | United States | 6178183908 | electrician | laurous@msn.com | BRN250GFCS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-09-30 | 2025-09-30 | 7 Mildred Road |  | Burlington | MA | 1803 | United States | As soon as the GFCI breaker is installed in the panel and turned on, it trips immediately and will not hold. The appliance (range) does not accept connection to a GFCI breaker. | miele | hr1422-31 |  | single family | As soon as the GFCI breaker is installed in the panel and turned on, it trips immediately and will not hold. The appliance (range) does not accept connection to a GFCI breaker. | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2Frange.jpg&form-id=2&field-id=42&hash=006d854896c6fba8b6bbf92e124b43380e6fd21cb89c87112cf4cb710da87736 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Lauro Tonani
2025-10-04 14:18 | Filipy | Ramos | 23223-A | 19 Sparhawk Dr |  | Burlington | MA | 1803 | United States | 7814205768 | Owner | filipyramos@gmail.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_2281.jpeg&form-id=2&field-id=22&hash=13f64c9d7b6cc37091eea8fffdcc2b9068e0fb946a0b0afc3dd06e00386e4cfe | 2025-09-14 | 2025-09-13 | 79 St John St |  | Palmer | MA | 1069 | United States | Breaker trips everytime oven is used | Maytag | MOED6030LZ01 |  | Single family | Kitchen | No | Yes | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_2282.jpeg&form-id=2&field-id=42&hash=3002244afe837e0c850657f0161ffca01ac0327ea11d207bf661e3996734e210 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_2283.png&form-id=2&field-id=42&hash=3d45a2d901d66e2bdb3b8f12c9d1c95a73a9c94d10ea2f26179ea9811a76f609 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Filipy ramos
2025-10-05 10:27 | Richard | Chase | 21093-A | 16 FERMANAGH ST |  | HAVERHILL | MA | 1835 | United States | 7815890262 | Owner/Electrician | Richard@ChaseElectricNE.com | THQL2150GFT2 | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-09-27 | 2025-09-01 | 15 Victory Ave. |  | Haverhill | Ma | 1830 | United States | GFCI breaker trips when the oven changes from a preheat cycle to a heat cycle. | General Electric | J250DF1WW |  | Single Family | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Richard Chase, Jr.
2025-10-05 22:20 | Vladimir | Gaber | 50675 | 22 Gerald Rd |  | Marblehead | MA | 1945 | United States | 508-333-6085 | Homeowner | vl.gaber@gmail.com | QPFB AJ4X9000 I2405090823 | Breaker |  | 30 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2Fgfci_breaker.jpg&form-id=2&field-id=22&hash=772bcfea760309804e0cec7549def11e62c35e53060a22cddbb5fc01817d61d2 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2Fgfci_breaker1.jpg&form-id=2&field-id=22&hash=7c145f53b3ec02252691c535db2abbfb6eeb2dac8759592f68da1b200da741a0 | 2025-09-04 | 2025-06-12 | [6 empty] | The equipment is Miele dual fuel range with electric oven. Once the oven is turned on, the breaker trips. | Miele | HR1934-3G DF |  | Single family house | Kitchen | No | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2Frange_name_plate.jpg&form-id=2&field-id=42&hash=768778e82ee5452894cae973122141a169bd8edfb223c7ef41f221285b631577 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2Frange1.jpg&form-id=2&field-id=42&hash=925b4935e70ff2a81b58fd873bb5bd90a5d43db79d1d37388e05be049679d6d6 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vladimir Gaber
2025-10-06 20:36 | Chet | Nichols | 28412e | 586 South Ave |  | Whitman | MA | 2382 | United States | 7817187772 | Journeyman Electrician | cnicholselectric@comcast.net | Square D hom240gfi | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-06 | 2025-10-06 | 22 Highland Ave |  |  | Ma | Plymouth | United States | breaker tripping when oven turned on | Frigidaire | pcwm3080afd |  | single family | kitchen wall oven | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Chester Nichols
2025-10-07 10:29 | Paul | Macrina | 13305A | 104 Adams Street |  | Medfield | MA | 2052 | United States | 508-359-7954 | Dispatcher | barbara@pmacrina.com | Dual function AFCI/GFCI 20A | Breaker |  | 20 |  | 1 Pole | Siemens | Residence |  | 2025-10-03 | 2025-09-22 |  | 100 Paul Revere Road | Needham | MA | 2052 | United States | Garbage disposal tripping out on arc fault when turned on. The disposal is bra nd new. | Insinkerator | Evolution .75 HP-1 | None | SFH | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Barbara MacCallum
2025-10-07 14:18 | Joseph | Silverio | 17118A | 32 Franklin St |  | Lowell, MA | MA | 1854 | United States | 9788514900 | electrician | fourstarlighting@gmail.com | EATON | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-10-03 | 2025-08-20 | 76 parker street |  | Acton | MA | 1720 | United States | stove tripping breaker with burners on and oven preheating | General Electric | RAS200DM2WW |  | kitchen | Kitchen stove/oven | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Joseph Silverio
2025-10-08 13:57 | John | Vespa | A17144 | 69 Montvale Street |  | Boston | MA | 2131 | United States | 617 325 1151 | Owner | jhnvespa@comcast.net | Q240U | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-03-14 | 2025-03-07 | [6 empty] | Oven nuisance tripping from GFCI installation | Cafe | CTD70DP2N3S1 |  | Residential home | kitchen oven kept tripping | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John Vespa
2025-10-08 19:44 | Carlos | Martinez | 8650-A1 | 44 | Jackson St | Canton | MA | 2021 | United States | 6172333925 | Owner | cemelectricinc@gmail.com | Siemens Indus QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_3771.PNG&form-id=2&field-id=22&hash=15ae9cfe6c2d23a4ec6b290f168a64e290687e45c6f73b567525c2a38f330d76 | 2025-09-23 | 2025-09-23 | 54 Brackenbury St |  | Malden | MA | 2148 | United States | I installed a SolarEdge EV charger, which is GFCI-protected by the manufacturer. The unit requires a receptacle connection. When the charger is plugged in and the GFCI breaker is turned on, the breaker trips within approximately two seconds. I tested the installation using a second GFCI breaker and experienced the same result. The charger operates normally only when connected to a standard (non-GFCI) breaker. | SolarEdge Home EV Charger | SE-EV-SA-KIT-LJ40P | NO | Single family | Only the receptacle that feeds the EV Charger | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FUnknown-163.pdf&form-id=2&field-id=42&hash=c03e94e544b28f2ddace7948eebf96d0e3b624541045d3bef3e873a50cf9118b , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_3590.jpeg&form-id=2&field-id=42&hash=58f782f90268f8ab3be2f6b8145fd9433e00a8600e0c92bfffa93de6082de6d6 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Carlos Eduardo Martinez Ramos
2025-10-09 10:40 | ROBERT | STAGNONE | 12430A | 33 Homestead Circle |  | Milford | NH | 3055 | United States | 6037652733 | V.P. NORMAN E DAY INC. ELECTRICAL CONTRACTORS | bstagnone@normaneday.com | GE ABB THQB2130GFT | Breaker |  | 30 |  | 2 Poles | ABB | Commercial |  | 2025-10-01 | 2021-07-14 | CLEAR PATH FOR VETERANS | 84 ANTIETAM STREET | DEVENS | MA | 1434 | United States | INTERMITENT TRIPPING. | GE | GFDS150EDOWW | N/A | MECHANICAL ROOM | ELECTRIC CLOTHS DRYER IS ONLY ITEM AFFECTED | No | Yes | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_5678photo.png&form-id=2&field-id=42&hash=8e0c0217a3d2207dadb27306497fae9371c714e28c127a9b90240afd9dd0461e | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | ROBERT J STAGNONE
2025-10-10 16:13 | Steven | Rooney | E50969 | 401 South Street |  | Marlborough | MA | 1752 | United States | 5084813299 | Service Manager | Steven@Giombettielectric.com | 2p40 BR GFI breaker | Breaker |  | 40 |  | 2 Poles | Eaton | Residence |  | 2025-10-10 | 2025-03-06 | kitchen | 147 Milk Street Unit 12 | Westborough | MA | 1581 | United States | breaker would trip when it was not in use | Frigidaire | FCRE3062AWE | n/a | kitchen | range | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Steven Rooney
2025-10-14 08:07 | Matthew | Holt | 2230JR | 3 | Breed Ave Unit F | Woburn | MA | 1801 | United States | 6037656746 | PM | mattholtsed@gmail.com | Eaton BR50 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-09-01 | 2025-07-01 | 90 Chestnut St |  | Ashland | Ma | 1721 | United States | GFCI tripping on stove during pre-heat cycle Total of 88 Units | Whirlpool | WEE515SOLS3 | NA | Apartment | Kitchen Total of 88 | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Matthew Holt
2025-10-14 08:07 | Matthew | Holt | 2230JR | 3 | Breed Ave Unit F | Woburn | MA | 1801 | United States | 6037656746 | PM | mattholtsed@gmail.com | Eaton BR50 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-09-01 | 2025-07-01 | 100 Chestnut St |  | Ashland | Ma | 1721 | United States | GFCI tripping on stove during pre-heat cycle Total of 86 Units | Whirlpool | WEE515SOLS3 | NA | Apartment | Kitchen Total of 86 | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Matthew Holt
2025-10-14 08:42 | kristopher | kopecky | 13330 B | 28 Willing Ave |  | Warwick | RI | 2888 | United States | 4013456247 | Director of Field Operations | kkopecky@eecne.com | GE THQL1120GFT | Breaker |  | 20 |  | 1 Pole | ABB | Residence |  | 2025-10-09 | 2025-09-02 | 100 Plank St. |  | Bedford | massachusetts | 1730 | United States | Toe kick heater in the bathroom Trips the 20amp GFCI breaker | Stelpro kick space heater | ASKS1001W | none | Apartment | Bathroom Toe kick heater | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kristopher Kopecky
2025-10-14 09:29 | kristopher | kopecky | 13330 B | 28 Willing Ave |  | Warwick | RI | 2888 | United States | 4013456247 | Director of Field Operations | kkopecky@eecne.com | GE THQL2150GFTA | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-10-14 | 2025-09-09 | 100 Plank St. |  | Bedford | MA | 1730 | United States | Range trips the 50amp 2 pole GFCI breaker | Range LG | LSEL6333*E | none | Kitchen | Kitchen range | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kristopher Kopecky
2025-10-15 08:48 | Daniel | Campbell | 12472-b | 15 claron |  | Boston | Massachusetts | 2131 | United States | 9788916006 | Electrician | danielcampbellelectric@yahoo.com | Qfga2n | Breaker |  | 20 |  | 1 Pole | Siemens | Residence |  | 2025-09-19 | 2025-09-13 | [6 empty] | Microwave causes nuisance trip. Circuit is dedicated with single outlet | Samsung | Me16a4021as | None | Kitchen | None | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Daniel campbell
2025-10-16 11:30 | Jeffrey | Pagnini | 8248A1 | 31 Coachman Lane |  | Natick | Ma | 1760 | United States | (857) 231-1460 | Electrician | Jeff.pagnini@gmail.com | Eaton/BRN120DF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-09-26 | 2025-09-25 | [6 empty] | Fridge trips breaker after about 90 seconds of being reset | Samsung | RF22K9381SR | No | Single Family | Kitchen area fridge | No | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Ryan Kerrissey
2025-10-16 13:49 | Chase | Locke | 14426-A Exp. 7-31-28 | 22 Owl's Nest |  | Plymouth | MA | 2360 | United States | 2076028923 | Assistant Construction Manager | clocke@tollbrothers.com | Eaton BRN250GF | Breaker |  | 15 |  | 1 Pole | ABB | Residence |  | 2025-10-03 | 2025-07-30 | [6 empty] | The homeowner has used their oven twice now and both times it has tripped. | KitchenAid | KOED530PSS |  | Single Family | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Chase Locke
2025-10-16 14:33 | John Michael | LoPriore | E50876 | 103 Foundry Street Suite 2B |  | wakefield | MA | 1880 | United States | 7815870875 | President | jml@jml-electric.com | Eaton 2p50amp GFCI | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-10-14 | 2025-10-10 | 12 Maple Ave | Rear Dwelling | Cambridge | MA |  | United States | Installed New 2p 50amp Eaton GFCI circuit breaker on the 4wire Range outlet. Tested for proper voltage and grounding. Unbonded the grounding strap in the frame of Samsung Electric Range. Installed Stove and plugged in to outlet. The Circuit tripped after 5 minutes not in use. Replaced circuit breaker with NEW like type and restored power. After 1 hour it tripped again. The circuit was tested for proper voltage to Appliance and was confirmed. Circuit remains off until approval is granted. | Samsung | NSE6DG8300SRAA | N/A | ADU | Kitchen Stove | No | Yes | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2Fimage0.jpeg&form-id=2&field-id=42&hash=4febc61ee064a662f5e74a628c13a1842b467a44017de62c120bef8758ec7cc6 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John Michael LoPriore
2025-10-20 11:15 | Christopher | Cornell | A18091 | PO Box 751 |  | Wrentham | MA | 2093 | United States | 5083808528 | Owner | cfcelectrical@yahoo.com | Eaton BRN250GFCS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-08-21 | 2023-12-06 | 58 Lyman Road |  | Milton | MA | 2186 | United States | When bottom oven is turned on the tripping occurs | Kitchen Aide | KSEG700ESS3 |  | single family | kitchen | No | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2Fshowing-breaker-use-.pdf&form-id=2&field-id=42&hash=40ca3765063bf476b81a620f4980cdc3a6cc8ee8c5818f4df98eeb71e14da6ea , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FFull-panel-.pdf&form-id=2&field-id=42&hash=6fdb9f513b62f4d04d1a460aba8d91874f62ea382f26c720c3817f5b06315c07 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FKitchen-aide-stove-unit-to-show-application-.pdf&form-id=2&field-id=42&hash=0675202ca01ef2339bc1588b77c61f8accc9d25411fd0a235233598c9261ae7d , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FName-plate-of-stove-model-number-.pdf&form-id=2&field-id=42&hash=f5dda8cc4c616448d9a758177bd6a62310311b67359c9df35663332568c946c3 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher F Cornell
2025-10-20 11:15 | Christopher | Cornell | A18091 | PO Box 751 |  | Wrentham | MA | 2093 | United States | 5083808528 | Owner | cfcelectrical@yahoo.com | Eaton BRN250GFCS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-08-21 | 2023-12-06 | 58 Lyman Road |  | Milton | MA | 2186 | United States | When bottom oven is turned on the tripping occurs | Kitchen Aide | KSEG700ESS3 |  | single family | kitchen | No | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher F Cornell
2025-10-20 11:57 | Ryan | LaBrache | 22042A | 109 School St |  | Watertown | MA | 2472 | United States | 617-924-8866 | Owner | ryan@lampasonabloomer.com | BRN240GF | Breaker |  | 40 |  | 2 Poles | Eaton | Residence |  | 2025-10-17 | 2025-07-24 | 40 Pickney St |  | Boston | MA | 2114 | United States | CB would trip during preheat | Wolf Appliance | DO3050PM/S/P |  | single family | kitchen | No | Yes | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Ryan LaBrache
2025-10-20 12:02 | Ryan | LaBrache | 22042A | 109 School St |  | Watertown | MA | 2472 | United States | 617-924-8866 | Onwer | ryan@lampasonabloomer.com | THQL2150GFT | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-10-17 | 2025-10-17 | 97 HillSide |  | Newton | MA | 2465 | United States | CB would trip on preheat | Wolf Appliance | DO3050PM/S/P |  | single family | Kitchen | No | Yes | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Ryan LaBrache
2025-10-20 13:35 | Daniel | Venezia | 20575A | 62 Hamilton Ave |  | Billerica | MA | 1821 | United States | 978-987-4774 | Owner | danvenezia3@gmail.com | Siemens | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-10-20 | 2025-10-04 | 110 Wilson Rd Unit 1 |  | Bedford | MA | 1730 | United States | when oven is turned on the breaker continuously trips | Cafe | CGS700P2MS1 Range | None | 2 family home | The kitchen | Yes | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Daniel Venezia
2025-10-20 13:41 | Daniel | Venezia | 20575A | 62 Hamilton Ave |  | Billerica | MA | 1821 | United States | 9789874774 | Owner | danvenezia3@gmail.com | Siemens | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-10-10 | 2025-10-04 | 110 Wilson Rd Unit 2 |  | Bedford | MA | 1730 | United States | Range continues to trip when oven is turned on | Cafe | CGS700P2MS1 Range | None | Single family home | range keeps tripping every time it turns on | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Daniel Venezia
2025-10-21 13:29 | Philip | Mendonca | 01757b | 6R Mount Vernon St. |  | Arlington | MA | 2476 | United States | 6178885434 | Owner | philipselectric@gmail.com | Square D Homeline 50 Amp two-pole GFCI circuit breaker HOM250GFICP | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-21 | 2025-09-02 | 11 Burroughs Rd |  | Lexington | MA | 2420 | United States | Breaker tripps when stove is turned on. Manufacturer specifications do not require GFCI protection. | Wolf | d03050pesp |  | Single family | kitchen stove | No | No | No | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Philip Mendonca
2025-10-22 07:37 | James | McCormack | 756814 | 196 High St | Unit 2 | Ipswich | Massachusetts | 1938 | United States | 9784710544 | Owner | jim@upwire-electric.com | QF250A | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-10-21 | 2025-10-01 | 6 School Way |  | Bedford | MA | 1730 | United States | When oven runs breaker trips | GE | JB655SK1SS |  | Single Family Home | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | James McCormack
2025-10-22 13:18 | Jake | Carlan | 1971 | 895 | Salem Street-2A | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | Eaton | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-06-10 | 2025-07-09 | 3 Wainwright | Unit 320 | Winchester | MA | 1890 | United States | Stove continually tripping | GE | JGSS66SEL5SS |  | Apartment | Stove, continous tripping | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jake Carlan
2025-10-22 13:58 | Mark | VanMolle | A-13527 | PO Box 1534 |  | Littleton | MA | 1460 | United States | 978-337-6541 | Contractor | castlecp@hotmail.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-10-03 | 2025-10-06 | 40 Caterina Heights |  | Concord | MA | 1742 | United States | Installed a new GFCI breaker on an existing oven. It continuously trips. | Thermodor | POD302W/01 |  | Single family | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark VanMolle
2025-10-23 09:03 | Joseph | Penney | A11412 | 3 Daniel Drive |  | Stoneham | MA | 2180 | United States | 6175900558 | electrician | joejr@penneyelec.com | BRN240GF | Breaker |  | 40 |  | 2 Poles | Eaton | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_2670.jpeg&form-id=2&field-id=22&hash=8c2b26e7d5e2960d6197da9b698bcb20295f0c2cfc8eb4e4f8a5a5f3ad3c4717 | 2025-10-02 | 2025-10-01 | 888 Massachusetts Ave |  | Cambridge | MA | 2139 | United States | Range trips while connected to 2 pole 40 gfci breaker. Manufacturer said it is incompatible with gfci protection. | Peerless-Premier Appliance Co. | EAK200BPS | none | kitchen | kitchen | Yes | No | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_26701.jpeg&form-id=2&field-id=42&hash=a60bc9d37dad6404dd539ce905b1d7ea0f84697f4fbad7b84169a4731281e9e6 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Joseph Penney
2025-10-23 09:14 | Joseph | Penney | A11412 | 3 Daniel Drive |  | Stoneham | MA | 2180 | United States | 6175900558 | electrician | joejr@penneyelec.com | BRN240GF | Breaker |  | 40 |  | 2 Poles | Eaton | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_26702.jpeg&form-id=2&field-id=22&hash=f0699d472c6bd357b27a53f2d21a90ae10b9a1b22da5627c79a7db739a0cf361 | 2025-10-08 | 2025-10-07 | 888 Massachusetts Ave unit 616 |  | Cambridge | MA | 2139 | United States | Range trips while connected to gfci breaker. | Peerless-Premier Appliance Co. | EAK220BP01 | none | apartment | kitchen | Yes | No | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_26703.jpeg&form-id=2&field-id=42&hash=38ec2b1116322487138500a275c8e9464c3c4f77c706b7dff17c86d113dbe0ec | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Joseph Penney
2025-10-23 16:00 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 503 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 15 |  | 1 Pole | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dk9ww |  | Apartment | Kitchen | No | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-10-24 10:47 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 504 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | JB625dkbww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-10-24 11:29 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 505 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb25dk9ww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-10-24 14:02 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 506 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dk9ww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-10-24 14:07 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 507 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dkbww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-10-24 14:16 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 508 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GE | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | Jb625dkbww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-10-24 14:21 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 509 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dkbww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-10-24 14:39 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 510 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GE | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | Jb625dkbww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-10-24 14:43 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 401 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb62dk9ww |  | Apartment | Appliance would trip GFCI breaker constantly. | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-10-25 13:39 | Jorge | Romero | 21628A | 335 Ferry St | El Valle De La Sultana Market | Everett | MA | 2149 | United States | 6179089677 | Electrician | jorge@rokocorp.com | b340gfhh | Breaker |  | 40 |  | 3 Poles | Siemens | Commercial |  | 2025-10-01 | 2025-10-07 | [6 empty] | Rotisserie chicken oven will not work with GFCI breaker, once oven starts, the breaker trips. | Henny Penny | SCR-8 |  | Super Market | Cafe | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jorge Romero
2025-10-25 13:46 | Jorge | Romero | 21628A | 335 Ferry St | El Valle De La Sultana Market | Everett | MA | 2149 | United States | 6179089677 | Electrician | jorge@rokocorp.com | b340gfhh | Breaker |  | 40 |  | 3 Poles | Siemens | Residence |  | 2025-10-01 | 2025-10-07 | [6 empty] | Rotisserie chicken oven will not work with GFCI breaker, once oven starts, the breaker trips. | Henny Penny | SCR-8 |  | Super Market | Cafe | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jorge Romero
2025-10-25 13:51 | Paul | Earnest | 57714-B | 117 Union Street | Unit 1 Front | Westfield | Ma | 1085 | United States | 4134541513 | Lead Foreman/Journeyman | paul@electricalexperts.com | Leviton LB230-G | Breaker |  | 30 |  | 2 Poles | Leviton | Residence |  | 2025-07-08 | 2025-07-08 | 83 Adams Road |  | Haydenville | Ma | 1039 | United States | Instant trip on multiple breaker attempts | Kitchenaid | KCIG550JBL | None | Home | Cooktop for kitchen counter | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Paul Earnest
2025-10-27 10:02 | John | Raimo | A18352 | PO Box 762 |  | Dennis | MA | 2638 | United States | 5087781804 | Owner | raimoelectric@yahoo.com | Siemens QFGA2 | Breaker |  | 20 |  | 1 Pole | Siemens | Residence |  | 2025-10-22 | 2025-10-22 | 28 Merrymount Road |  | West Yarmouth | MA | 2673 | United States | New kitchen with new wiring, therefore new Frigidare refrigerator was installed and as soon as it was plugged in, the tripping occurred. Refrigerator was plugged into two other GFCI and tripping happened again. Finally, refrigerator was plugged into a non-GFCI that is not in the kitchen and no tripping. | Frigidaire | PRMC2285AF07 | None | Single family home | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FRefrigerator-outlet.jpg&form-id=2&field-id=42&hash=4a8c681ecc8638b7b431e09a861fed0afaebdac646ebcdeab2d147a47bfb5983 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FRefrigerator-Model.jpg&form-id=2&field-id=42&hash=69bfa5c6249e9427f3fbb8dfff6e14e49a14e6c17568644b22ad02f9852bf389 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FFridge-outlet.jpg&form-id=2&field-id=42&hash=1d56d5113ad20d0b0d838d5a40308ce3d95f74fe3a6cf70ddf05142c12d76ad7 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FCircuit-Breaker.jpg&form-id=2&field-id=42&hash=2745aadbaa126290c8607fb61c3361343fc6cbf2648d265e15334dfb86608cca | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John B Raimo
2025-10-27 10:15 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker | Breaker | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #201 | Winchester | MA | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESSN2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 10:31 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #202 | Winchester | MA | 1890 | United States | Breaker Tripping when dryer is in use frequently | GE | GFD55ESSN2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 10:35 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #203 | Winchester | MA | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESSN2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 10:40 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #204 | Winchester | MA | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESSN2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 10:47 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #205 | Winchester | MA | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 10:51 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #206 | Winchester | MA | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 10:54 | k | c | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #207 | Winchester | MA | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 10:57 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #208 | Winchester | MA | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 11:01 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #209 | Winchester | MA | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 11:04 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #210 | Winchester | MA | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 11:21 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #212 | Winchester | MA | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 11:24 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #301 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 11:27 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #302 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 11:30 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #303 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 11:35 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #305 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 11:50 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #306 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 11:54 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #307 | w | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 11:58 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #308 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 12:01 | Eric | Caldon | 21306a | 100 Deanville Rd |  | Attleboro | MA | 2703 | United States | 7742296409 | owner | Ecaldonmidstate@gmail.com | Eaton | Breaker |  | 30 |  | 2 Poles | Eaton | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F34-augsburg-2.jpeg&form-id=2&field-id=22&hash=5e3ac3e570e163a700892514417e7d4b30e571e8d2c569459e51fa7538712feb | 2025-10-16 | 2025-06-17 | 43 Augsburg St |  | Attleboro | MA | 2703 | United States | Dryer trips randomly | Samsung | DVE50R5200w/a3 | none | Laundry room | Laundry room when dryer trips | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F34-augsburg-1.jpeg&form-id=2&field-id=42&hash=1d31f38a97fbbc8cd6854d1f994771df17c055c6b876b42ece17a8fe6d012bf4 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Eric Caldon
2025-10-27 12:05 | Kevin | c | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #309 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 12:49 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #310 | Winchester | MA | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 13:22 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #311 | Winchester | Ma | 1890 |  | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 13:25 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #312 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 13:27 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #313 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 13:30 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #314 | Winchester | Ma | 1890 |  | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 13:33 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #315 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 13:36 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #316 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-27 14:23 | Tyler | Daniels | 1971 | 895 Salem Street 2A |  | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | BRP120F | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-09-05 | 2025-10-06 | 3 Wainwright Rd | Unit 525 | Winchester | MA | 1890 | United States | Stove repeatedly tripping breaker | GE Appliances | JGSS66SEL5SS | n/a | Apartment | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels
2025-10-27 14:23 | Tyler | Daniels | 1971 | 895 Salem Street 2A |  | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | BRP120F | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-09-04 | 2025-10-06 | 3 Wainwright Rd | Unit 516 | Winchester | MA | 1890 | United States | Stove repeatedly tripping breaker | GE Appliances | JGSS66SEL5SS | n/a | Apartment | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels
2025-10-27 14:23 | Tyler | Daniels | 1971 | 895 Salem Street 2A |  | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | BRP120F | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-09-04 | 2025-10-06 | 3 Wainwright Rd | Unit 506 | Winchester | MA | 1890 | United States | Stove repeatedly tripping breaker | GE Appliances | JGSS66SEL5SS | n/a | Apartment | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels
2025-10-27 15:52 | John | Raimo | A18352 | Box 762 |  | Dennis | MA | 2638 | United States | 5087257259 | Manager | raimojraimo@yahoo.com | Square D - QO250GFICP | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Commercial | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_130446.jpg&form-id=2&field-id=22&hash=ca0b17cc6c190283ea42c28a26fa439cc094f4d9a59ac53af16c8f5ae034fbef , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_1304461.jpg&form-id=2&field-id=22&hash=c0697947ed02178d6912cab34500652770b60520679d26fca74c51b7abf64fc0 | 2025-10-27 | 2025-10-27 | 94 Thad Ellis Rd |  | Brewster | MA | 2631 | United States | GFCI trips after turning on the oven for about 3 minutes. | Frigidaire | FCRE3052ask | none | ( Breakroom) Kitchen Range | (Breakroom) Kitchen Range | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_1304462.jpg&form-id=2&field-id=42&hash=6e020c2adc7ebcfa2bd117f40665de145ab5b09370b443fb14fcd913d817fd12 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_130218.jpg&form-id=2&field-id=42&hash=ac30f496e7dcdb37a22bce16ca0606729fe239441f32cad15a4f4df7ffec6397 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_130106.jpg&form-id=2&field-id=42&hash=78df491c9d0249ad771c53ada340a0c50ebd24d3d1d786c2a2822bf7cf222af6 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_130103.jpg&form-id=2&field-id=42&hash=0a13595e70dc45268c665df0d4f15ad38c906a3f8835d834344c8090e83ca885 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_130040.jpg&form-id=2&field-id=42&hash=953761a95f90282849dcffed643cbf8770f162c92a76f8993602b29bbf49ac1f , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_1300401.jpg&form-id=2&field-id=42&hash=f1348712b042c2e45e93ef03cb9b409cd81faab2db24094a65e91a033f6b53cc | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John B Raimo
2025-10-27 16:05 | John | Raimo | a18352 | Box 762 |  | Dennis | MA | 2638 | United States | 5087257259 | Manager | raimoelectric@yahoo.com | Square D - QO250GFICP | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Commercial | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_1304463.jpg&form-id=2&field-id=22&hash=c2f95140b69f12f15217132af215053fe7313c354891c22b1653694bf5f32f17 | 2025-10-27 | 2025-10-27 | 94 Thad Ellis Rd |  | Brewster | ma | 2631 | United States | Breaker Trips about 3min after turning the oven on. | Frigidiare | fcre3062ask | no | Stove (Breakroom) | Stove (Breakroom) | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_1304464.jpg&form-id=2&field-id=42&hash=35105a5235ca6e1edeffc4e0787b10c9beb5505b42d11ff184edef2caff28a73 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_1302181.jpg&form-id=2&field-id=42&hash=291ffae42d25ca0a5e1ff6501c4450cee85b5cab00ca7e5c8ea7051b58e72af3 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_1301061.jpg&form-id=2&field-id=42&hash=8ee10a01622d5d09c528a7a4c0e78112dfe50d8dd6bf87e20e9fd89e5b9392cb , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_1301031.jpg&form-id=2&field-id=42&hash=c5ca2db980f30be0037de2c8af54f63faf5c30f121b40ddc74ee600216cd031d , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_1300402.jpg&form-id=2&field-id=42&hash=493531cea0870ddf03cc2c4635f6743f3b4a970de4f2206adeb515e018bded20 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2F20251027_130019.jpg&form-id=2&field-id=42&hash=89841e1479a9c352740c6fa95b9b16230bd3dd83edc8cae6c2ac821ed5190fb6 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John B Raimo
2025-10-27 17:35 | Thai | Nguyen | 22299 | 10 Ashland st |  | Quincy | MA | 2169 | United States | 8573432181 | Electrician | Bostonnguyenelectric@gmail.com | Eaton GFTCB250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-03-26 | 2025-03-26 | 114 Temple st |  | Newton | Ma | 2465 | United States | We ran wire, installed outlet, plugged the stove in and breaker tripped as soon the breaker turned on. | Frigidaire Pro | PCF13670AF |  | Residence | Kitchen | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Thai Nguyen
2025-10-28 10:06 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #317 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 10:21 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #318 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 10:25 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | ABB | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #319 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 10:28 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #320 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 10:31 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #321 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 10:34 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #322 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 10:38 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #323 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 10:41 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #324 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 10:44 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #325 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 10:47 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #326 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | Breaker tripping when dryer is in use frequently | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 11:43 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #327 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 12:56 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #328 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 13:03 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #330 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 13:08 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #401 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 13:10 | k | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #402 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 13:13 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #403 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 13:16 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #405 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 13:19 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #406 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 13:22 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #407 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 13:25 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #408 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 13:27 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #409 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-28 13:53 | David | Kenton | 53032-b | 10 westview terrace |  | Woburn | Ma | 1801 | United States | 7815073328 | Electrician | dkenton1713@gmail.com | Eaton / E-45310 type brn | Breaker |  | 40 |  | 2 Poles | Eaton | Residence |  | 2025-09-20 | 2025-08-01 | 7 cross street |  | Wilmington | Ma | 1887 | United States | Frigidaire electric range Model FCRE 3062ASE. Tripping randomly in the middle of using the oven - as well as randomly when oven is not in use or under a load. Maybe potential electrical leakage in the oven that the breaker is too sensitive for. This has happened everyday for almost a month. Other reports of same oven also tripping on the same breaker. | Frigidaire | FCRE3062ASE | None | condo | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | David Kenton
2025-10-29 15:29 | James | Loughlin | 17387a | PO BOX 72 |  | Franklin | MA | 2038 | United States | 5085280765 | owner | ken@loughlinelectric.com | qf250a | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-10-18 | 2025-10-18 | 8 Fleetwood Dr | PO BOX 72 | Norfolk | Ma | 2056 | United States | when installing a gfci breaker on the range with a new circuit installed the circuit trips immediately | GE | `JBP24BHIWH | NO | SINGLE FAMILY | KITCHEN RANGE | Yes | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | James Loughlin
2025-10-29 15:37 | James | Loughlin | 17387A | PO BOX 72, |  | Franklin | Massachusetts | 2038 | United States | 5085280765 | OWNER | sales@loughlinelectric.com | QF250A | Breaker |  | 50 |  | 1 Pole | Siemens | Residence |  | 2025-10-29 | 2025-10-29 | 66 Roosevelt Ave | PO BOX 72 | North Attleboro | Ma | 2760 | United States | installed 2 pole 50 gfci for electric range and it tripps | ge | jtd5000sv1ss | no | single family | kitchen range | Yes | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | James Loughlin
2025-10-29 18:17 | Anthony | Triolo | 54913-B | 39 Lantern Lane | Unit 1 | Braintree | MA | 2184 | United States | 5088136244 | Electrical Contractor | atrioloelectric@gmail.com | AD-910 | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_2954.jpeg&form-id=2&field-id=22&hash=3e86a59ef4a73f6aa733ad2651e52d6f4946b348c2e9ca92f360dc9bba2cc89f | 2025-10-29 | 2025-10-29 | [6 empty] | Brand newStove trips immediately | Refresh Electric | LREL6321 |  | Kitchen | Kitchen stove | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_3916.jpeg&form-id=2&field-id=42&hash=fd038f528811abbafb10d2a640b8a5d95f2bb43d019610c3ccc2f25549e1da80 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Anthony Triolo
2025-10-29 18:23 | Anthony | Triolo | 54913-B | 39 Lantern Lane | Unit 3 | Braintree | MA | 2184 | United States | 5088136244 | Electrical Contractor | atrioloelectric@gmail.com | AD-910 | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_29541.jpeg&form-id=2&field-id=22&hash=026051448e55e8a60178f5df42853099381c6b9a78fa3b6b01815a7d6b4b1896 | 2025-10-29 | 2025-10-29 | [6 empty] | Brand new stove trips immediately | Refresh Electric | LREL6321 |  | Kitchen | Kitchen Stove | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_3920.jpeg&form-id=2&field-id=42&hash=665fe1a1f798f3d8e88747b203e1c8f8491eb5a7006d7f7c1e581bec840eae3e , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F10%2FIMG_3918.jpeg&form-id=2&field-id=42&hash=9b7d422e5defc17ade453eca3a2781c68a8533fd76a792b38c63c379a979596f | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Anthony Triolo
2025-10-30 11:07 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #410 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:10 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #411 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:12 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #412 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:16 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #413 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:18 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #414 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:21 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #415 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:25 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #416 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:29 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #417 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:31 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #418 | Winchester | MA | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:34 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #419 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:36 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 23 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #420 | Winchester | MA | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:39 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | h | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #421 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:42 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #422 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:46 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #423 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:49 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #424 | Winchester | Ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:52 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #425 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 11:54 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #426 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 12:01 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #427 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 12:03 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #428 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 12:11 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #428 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 12:16 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #430 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 12:20 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #501 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 12:24 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #502 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 12:26 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #503 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 12:29 | Kevin | Callahan | 20710A | 275 Centre St | u | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #505 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 12:31 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | h | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #506 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 12:34 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #507 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 12:36 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-05-01 | 3 Wainwright Road | Apt #508 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 12:39 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #509 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 12:41 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #510 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-30 14:23 | Jarrad | Paskovas | 23516-A | 778 main st | MAIN STREET | osterville | MA | 2655 | United States | 5084286365 | Master electrician | trish@carlriedell.com | M2503050075 | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-06-03 | 2025-05-21 | 219 cotuit bay drive |  | cotuit | massachusetts | 2635 | United States | Installed 50 amp siemens gfci breaker for stove. holds until you turn on the stove. once you turn on the stove the breaker trips. customer called back complaining because he cannot use his stove we just installed | Frigidaire 30" Front Control Induction Range with Total Convection | WX09X10037 |  | Kitchen | Kitchen stove | No | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jarrad Paskovas
2025-10-31 08:20 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | Ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #511 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:23 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #512 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:26 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #513 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:28 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 | Apt #514 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:31 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #516 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:34 | k | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #517 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:36 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #518 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:38 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #519 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:41 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #520 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:43 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #521 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:45 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #522 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:48 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #523 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:50 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #524 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:53 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #525 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 08:58 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #526 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 09:00 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #527 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 09:03 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #528 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 09:05 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #530 | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 09:08 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN230Gf | Breaker |  | 30 |  | 2 Poles | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | SFAM | Winchester | ma | 1890 | United States | Breaker tripping when dryer is in use frequently | GE | GFD55ESS2WW |  | Apartment | Dryer | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 09:21 | Douglas | Chick | E51010 | 185 Forbes Road |  | Rochester | MA | 2770 | United States | 774-712-0670 | Licensed Electrician | dchickelectric@gmail.com | BRN250GFCS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-09-12 | 2025-09-12 | 233 Cliff Drive |  | North Attleboro | MA | 2760 | United States | Induction cooktop installed with GFCI keeps tripping. | Wolf | CI365TF/S |  | Single Family Home | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Chick
2025-10-31 09:21 | Douglas | Chick | E51010 | 185 Forbes Road |  | Rochester | MA | 2770 | United States | 774-712-0670 | Licensed Electrician | dchickelectric@gmail.com | GFTCB220 | Breaker |  | 20 |  | 2 Poles | Eaton | Residence |  | 2025-09-12 | 2025-09-12 | 233 Cliff Drive |  | North Attleboro | MA | 2760 | United States | Wall oven installed with GFCI keeps tripping. | Wolf | CSOP3050PE/S/P | None | Single Family Home | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas Chick
2025-10-31 10:35 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | SFAM | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 11:15 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #511 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 11:17 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #512 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 11:20 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #513 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-10-31 11:22 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #514 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-01 18:19 | Mark | Roussel | a21100 | 33 old forge Ln |  | Sudbury | MA | 1776 | United States | 9784438888 | electrician | Baseball78@verizon.net | Siemens Q230GFP | Breaker |  | 30 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FSIEMENS-breaker.jpg&form-id=2&field-id=22&hash=526cd97e11fa1acb2884eb6e37ac0010b2d820ff2709cc7d9872f22e45e8e044 | 2025-10-31 | 2025-10-31 | 372 Dutton Rd |  | Sudbury | MA | 1776 | United States | installation of 2 different breakers had the same result (tripping happened immediately upon turning breaker on | Monogram | ZSB9232v1ss | NOTHING | RESIDENTIAL KITCHEN | 1 ROOM ONLY--- KITCHEN OVEN | No | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2F372-Dutton-microwave.jpg&form-id=2&field-id=42&hash=de23adc2cfda9b56bc49aa7ddf0de274e65644b9baa6f11867eaa280a9273842 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark R Roussel
2025-11-01 18:27 | Mark | Roussel | a21100 | 33 old forge Ln |  | Sudbury | MA | 1776 | United States | 9784438888 | electrician | Baseball78@verizon.net | Siemens Q220GFP | Breaker |  | 20 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2Fsiemens-20-amp.jpg&form-id=2&field-id=22&hash=c65412e1e72b608c8c903018efa2f19f21d1a27ca0e9808193c05c0ac1c97fe4 | 2025-10-31 | 2025-10-31 | 372 Dutton rd sudbury MA |  | Sudbury | MA | 1776 | United States | breaker trips within first 30 seconds afterturning on | siemens | Q220GFP |  | residential | kitchen oven only | No | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2F372-Dutton-oven.jpg&form-id=2&field-id=42&hash=0944b5d74d68e32559788293fa042f40c26f399bf7ec0d3a2b18c478f05f1d5a | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark R Roussel
2025-11-03 12:04 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 401 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb62dk9ww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-11-03 12:07 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 402 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | Jb625dkbww |  | Apartment | Appliance would trip GFCI breaker constantly. | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-11-03 12:11 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 403 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GE | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dkbww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-11-03 12:57 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 404 | North Cambridge | MA | 2140 | United States | 6179089677 | 6179089677 | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dkbww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-11-03 13:00 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 405 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | Jb625dk9ww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-11-03 13:04 | Vanessa | Romero | 60928-B | 432 Rindge Ave | 406 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | Jb625dkbww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-11-03 13:08 | Vanessa | Romero | 60928-B | 43 Rindge Ave | 503 | North Cambridge | MA | 2140 | United States | 6179089677 | Electrician | Vanessa@rokocorp.com | GFTCB250CS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-04-03 | 2025-04-03 | [6 empty] | Appliance would trip GFCI breaker constantly. | GE | jb625dk9ww |  | Apartment | Kitchen | Yes | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Vanessa Romero
2025-11-04 07:53 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #515 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 07:56 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #516 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 07:59 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #517 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 08:04 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #518 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 08:07 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #519 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 08:09 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #520 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 08:12 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #521 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 08:14 | Steven | Rooney | A13678 | 401 South Street |  | Marlborough | MA | 1752 | United States | 508-481-3299 | Service manager - Giombetti Electric | Steven@Giombettielectric.com | HOM250GFICP | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-31 | 2025-10-31 | kitchen | 79 Plymouth Street | Marlborough | MA | 1752 | United States | breaker trip when running oven | Frigidaire Gallery | GCRE3060BFC | none | single family | kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Steven P Rooney
2025-11-04 08:25 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #522 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 08:27 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #523 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 08:30 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #524 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 08:32 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #525 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 08:35 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #526 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 08:37 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #527 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 08:39 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #528 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 08:42 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #530 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 08:46 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #201 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:08 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 401 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:10 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #202 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:13 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #203 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:14 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 402 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:15 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #204 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:17 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 403 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:18 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #205 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:20 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 405 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:21 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #206 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:23 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #207 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:25 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #208 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:28 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #209 | Winchester | ma | 2343 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:29 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 406 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:30 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #210 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:32 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #212 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:32 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 407 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:37 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 408 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:39 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 409 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:42 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 410 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:44 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 411 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:46 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 412 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:48 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 413 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:51 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 414 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:52 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 415 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:55 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 416 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:57 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 417 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 09:59 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 418 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:01 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 419 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:02 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #301 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:02 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 420 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:04 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 421 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:04 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #302 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:05 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 422 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:06 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 23 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #303 | Winchester | Ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:07 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 423 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:08 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 424 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:09 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #305 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:10 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 425 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:11 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 426 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:12 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #306 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:12 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 427 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:14 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 428 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:14 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #307 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:15 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 430 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:17 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #308 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:17 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 501 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:19 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 502 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:20 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-05-01 | 3 Wainwright Road | Apt #309 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:20 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 503 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:21 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 505 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:22 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #310 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:23 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 506 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:24 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 507 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:25 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 508 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:25 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #311 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:27 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 509 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:28 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | APT 510 | Winchester | MA | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:29 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | h | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #312 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 10:58 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #313 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:01 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #314 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:08 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | h | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #314 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:11 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #315 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:14 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #316 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:16 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #317 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:19 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #318 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:21 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #319 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:24 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #320 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:26 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #321 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:29 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #322 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:31 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #323 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:33 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #324 | Winchester | ma | 2343 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:39 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | ABB | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #325 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:41 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #326 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:47 | Kevin | Callahan | 20710A | 275 Centre St | u | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #327 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:49 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #328 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 11:51 | Kevin | Callahan | 20710A | 275 Centre St | Unit 14 | Holbrook | ma | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-03-01 | 2025-04-01 | 3 Wainwright Road | Apt #330 | Winchester | ma | 1890 | United States | Breaker tripping when using the microwave frequently | GE | JVM6175SK6SS |  | Apartment | Microwave Only | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-04 12:46 | Daniel | Greenberg | 54913B | 13 Narragansett Dr | Norfolk Ave. | West Bridgewater | MA | 2379 | United States | 7812647746 | Construction Manager | Dgreenberg@stonebridgehomesinc.com | DP-4075 | Breaker | - | 40 | - | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_6617.jpg&form-id=2&field-id=22&hash=e9702d5461edeeedb29b237d5d193ca99414b2b2c4fd8f334e28798515c7f68f , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_6616.jpg&form-id=2&field-id=22&hash=2934aa91d719acf14f203448358405d8cdc1c0ff08da102f7d0811df1fc6849f | 2025-10-31 | 2025-10-21 | [6 empty] | Electric oven circuit trips when oven is turned on. | Frigidaire | GCRE3060BFD | - | Single Family Home with attached In-law apartment | Kitchens in both the main house and the inlaw apartment | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_6613.jpg&form-id=2&field-id=42&hash=f0fe221428f949939b6f78c3c31770242199137f77a87b6bd54e0662e49330e8 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_6612.jpg&form-id=2&field-id=42&hash=efa31230bea52100da08f2c2772be7357f8ef983757c8d8a3f35ab0487439258 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_6611.jpg&form-id=2&field-id=42&hash=aeef6281cb40b95f8fc035db2f6a5a32f7a2d2acc143ed8acb4f33ba403bf785 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_6610.jpg&form-id=2&field-id=42&hash=d3d801f0f8e79bb9e8f093c86ab88d5648709464dac913b0ce2120b79cca23b7 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Daniel M. Greenberg
2025-11-05 11:41 | Cal | Harvey | 14426 | 8 | Pleasant Street | Plymouth | Massachusetts | 2360 | United States | 7816974950 | Assistant Project Manager | cal.harvey@thorndikedevelopment.com | BR240GF | Breaker |  | 40 |  | 2 Poles | Eaton | Residence |  | 2025-11-05 | 2025-10-29 | 90 Miter Dr |  | Plymouth | Massachusetts | 2360 | United States | Range causing breaker to trip repeatedly during normal use | Cafe | CHS900P2M9S1 |  | Townhome | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Cal Harvey
2025-11-06 11:02 | Peter | Daigle | 12359-B | 359 Main St. |  | Centerville | MA | 2632 | United States | 7742223888 | Owner of Robert Pierce Electrician | rwpelectrician@gmail.com | Legrande 1597-TRW | Receptacle |  | 15 | 20 Amp circuit | 1 Pole | Legrand | Residence |  | 2025-11-06 | 2025-11-05 | [6 empty] | Dishwasher trips multiple GFCI receptacles instantly. | Fisher Paykel | DD24DT19N | None | Home | Kitchen | No | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2Fimage.jpg&form-id=2&field-id=42&hash=fb6ade8107c1be5bb38249c8e1e134612b2d5fe44c5bb93db4eaa931f3b0c9de | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Robert W. Pierce
2025-11-06 14:40 | Jhon W | Herrera | 23281 | 35 Eutaw st |  | East Boston | Ma | 2128 | United States | 9789301547 | Electrician | jhon@theelectrichero.com | Eaton GFCI Type | Breaker |  | 50 |  | 1 Pole | Eaton | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FGFCI_Unwanted_Tripping_Report_Electric_Hero.pdf&form-id=2&field-id=22&hash=405dd2c1947a1a750d876cd6ed3c34fc258a809a68ad1719f549c51a72f2ae02 | 2025-10-14 | 2025-10-14 | [6 empty] | During inspection of a newly rewired kitchen circuit, a Miele KM7745 FL 240V induction cooktop was connected to an Eaton 50A 2-pole GFCI breaker to comply with code requirements. When the cooktop was energized, the breaker tripped immediately every time power was applied, preventing the appliance from operating. A complete diagnostic test was performed, including continuity and insulation resistance checks between both hot conductors (L1–L2) and the equipment grounding conductor. All readings were normal, and no faults or leakage to ground were detected. After confirming proper wiring and grounding, the GFCI breaker was replaced with a standard Eaton 50A 2-pole breaker, under which the cooktop operated normally. The tripping was determined to be caused by normal high-frequency leakage currents from the cooktop’s internal EMI filters and inverter circuits, which exceed Class A GFCI sensitivity thresholds but are within manufacturer specifications. | Miele Induction Cooktop (hard-wired appliance) | KM7745 FL | None – dedicated branch circuit for cooktop only | Single-family residence | Kitchen – dedicated 240V branch circuit supplying a hard-wired Miele induction cooktop. The GFCI breaker trips immediately when the cooktop is energized, preventing operation. | Yes | No | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FWhatsApp-Image-2025-11-06-at-2.22.23-PM.jpeg&form-id=2&field-id=42&hash=94bafd7d3f4f666e6686e8c044f71202080860308cb70ae9e0f4c8ee54eb83fe , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FWhatsApp-Image-2025-11-06-at-2.22.23-PM-1.jpeg&form-id=2&field-id=42&hash=f2932b7ab903fec20375d9c5307d8da439418704d78419e3f26f0c32bf6cfd63 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FWhatsApp-Image-2025-11-06-at-2.22.23-PM-2.jpeg&form-id=2&field-id=42&hash=8d68002b1289707e9053241cde8d0646ac795971c316f7ab53b174c0f3089580 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FWhatsApp-Image-2025-11-06-at-2.22.23-PM-3.jpeg&form-id=2&field-id=42&hash=5c817b7408c530b3a9d9971e9d29a2efb3b409058526fc57f9ae73921678e95b , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FWhatsApp-Image-2025-11-06-at-2.22.23-PM-4.jpeg&form-id=2&field-id=42&hash=422a4301f2b792e70b488f6241033b3c8b001c5b43e59353e602e6c6c085f63b , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FWhatsApp-Image-2025-11-06-at-2.22.23-PM-5.jpeg&form-id=2&field-id=42&hash=ba4237d5dc89f387a9eaa29d074e3397a42f8e3edc5a6f5882784f1e207c023b , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FWhatsApp-Image-2025-11-06-at-2.22.23-PM-6.jpeg&form-id=2&field-id=42&hash=457e831ec88784fc66e55b08b4aec55639ff889f28ff2e75f5c2c4a1464860d6 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FWhatsApp-Image-2025-11-06-at-2.22.23-PM-7.jpeg&form-id=2&field-id=42&hash=fae7e380b6d20396a1407d08ac6143a7d6060d6373377190e1b1fcaa858a5059 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FWhatsApp-Image-2025-11-06-at-2.22.23-PM-8.jpeg&form-id=2&field-id=42&hash=1b82ef8d8fa2c4606d0a7cbe64eac7940e4b256a3a42a150d5db04e3518a3754 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FWhatsApp-Image-2025-11-06-at-2.24.57-PM.jpeg&form-id=2&field-id=42&hash=31468ffaafdb55987dde2cb6c3978054cb8b6221ce6f3fd0e19ad80e97ed56e0 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jhon W Herrera
2025-11-06 16:14 | bernardo | empereur | 23648-A | 25 Walnut St | 25 walnut st | Milford | MA | 01757-2062 | United States | 7815181262 | CEO | bernardo@firstclasselectric-inc.com | LB250-G | Breaker |  | 50 |  | 2 Poles | Leviton | Residence |  | 2025-11-06 | 2025-11-03 | Kitchen | 80 Louise rd Newton MA | Newton | MA | 2467 | United States | We checked the stove to ensure the cord was connected correctly and confirmed that the ground and neutral wires were not mixed. We also inspected the panel, and everything was wired properly. Based on our findings, we believe the issue is with the stove itself. As soon as we turn it on, it trips the breaker. | Electrolux | ECFI3668AS |  | Residential | Kitchen/stove | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | bernardo empereur
2025-11-06 16:14 | bernardo | empereur | 23648-A | 25 Walnut St | 25 walnut st | Milford | MA | 01757-2062 | United States | 7815181262 | CEO | bernardo@firstclasselectric-inc.com | LB250-G | Breaker |  | 50 |  | 2 Poles | Leviton | Residence |  | 2025-11-06 | 2025-11-03 | Kitchen | 82 Louise rd Newton MA | Newton | MA | 2467 | United States | We checked the stove to ensure the cord was connected correctly and confirmed that the ground and neutral wires were not mixed. We also inspected the panel, and everything was wired properly. Based on our findings, we believe the issue is with the stove itself. As soon as we turn it on, it trips the breaker. | Electrolux | ECFI3668AS |  | Residential | Kitchen/stove | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | bernardo empereur
2025-11-07 08:57 | Tyler | Daniels | 1971 | 895 | Salem Street-2A | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | Schnider Electric | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-08-27 | 2025-10-30 | 2 School House Road | Unit 1407 | Gloucester | MA | 1930 |  | Stove continually tripping | GE | JB645RK6SS |  | Apartment | Kitchen stove | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels
2025-11-07 09:02 | Tyler | Daniels | 1971 | 895 | Salem Street-2A | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | Schnider Electric | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-09-24 | 2025-10-30 | 2 School House Road | Unit 2313 | Gloucester | MA | 1930 |  | Stove continuous tripping | GE | JB645RK6SS |  | Apartment | Kitchen, stove | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels
2025-11-07 12:52 | Stephen | Daniels | 16467A | 895 Salem Street 2A |  | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | THQL2150GFI | Breaker |  | 50 |  | 1 Pole | ABB | Residence |  | 2025-09-09 | 2025-10-20 | 71 Boston Road |  | North Billerica | MA | 1862 | United States | Stove frequently tripping breaker | GE Appliances | JS660SL2SS |  | Apartment | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Stephen Daniels
2025-11-10 10:13 | James | Loughlin | A17387 | PO BOX 72 |  | Franklin | MA | 2038 | United States | 5085280765 | OWNER | sales@loughlinelectric.com | QF250A | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-10-18 | 2025-10-18 | GARAGE PANEL | 8 FLEETWOOD DR | Franklin | Massachusetts | NORFOLK 02053 | United States | START UP THE STOVE THE GFCI BREWAKER TRIPPS | GE | JBP24BH1WH | NO | KITCHEN | KITCHEN RANGE TRIPS WHEN IT COMES ON | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | James Loughlin
2025-11-10 10:44 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-10-01 | 2025-10-02 | 2101 Codman Way | West Park Drive | Westborough | MA | 1581 | United States | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 10:46 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2102 Codman Way |  | Westborough | MA | 1581 | United States | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 10:49 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2103 Codman Way |  | Westborough | Massachusetts | 1581 | United States | When warming up the oven | Whirpool | WFE775H0HZ5 |  | Condo | When warming up the oven | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 10:50 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2104 Codman Way | Unit #5 | Westborough | MA | 581 | United States | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 10:52 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2105 Codman Way |  | Westborough | MA | 1581 | United States | When warming up the oven | Whrilpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 10:55 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2106 Codman Way | West Park Drive | Westborough | MA | 1581 | United States | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 10:58 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2107 Codman Way |  | Westborough | MA | 1581 | United States | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:17 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2108 Codman Way |  | Westborough | MA | 1581 | United States | When warming up the oven | Whirpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:19 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2109 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:22 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2110 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:24 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2111 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:27 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2112 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:29 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2113 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:30 | Dominic | Giancaterino | 23014-a | 55 wedge wood ave | Apt 1 | Worcester | Ma | 1604 | United States | 9783209228 | Master electrician | domcg94@gmail.com | JBS360DMBB | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-11-07 | 2025-11-07 | [6 empty] | Tripped when stove was on | General Electric | JBS360DMBB |  | Duplex | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_0062.jpeg&form-id=2&field-id=42&hash=5526d44efa866ddce9a672777f6090eaa63e1c05f86e2de84d400e1568802967 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Dominic giancaterino
2025-11-10 11:31 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2201 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:32 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2202 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:34 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2203 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:35 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2204 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:37 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2205 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:37 | Dominic | Giancaterino | 23014-A | 55 wedgewood ave | Apt 2 | Worcester | Ma | 1604 | United States | 9783209228 | Master electrician | domcg94@gmail.com | JBS360DMBB | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-11-07 | 2025-11-07 | [6 empty] | Tripped when stove was on | General Electric | JBS360DMBB |  | Duplex | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_00621.jpeg&form-id=2&field-id=42&hash=9f057b8edf0c07f7250ad0e4c9dff5287b96c31a1c7802752d52bf87b03d6174 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Dominic giancaterino
2025-11-10 11:38 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2206 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:40 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2207 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:41 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2208 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:43 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2209 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:44 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2210 Codman Way |  | Wstborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:45 | Dominic | Giancaterino | 23014-a | 55 wedgewood ave | Apt 2 | Worcester | Ma | 1604 | United States | 9783209228 | Master electrician | domcg94@gmail.com | GTD45EASJWS | Breaker |  | 30 |  | 2 Poles | Siemens | Residence |  | 2025-11-07 | 2025-11-07 | [6 empty] | Tripping when dryer is on | General Electric | GTD45EASJWS |  | Duplex | Laundry room | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_00622.jpeg&form-id=2&field-id=42&hash=4c0d36c1a8bbed174cc3cc42edf2e8618ea34fc4c52c71919a1d19f9e3a574ff | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Dominic giancaterino
2025-11-10 11:46 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2211 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:47 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2212 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:49 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2213 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:49 | Dominic | Giancaterino | 23014-A | 55 wedgewood ave | Apt 1 | Worcester | Ma | 1604 | United States | 9783209228 | Master electrician | domcg94@gmail.com | GTD45EASJWS | Breaker |  | 30 |  | 2 Poles | Siemens | Residence |  | 2025-11-07 | 2025-11-07 | [6 empty] | Tripping when dryer is on | General Electric | GTD45EASJWS |  | Duplex | Laundry room | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_00623.jpeg&form-id=2&field-id=42&hash=8a412b8a8a1a54c3a24cc9763fdc81618ee713074bfc802d161513e0a9db959d | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Dominic giancaterino
2025-11-10 11:57 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2301 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 11:58 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2302 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:00 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2303 Codman Way |  | Wetsborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:02 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2304 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:04 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2305 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:06 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2306 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:07 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2307 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:11 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2308 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:12 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2309 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:14 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2310 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:17 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2311 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:20 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2312 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:27 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2401 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:29 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 15 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2402 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:31 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2403 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:33 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2404 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:34 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2405 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:36 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2406 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:37 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2407 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:39 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2408 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:40 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2409 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:41 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2410 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:43 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2411 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-10 12:45 | Mark | Thibault | 14667 | 1 Industrial Way | Unit #5 | Tyngsboro | MA | 1879 | United States | 9782265946 | President | mark@stelectrical.net | Schneider HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-01 | 2025-10-02 | 2412 Codman Way |  | Westborough | MA | 1581 |  | When warming up the oven | Whirlpool | WFE775H0HZ5 |  | Condo | Kitchen | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Thibault
2025-11-11 09:20 | Jhoan | Sanchez | 11008 B | 23 Fairmount ST 1 |  | Dorchester | MA | 2124 | United States | 6179087871 | ELECTRICIAN | JHOAN170@GMAIL.COM | BRN250GFCS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FScreenshot_20251111_090831_Samsung-Internet.jpg&form-id=2&field-id=22&hash=bb6424aa49a89ce10f2e153e9ea13fdd28bd73ade315adb05caf168372996c60 | 2025-09-23 | 2025-09-23 | 4 LISA LANE |  | ACTON | MA | 1720 | United States | As soon as the 50A GFCI breaker for the cooktop was turned on, the breaker tripped immediately. | MIELE | KM7740 |  | SINGLE FAMILY HOME | THE ROOM AFFECTED BY TRIPPING IT THE KITCHEN cooktop. | No | Yes | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | JHOAN SANCHEZ
2025-11-11 19:19 | Peter | Daigle | 12359-B | 359 Main St. |  | Centerville | MA | 2632 | United States | 7742223888 | Owner of Robert Pierce Electrician | rwpelectrician@gmail.com | Legrande 1597-TRW | Receptacle |  | 15 | 20 Amp circuit | 1 Pole | Legrand | Residence |  | 2025-11-06 | 2025-11-05 | [6 empty] | Dishwasher trips multiple GFCI receptacles instantly. | Fisher Paykel | DD24DT19N | None | Home | Kitchen | No | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Robert W. Pierce
2025-11-12 11:14 | phillip | Aiello | 56112 | 399 Page St |  | Lunenburg | MA | 1462 | United States | 9788360515 | owner | philaielloelec@gmail.com | Siemens | Breaker |  | 40 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2Fstove.jpeg&form-id=2&field-id=22&hash=f056260ce52908af434bbcea741c03c44af5fa16bf994746245b034167bb9576 | 2025-11-05 | 2025-11-04 |  | 44 Nodd Rd. | Groton | MA |  | United States | The GFCI breaker for the stove immediately trips right when the breaker is turned on. Tried installing a different breaker and that did not work. | Electrolux | ECFI3668AS |  | Single family | kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2Fstove1.jpeg&form-id=2&field-id=42&hash=52dde091d26ad69764d0c028a26fbfa141aadcc519aa52e84746ac2157527deb | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Phillip Aiello
2025-11-12 12:58 | Tyler | Daniels | 1971 | 895 Salem Street-2A |  | Groveland | MA | 1834 | United States | 9783731393 | electrician | office@danielsel.com | Siemens | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-09-24 | 2025-10-20 | 37 Woodcock Unit 24 |  | Haverhill | MA | 1832 |  | Trips continoulsy while stove is heating | GE | JB256DM2BB |  | Apartment | Kitchen stove | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels
2025-11-12 14:59 | John | McCurdy | 20172 A | 330 Lynnway | Suite 210 | Swampscott | Massachusetts | 1907 | United States | 7815957074 | President | info@mccurdyelectric.com | Q230GFP | Breaker |  | 30 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FSiemens-30A-GFCI-Breaker.jpg&form-id=2&field-id=22&hash=dfcf20a99de8615583ddf5d22d04228f6fde126ecdb60d689746ba3ecf1d1a1a | 2025-10-03 | 2025-09-02 | Trebisacci Residence | 3 Gerry Street | Marblehead | MA | 1945 | United States | The 240V 30A circuit is for an electric clothes dryer. The dryer equipment spec mentions an integral GFCI device, which appears to be incompatible with the Siemens GFCI breaker and was causing the breaker to trip. | Samsung | WD53DBA900HZ | None | Single Family Dwelling | First Floor Bathroom Laundry Closet | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FDryer.jpg&form-id=2&field-id=42&hash=3ee742d90ec939de64a527d59d766e1bfe847fd32cf11f0c7ae1d74235158a22 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Douglas McLeod
2025-11-13 07:48 | Tyler | Daniels | 1971 | 895 Salem Street-2A |  | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | Siemens | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-10-09 | 2025-11-11 | 52 Victor | Unit 15 | Haverhil | MA | 1834 | United States | Trips while stove is heating | GE | JB256DM2BB |  | Apartment | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels
2025-11-13 09:16 | steven | marcouillier | 52053 | 18 shufelt road |  | walpole | ma | 2081 | United States | 978-460-9420 | inspector for sunrun | steven.marcouillier@sunrun.com | eaton | Breaker |  | 40 |  | 2 Poles | Eaton | Residence |  | 2025-11-11 | 2025-11-07 | [6 empty] | we installed the gfi brealer to come up to the code requirement but it started tripping we reset it and again it trip so we replaced it wirh a requglar two pole eaton breaker and it is working | whirlpool | part number 8053304 rev b | no | kitchen | just the stove | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_8719.JPG&form-id=2&field-id=42&hash=3b2969a2668ea1bc8ff105efb43db1e0846aa843b16166f648f00cf6388474f1 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_8720.JPG&form-id=2&field-id=42&hash=072ecea68ef8ea7b838d3c9cfa8f388a7a30e7958194243a3e8fe37c95586569 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | steven marcouillier
2025-11-13 12:54 | Welch | Electrical Systems, Inc. | 17139A | 190 Pleasant Street |  | Rockland | MA | 02370-1229 | United States | 781-878-6001 | Master Electrician/Business Owner | wwelch@welchelectricalsystems.com | QO 250 | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-08-07 | 2025-07-18 | 60 Jerusalem Road |  | Cohasset | MA | 2025 | United States | The induction range is tripping after most uses. Tried to reset the breaker multiple times and changed the breaker. Neither resolved the issue. | Wolf | IR36551/S/P | None - The stove is on a separate circuit. | Single family residence | The kitchen in a single family residence. | No | No | No | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | William Welch
2025-11-14 08:09 | Jennifer | Sweet | 18329 | 525 | Coronation Drive | Franklin | MA | 2038 | United States | 5085414117 | Owner | jensweetelectricllc@yahoo.com | Siemens gfci breaker | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-10-01 | 2024-09-25 | 126 | Summer st | Medway | MA | 2053 | United States | The oven has been tripping periodically since it was installed | Kitchenaid | Ksdg950ess6 | No | Single family dwelling | Kitchen oven | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_9625.jpeg&form-id=2&field-id=42&hash=1fa8f85478a1b9f5e94a23fd4327123624a141f934b33835ac6a54b93a741d54 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_9626.jpeg&form-id=2&field-id=42&hash=fafe99758a1709e66231d646b0bd3e5509e2623d2f1743a78ca5fa22aa45797d | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jennifer Sweet
2025-11-14 16:41 | Steve | Laurencio | 18079 | 37 Carey Ave |  | Burlington | Ma | 1803 | United States | 978 621-7221 | Electrician | steve@desousaelectric.com | Square D Hom230GFI | Breaker |  | 30 |  | 2 Poles | Schneider Electric | Residence |  | 2025-11-14 | 2025-11-14 | 37 Carey Ave |  | Burlington | Ma | 1803 | United States | Circuit breaker trips on baking cycle. | Wolf | S03050PE/S/P | no | Single family | Kitchen wall oven. | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Steve Laurencio
2025-11-16 08:39 | Hector | Quinonez | 53239-B | 1277 Washington St |  | Abington | MA | 2351 | United States | 9789962429 | Owner | hraulq@gmail.com | QF250AP | Breaker |  | 50 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FSiemens-GFCI.jpg&form-id=2&field-id=22&hash=f4dbffeb276e47a57202348ab561e8c7e1c71d21381fb99f909f7b79046c06dd | 2025-10-18 | 2025-11-08 | [6 empty] | Breaker trips any time the oven is set to above 300F | Whirpool | WFE505W0JZ3 |  | Single Home | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FNew-Breaker.jpg&form-id=2&field-id=42&hash=1786168dcee64e6b92d49cafe790cc8ddcc5e0017a9d67d8db07c47d766cbed7 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Hector Quinonez
2025-11-17 12:51 | Gregory | Doelp | E51570 | 9 Uncle Marks Way |  | Orleans | MA | 2653 | United States | 7814243940 | Homeowner | grdoelp@comcast.net | Schneider Electric Square D Homeline HOM230GFI (4884006004, Type S1 120/240V 60 Hz, HACR Type, Listed C.B.W./G.F.C.I. Issue No. AD-910) | Breaker |  | 30 |  | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_2277.JPG&form-id=2&field-id=22&hash=5208357a8776872ca807c4801fc3a25885f11144ca8953dc159b318a5a1bca33 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_2276.JPG&form-id=2&field-id=22&hash=e2f0b3a4f16087481933287033ffbf65b447ed50dae8620db9315c18a4a82f60 | 2025-10-27 | 2024-03-11 | [6 empty] | GFCI Breaker trips immediately as soon as a cycle is started on the clothes dryer. When the breaker is reset, power is provided to the clothes dryer (as indicated by the lights on the control panel that come on). As soon as you try to start the dryer, the breaker trips immediately. Even if there are no clothes in the dryer, the breaker trips as soon as you try to start the dryer. Note: I notified the local electrical building inspector (wire inspector) as required on the Consent Form below, and he said no further action is required by him. The Consent Form says &quot;my review included ... field cord connections and equipment grounding return paths&quot;. I am the homeowner, not an electrician or electrical inspector so I am not qualified to inspect the wiring. The electrical contractor and wiring inspector reviewed the wiring when the electrical contractor installed the GFCI breaker. | Electrolux (Clothes Dryer) | ELFE7637AT0 | None | Single Family Residence | Laundry Room Note: I notified the local electrical building inspector (wire inspector) as required on the Consent Form below, and he said no further action is required by him. The Consent Form says &quot;my review included ... field cord connections and equipment grounding return paths&quot;. I am the homeowner, not an electrician or electrical inspector so I am not qualified to inspect the wiring. The electrical contractor and wiring inspector reviewed the wiring when the electrical contractor installed the GFCI breaker. | No | Yes | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FDryer-Nameplate.JPG&form-id=2&field-id=42&hash=d0031179493cc92fda32fd6ecc869def278c18e67878c5be200bb47bbb04f790 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FClother-Dryer-Installation.JPG&form-id=2&field-id=42&hash=9be2b6e80d9190b7fa1d91c985f8952ade0fca133e2fc90fa0c1264ecb68bf63 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Gregory R Doelp (Home Owner - not Electrician)
2025-11-17 17:18 | Robert | Burkett | 14236 | 193 L St |  | Boston | MA | 2127 | United States | 6173892257 | manager | burkettelectric@gmail.com | Eaton BRP120Df | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-11-17 | 2025-11-17 | 275 Old Colony |  | Boston | MA | 2127 | United States | Dishwasher trips on a regular basis despite install a new dual function breaker some months ago | Asko | D5656 |  | Multi family dwelling | Kitchen | No | Yes | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FIMG_8931.jpeg&form-id=2&field-id=42&hash=5f9e155a4a93e3dad9f5d6aa38690e8b4c15cf492e905006e7bb240845a74219 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Robert S. Burkett
2025-11-17 18:27 | Michael | Carpenter | 13686 B | 76 Essex Avenue | b | Gloucester | MA | 1930 | United States | 9785091789 | Owner/Operator Michael Carpenter Electrician, LLC | mike.carp23@comcast.net | BRN250GF | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-11-10 | 2025-10-31 | 5 Middleton Rd |  | Boxford | MA | 1921 | United States | Trips every time the oven or cook top is turned on | AGA | AEL481IN | none- dedicated circuit | One family | Kitchen | No | No | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FAGA-Elise-481-IN-SPECS.pdf&form-id=2&field-id=42&hash=a58abf785c8b1fdbc23dae382e025d7757de4c0f72b7538847796049e96d739e | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Michael Carpenter
2025-11-18 08:11 | Michael James | Ballou | 23028-a | 4 Lalia Ln |  | Billerica | MA | 1821 | United States | 6033659916 | Electrician | mballouelectrician@yahooo.com | Seimens | Breaker | GFCI | 50 |  | 2 Poles | Siemens | Residence |  | 2025-11-18 | 2025-11-18 | 49 Fernglade |  | Burlington | MA | 1803 | United States | Stove runs for 3-4 minutes then trips GFCI | Frigidaire | GCRE3060AFG |  | Home | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Michael J Ballou
2025-11-18 09:21 | Luke | Fontes | A15437 | 345 Washington Street |  | Pembroke | Massachusetts | 2359 | United States | 7812647062 | Project Manager | lfontes@yourelectricalsolutions.com | BRN250GFCS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-02 | 2025-01-01 | 6 Lamartine Street |  | Boston | Massachusetts | 2130 | United States | Electric range and cooktop breaker trips after a few seconds of being energized. Manufacturer acknowledges the issue and insisted this is due to the moisture/oil in the components from factory/shipping. Referred to as nuisance tripping and was suggested this is a known issue in the industry that range and breaker manufacturers have yet to fully address. | Whirlpool | WCC31430AW | NA | Apartment | 123 Units within apartment building. | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Luke Fontes
2025-11-18 09:30 | Luke | Fontes | A15437 | 345 Washington Street |  | Pembroke | Massachusetts | 2359 | United States | 781-331-3500 | Project Manager | lfontes@yourelectricalsolutions.com | BRN250GFCS | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-06-01 | 2025-01-01 | 2 Lamartine |  | Boston | Massachusetts | 2130 | United States | Electric range and cooktop breaker trips a few seconds after being energized. Manufacturer acknowledges the issue and insists this is due to moisture/oil in the components from factory/shipping. Referred to as nuisance tripping and was suggested this is a known issue in the industry that range and breaker manufacturers have yet to full address. | Whirlpool | WCC31430AW | NA | Apartment | 100 Units within the apartment building. | No | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Luke Fontes
2025-11-19 12:25 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 201 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:29 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 202 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:33 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 203 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:35 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 204 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:37 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 205 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:38 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 206 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:40 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 207 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:41 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 208 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:42 | Chase | Locke | 14426-A Exp. 7-31-28 | 52 Kestrel Heights |  | Plymouth | MA | 2360 | United States | 2076028923 | Assistant Construction Manager | clocke@tollbrothers.com | Eaton BRN250GF | Breaker |  | 15 |  | 1 Pole | ABB | Residence |  | 2025-10-03 | 2025-07-30 | [6 empty] | The homeowner has used their oven twice now and both times it has tripped. | KitchenAid | KOED530PSS |  | Single Family | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Chase Locke
2025-11-19 12:42 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 209 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:45 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 210 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:47 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 212 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:48 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 301 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:49 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 302 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:50 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 303 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:51 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 305 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:52 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 306 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:54 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 307 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:55 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 308 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 12:59 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 309 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 13:01 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 310 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 13:30 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 311 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 13:34 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 312 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 14:15 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 313 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 14:16 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 314 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 14:27 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 315 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 14:29 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 316 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 14:32 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 317 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-19 17:35 | Hristo | Petrov | 52190 | 85 Merrimac Street |  | Woburn | MA | 1801 | United States | 7816408969 | Electrician | hristopetrov1974@yahoo.com | Eaton/BRN250GF | Breaker |  | 50 |  | 2 Poles | Eaton | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2Fimage1.jpg&form-id=2&field-id=22&hash=f1a47da1d8f185fa7c09693b7027d720501d99027f904cf9c10b154c76b88691 | 2025-11-18 | 2025-03-28 | 12 Wilson Rd |  | Lexington | MA | 2420 | United States | Couple min after turning the oven on the GFCI breaker trips. | Thermador | ME302 YP |  | House / kitchen | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F11%2FView-recent-photos.jpeg&form-id=2&field-id=42&hash=5cf2b2fb3161a3864d9429cd8d34a8875f90eb087355297d3f6bb67655043e7f | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Hristo Petrov
2025-11-19 20:25 | Andy | Courtade | 39574e | 11 1st Ave |  | Bellingham | MA | 2019 | United States | 5088162001 | Owner | ezek1@verizon.net | Seimans | Breaker |  | 30 |  | 2 Poles | ABB | Residence |  | 2025-06-02 | 2025-06-02 | 11 1st Ave |  | Bellingham | MA | 2019 | United States | Cooktop will not work with gfci breaker | Fridgidare gallery | GC-CI3067AB |  | Residential | In law kitchenette | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Andy Courtade
2025-11-19 22:28 | Michael | Hughes | A18156 | 1152 Main St |  | Reading | Ma | 1867 | United States | 7817109912 | Owner M Hughes Electrical Contractor Master Electrician | wirenut277@verizon.net | THQL2150GFT2 | Breaker |  | 50 |  | 2 Poles | ABB | Residence |  | 2025-11-09 | 2025-09-04 | 16 Ramgren Road | 16 Ramgren Road | Reading | Ma | Lunenburg | United States | Installed Breaker. Turned on range top burners no issue. Then turned on oven and gfci trip at 1.5 minutes. I have tried 3 different gfci breakers all with same result. Performed 500 degree oven temp for 1 hour. Let cool and replaced breaker again for the 4th time and tripped at 1.5 minutes. That is 4 different brand new breakers. Customer was very mad and I pulled gfci breaker out. installed regular breaker with no issues. | Ge electric stove with oven | J BP35DM1WW | No Seperate circuit | Single family cape style house | Kitchen stove | No | Yes | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Michael E Hughes
2025-11-20 07:51 | Steven | Rooney | A13678 | 401 South Street |  | Marlborough | MA | 1752 | United States | 5084813299 | Service manager - Giombetti Electric | Steven@Giombettielectric.com | BRN250GF | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-11-18 | 2025-11-14 | 401 South Street |  | Marlborough | MA | 1752 | United States | breaker trip as soon as you turn the range on | Thermador | PRI30LBHU/05 | none | single family home | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Steven Rooney
2025-11-20 08:41 | Steven | Rooney | A13678 | 401 South Street |  | Marlborough | MA | 1752 | United States | 508-481-3299 | Service Manger - Giombetti Electric | Steven@Giombettielectric.com | BRN250GF | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-11-18 | 2025-11-14 | 128 Prendville Way |  | Marlborough | MA | 1752 | United States | breaker trips as soon as you turn on the range | Thermador | PRI30LBHU/05 |  | single family home | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Steven Rooney
2025-11-20 09:35 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 318 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-20 09:37 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 319 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-20 10:39 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 320 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-20 11:32 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 321 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-20 11:38 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 322 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-20 11:42 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 323 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-20 11:44 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 324 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-20 11:51 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 325 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-20 12:01 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 326 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-20 13:43 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET | PO BOX 384 | LEE | Massachusetts | 1238 | United States | 2430690 | OWNER/VP | john@henryselectricinc.com | BR240 | Breaker |  | 40 |  | 2 Poles | Eaton | Residence |  | 2025-09-19 | 2025-02-27 | 200 LAUREL ST | APT 11 | LEE | Massachusetts | 1238 |  | BREAKER DOES NOT HOLD, KEPT TRIPPING. | SUMMIT | REXT20SS |  | Apartment | KITCHEN | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | JOHN LEPREVOST
2025-11-20 13:57 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET | PO BOX 384 | LEE | Massachusetts | 1238 | United States | 4132430690 | OWNER/VP | john@henryselectricinc.com | B250 | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-11-13 | 2025-01-27 | 200 LAUREL ST | APT 15 | LEE | Massachusetts | 1238 | United States | BREAKER DOES NOT HOLD, KEPT TRIPPING. | FRIGIDIARE | FCFE2425AS |  | APARTMENT | KITCHEN | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | JOHN LEPREVOST
2025-11-20 14:06 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 327 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-20 14:21 | JOHN | LEPREVOST | 32553 | 252 MAIN STREET | PO BOX 384 | LEE | Massachusetts | 1238 | United States | 4132430690 | OWNER/VP | john@henryselectricinc.com | SQUARE D QO120 | Breaker |  | 20 |  | 1 Pole | Schneider Electric | Residence |  | 2018-11-13 | 2025-10-30 | 24 LAKESIDE TERRACE |  | MONTEREY | Massachusetts | 1245 | United States | BREAKER DOES NOT HOLD, KEPT TRIPPING. | SUBZERO | BI-36UG/S/PH-LH |  | SINGLE FAMILY | BASEMENT BAR | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | JOHN LEPREVOST
2025-11-21 07:28 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 328 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 07:29 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 330 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 07:30 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 401 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 07:32 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 402 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 07:33 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 403 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 07:34 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 405 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 07:35 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 406 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 07:40 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 407 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:14 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 2 Poles | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 408 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:16 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 409 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:18 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 410 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:21 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 411 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:22 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 412 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:23 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 413 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:24 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 414 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:25 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 415 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:50 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 416 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:52 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 417 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:55 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 418 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:56 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 419 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:58 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 420 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 09:59 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 421 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:00 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 422 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:01 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 423 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:02 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 424 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:03 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 425 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:04 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 426 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:05 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 427 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:06 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 428 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:07 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 430 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:08 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 501 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:09 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 502 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:10 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 503 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:11 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 505 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:12 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 506 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:13 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 507 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:14 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 508 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:15 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 509 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:16 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 510 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:17 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 511 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:18 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 512 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:19 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 513 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:20 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 514 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:21 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 515 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:21 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 516 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:23 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 517 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:24 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 518 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:25 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 519 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:25 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 520 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:27 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | MA | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 521 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:28 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 522 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:29 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 523 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:30 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 524 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:32 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 525 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:33 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 526 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:34 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 527 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:35 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 528 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:36 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | APT 530 | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 10:37 | Kevin | Callahan | 20710A | 275 Centre Street | 14 | Holbrook | Massachusetts | 2343 | United States | 781-864-5785 | Owner | kevinc@gopesinc.com | BRN120GF | Breaker |  | 20 |  | 1 Pole | Eaton | Residence |  | 2025-04-01 | 2025-03-01 | 3 Wainwright Road | SFAM | Winchester | MA | 1890 | United States | BREAKER TRIPPING WHEN USING THE GAS STOVE FREQUENTLY | GE | JGSS66SEL5SS |  | APARTMENT | GAS STOVE ONLY | Yes | Yes | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Kevin Callahan
2025-11-21 14:49 | Steven | Rooney | A13678 | 401 South Street |  | Marlborough | MA | 1752 | United States | 5084813299 | Service Manger / Giombetti Electric | Steven@Giombettielectric.com | Eaton BRN240GF | Breaker |  | 40 |  | 2 Poles | Eaton | Residence |  | 2025-11-19 | 2025-10-31 | 261 Boston Post Road East Unit 1 |  | Marlborough | MA | 1752 | United States | breaker trip when range is turned on | General Electric | J Bp23D R2WW |  | apartment style condo | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Steven Rooney
2025-11-24 11:48 | Jeffrey | Pagnini | 58824 B | 31 Coachman Lane |  | Natick | MA | 2056 | United States | (857) 231-1460 | Electrician | Jeff.pagnini@gmail.com | Eaton/BRN120DF | Breaker |  | 20 |  | 1 Pole | ABB | Residence |  | 2025-09-26 | 2025-09-25 | [6 empty] | Fridge trips breaker after about 90 seconds of being reset | Samsung | RF22K9381SR |  | House | Kitchen area fridge | No | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jeffrey Motha
2025-11-24 15:56 | Cal | Harvey | 14426 | 8 Pleasant Street | A-2 | Natick | Massachusetts | 1760 | United States | 7816974950 | Assistant Project Manager | cal.harvey@thorndikedevelopment.com | BRN240GF & BRN250GF | Breaker | BR | 40 | 50 | 2 Poles | Eaton | Residence |  | 2025-11-20 | 2025-11-06 | 53 Oxbow Road |  | Raynham | Massachusetts | 2767 | United States | The breakers for both the kitchen range as well as the dryer are tripping constantly and the homeowner has filed a complaint | GE | GE Stainless GRF500PVSS |  | Townhome | Kitchen and Laundry Room | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Cal Harvey
2025-11-28 09:08 | Gilbert | Martin | 24698E | 59 Gurnet Rd |  | Duxbury | MA | 2332 | United States | 617-293-7627 | Installation oversight | gc@martinsrock.net | Square D QO230GFI | Breaker |  | 30 |  | 2 Poles | Schneider Electric | Residence |  | 2024-10-24 | 2024-10-24 | 319 Cushing St |  | Hingham | MA | 2043 | United States | The manufacturer's installation instructions illustrate a 3 wire connection (240V with ground) and also indicates installation not compatible with GFCI protection. Return current for the smart house communications module is imposed on the ground in excess of 5mA. | Bosch | NITP060SUC | not applicable | Single family dwelling | Kitchen | No | No | No | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Gilbert E Martin, Jr
2025-12-01 08:04 | John | Tamasi | 12321A | 6 Easy st |  | Windham | New Hampshire | 3087 | United States | 6032476135 | Electrician | johntamasi@yahoo.com | Siemens Q120DFP | Breaker |  | 20 |  | 1 Pole | Siemens | Residence |  | 2025-09-09 | 2025-09-09 | 480 Washington Street |  | Brookline | mass | 3087 | United States | Installed Siemens 20-amp new dual beaker day 1 held. Overnight tripped. Went back checked for any leaks in the wiring. All good. Replaced with new 20-amp dual breaker and tripped overnight again. | Bosch | B36CT80SNS/44 | No | Single Family Home | Kitchen Fridge only | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | John Tamasi
2025-12-02 07:43 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker | N/A | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1 KELLEHER RD | UNIT 1 | BEVER | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 07:45 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 2 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 07:52 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 3 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 07:57 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 4 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 07:59 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 5 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:01 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 6 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:03 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 7 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:06 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 8 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:08 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 9 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:11 | Joseph | Spinale | 38463E | 28 Turner Dr |  | North Reading | Massachusetts | 1864 | United States | 6178772227 | Owner | jspinale75@gmail.com | HOM250GFI | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-12-01 | 2025-11-21 | 24 Mt Zion Rd |  | Melrose | MA | 1876 | United States | New freestanding Range. Once you turn on equipment it immediately trips. We double checked the cord wiring and neutral isolation. Installed a new GFCI breaker and same problem. Equipment will not work with GFCI protection | Bosh | HIS8655U /07 | No | Single Family | Kitchen Range | No | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Joseph Spinale
2025-12-02 08:12 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 10 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:14 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 11 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:17 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 12 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:21 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 13 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:23 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 14 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:28 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 15 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:30 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 16 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:37 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 17 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:41 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 18 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:48 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 19 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:52 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 20 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:55 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 21 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:56 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 22 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 08:59 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240a | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 23 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:00 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 24 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:05 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 25 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:07 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 26 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:10 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 27 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:12 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 28 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:33 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 29 | BEVERLY | MA |  | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:35 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 30 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:36 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 31 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:38 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 32 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:42 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 33 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:44 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 34 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:45 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 35 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:51 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 36 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:53 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 37 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:57 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 38 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 09:58 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 39 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 10:01 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 40 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:04 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 41 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:05 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 42 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:07 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 43 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:11 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240a | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 44 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:12 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 45 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:14 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 46 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:16 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 47 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:18 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 48 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:19 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 49 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:23 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 50 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:25 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 51 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:26 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 52 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:27 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 53 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:29 | Christopher | Stevens | 20665A | 275 Centre Street | Suite 1 | Holbrook | MA | 2343 | United States | 7812935701 | manager | ashley@cdscontracting.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-21 | 2025-11-21 | 1-54 KELLEHER RD | UNIT 54 | BEVERLY | MA | 1915 | United States | The stove trips right away when the stove is turned on. Tried resetting the circuit breaker many times, but it will not hold. | FRIGIDAIRE | FCFE2425AW |  | KITCHEN | KITCHEN | Yes | No | Yes | Yes |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Christopher Stevens
2025-12-02 11:38 | Anthony | Triolo | 54913-B | 8 Hayford Trail |  | Hanson | MA | 2341 | United States | 5088136244 | Electrical Contractor | atrioloelectric@gmail.com | AD-910 | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG_2954.jpeg&form-id=2&field-id=22&hash=97fc4bbaf3819b94472e860718119f2c27f5b7b62ee348c90c208571de74761e | 2025-12-02 | 2025-12-02 | [6 empty] | Stove trips immediately | Electrolux | GCFE3060BFG |  | Duplex | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG_2156.jpeg&form-id=2&field-id=42&hash=c0a82988c5d6056dbe278496222e6dfc44b3909693b88422ec5c17e31b5b91f4 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG_2292.jpeg&form-id=2&field-id=42&hash=9535c26cf433c78c27beb28f36f365cea8f7602403c8a0d18e6cc102d720f1ba | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Anthony Triolo
2025-12-02 11:55 | Anthony | Triolo | 54913-B | 6 Hayford Trail |  | Hanson | MA | 2341 | United States | 5088136244 | Electrical Contractor | atrioloelectric@gmail.com | AD-910 | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG_29541.jpeg&form-id=2&field-id=22&hash=a7b7a06ace95517f0aa4a45b0f005203e0fbd616f424800812d60bfc878f2c0d | 2025-12-02 | 2025-12-02 | [6 empty] | Stove trips immediately | Electrolux | FCRE3062ABC |  | Duplex | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG_4204.jpeg&form-id=2&field-id=42&hash=48f3b087611158bb4dea555f6e07358a7262841a05a3df9825ce63074180fd86 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG_4202.jpeg&form-id=2&field-id=42&hash=478f54f5ee5acd6ac734b285c3c6f8978e1bc452944bbcea440cd3e25bfd4e4a | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Anthony Triolo
2025-12-03 14:06 | Mark | VanMolle | A-13527 | PO Box 1534 |  | Littleton | MA | 1460 | United States | 978-337-6541 | Contractor | castlecp@hotmail.com | Siemens Q120DFN | Breaker |  | 20 |  | 1 Pole | Siemens | Residence |  | 2025-11-21 | 2025-06-05 | 366 King St. |  | Littleton | MA | 1460 | United States | Installed a 20-amp dual-function breaker on a new microwave. It continuously trips. Replaced the breaker. No change. | Samsung | ME11A7510DS |  | Apartment | Kitchen. | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark VanMolle
2025-12-03 20:19 | David | Escalante | 22891-A | 3 Henry's Path |  | Upton | MA | 1568 | United States | 7742440340 | Master Electrician | escalanteelectric@gmail.com | EATON CHC BRN240GF 2pole 40amp GFI | Breaker |  | 40 |  | 2 Poles | Eaton | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FElectrical-Permit-32-Churchill-Rd-Sudbury.jpg&form-id=2&field-id=22&hash=bad548c57f1bd182da3f128e65bf1c87d81e6b8eddbf6713e552f26e6f04295a , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FWall-Oven-Specs.pdf&form-id=2&field-id=22&hash=7d2f7e732918e77b23229e01daa02761c25ce875b86da013b2d2e890d533c38c | 2025-11-03 | 2025-10-27 | 32 Churchill St |  | Sudbury | MA | 1776 | United States | Upon wiring and installing a brand new oven, it trips the GFI breaker randomly. We have spoken with the manufacturer, the store it was purchased at, as well as the electrical inspector about this issue. All installation and wiring has been double checked for accuracy. | Bosch | HBL87M53UC |  | House | Kitchen, Oven | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2F40amp-GFI-Breaker-install-picture-2.jpg&form-id=2&field-id=42&hash=91074c909e449c8afbabd93920406cf9a9192d74d35563eea5aff9740422ed52 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2F40amp-GFI-Breaker-install.jpg&form-id=2&field-id=42&hash=58f3a26e917689924f728031c3d274f858b99720a9646ca2f85b9dfad06835e4 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FOven-hardwired-junction-box.jpg&form-id=2&field-id=42&hash=b491ba79f66031da47e9337bbd267786663cdc57d9784db33d2f7ef2aa7cf0f0 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FName-plate-3.jpg&form-id=2&field-id=42&hash=68e586c8d7b660c033aa360aefe8d5a08dc60b4cba3488811ddf720ded015c20 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FName-plate-2.jpg&form-id=2&field-id=42&hash=6d1305075050c52c60d36ebc50409af73f15841eb32554acc897ce84c9b8c592 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FName-plate-1.jpg&form-id=2&field-id=42&hash=16c775a80f3255e6ee51101bff22cae3759e036064753b6be512cba909799454 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | David Escalante
2025-12-05 10:07 | Jeffrey | Hobson | E31770 | 620 Marshall St |  | Holliston | MA | 1746 | United States | 5088896200 | Electrician | jphobsonelectric@gmail.com | L1412180470 | Breaker |  | 50 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG_3550.jpeg&form-id=2&field-id=22&hash=1cfc3db8e273585cc879a91ffbdd76dcf23e73ae24e2268eb21be9bd6a504792 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG_0774.jpeg&form-id=2&field-id=22&hash=b98091be5b29b0c920148fb61f8a6f4b817ecadff2dbceecf573064ffcf981bc | 2025-12-01 | 2025-12-01 | 41 Bonwood |  | Needham | MA | 2492 | United States | Thermador Electric stove is tripping a Siemns 50 Amp GFI breaker in panel | Thermador | PR130LBHU | None | Single family residence | Kitchen | Yes | No | Yes | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FFILE_7477.pdf&form-id=2&field-id=42&hash=8369d80c7af0383623b1d8cd82653174412d1d4046b59fcfcaa3d278fa55f4ed , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG_3025.jpeg&form-id=2&field-id=42&hash=f35d257e692e659aea188d2db465f459f8fbef95aea94b527b8e51e92f2f9b37 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG_3082.jpeg&form-id=2&field-id=42&hash=b3cbe89aa0a54910ddba29fd034f83a80e11d0d1860ca8c4f5384c3b091c5bc1 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG_6086.jpeg&form-id=2&field-id=42&hash=db508d4278a8c98c8121231e16e52fa4b6d2645384f86295ce17fbd2d2a6ea50 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Jeffrey P Hobson
2025-12-05 10:51 | Brian | Ball | 22164A | 7 Story Acres |  | Essex | Massachusetts | 1929 | United States | 978-767-0885 | Homeowner | brianball80@yahoo.com | Siemens | Breaker |  | 30 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2F1AADD71F-DF80-48F7-81BE-348A3ACCA039.jpeg&form-id=2&field-id=22&hash=5b9527318c10f0a288717090d40da1cc50c8e472cbe16f5158f651796950d5ed | 2025-04-15 | 2025-04-01 | 7 Story Acres Rd. |  | Essex | Massachusetts | 1929 | United States | Breaker trips several moments after oven is turned on | GE range, Cafe' series | C2S950P3M1D1 | none | Apartment | Kitchen | No | Yes | Yes | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FD6B714CF-0239-40E2-A30F-DAB31B5802DE_1_201_a.jpeg&form-id=2&field-id=42&hash=b5ade135d5b80a97806041c0c0e1c25491b204c43f2fe0662547935d17100ecd | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Brian Ball
2025-12-05 13:19 | Mark | Raposo | 20105 | 20 Charles Joseph Drive |  | Dartmouth | MA | 2747 | United States | 5089859555 | Master electrician | tiffanyraposo@gmail.com | QF240A | Breaker |  | 40 |  | 2 Poles | Siemens | Residence |  | 2025-11-26 | 2025-11-26 | 550 Liberty Street | Unit 102 | Braintree | MA | 2184 | United States | GFCI breaker would trip once the oven pre-heated to 100 Fahrenheit. Once standard 2p 40amp breaker was installed oven reached temps over 100 degrees Fahrenheit and held temperature. | GE | JTD3000SN2SS |  | KITCHEN | GE Wall oven in kitchen. | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | MARK RAPOSO
2025-12-05 21:19 | Andrew | Harland | 21030A | Harland Electric | PO Box 94 | Littleton, MA | MASSACHUSETTS | 1460 | United States | 9784868154 | President | andy@harlandelectric.com | BRN250GF | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-11-22 | 2025-11-21 | 25 Bulkeley Rd |  | Littleton | MASSACHUSETTS | 1460 | United States | Installed new 50A GFCI protected circuit and 4 wire range receptacle in kitchen area. Customer plugged in existing stove (approx. 3 years old). GFCI breaker tripped when oven was in preheating mode. GFCI breaker was removed, range worked as it should, GFCI was reinstalled and tripped during preheating. Appliance cord connections and receptacle connections checked, no issues found. Removed GFCI breaker and installed standard 2p 50A breaker. | Frigidaire | FCFE3062ASA |  | Single family w/ in-law apt. | Kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2F25-Bulkley.jpg&form-id=2&field-id=42&hash=a6b059220c53d51c4485d561a6718c90d89a75c1dafa9fb4f8f8ec1635cbef41 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Andrew Harland
2025-12-07 02:00 | Mark | Roussel | 8868A1 | 33 old forge Ln |  | Sudbury | MA | 1776 | United States | 9784438888 | electrician owner | Baseball78@verizon.net | SquareD | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2Fking-phillip-UL-tag.jpg&form-id=2&field-id=22&hash=d84bbd5fb361df9f14504664610f1da800ec84f4fbd5a8bc6a16b020f8ae3507 | 2025-12-06 | 2025-12-06 |  | 68 King Phillip Rd Sudbury MA | sudbury | MA | 1776 | United States | At initial installation the installed breaker immediately trips | LG | LSIL6336XE/00 | nothing | residential | kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2Fking-phillip-UL-tag1.jpg&form-id=2&field-id=42&hash=50efe35f8f9f1830fbe7b10426ccb7f83340c674aded455ce8709c3164ad2896 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Mark Roussel
2025-12-08 10:05 | James K | Kane Jr | 38193 | 31 Symonds st #11 | Unit 11 | Salem | MA | O1970 | United States | 7819533858 | Electrician | kaneelectriclynn@gmail.com | L2402020616 | Breaker |  | 50 |  | 2 Poles | ABB | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2F17652018836348942553596920859399.jpg&form-id=2&field-id=22&hash=31d3c2624a72ff16b210c48444e775a0911f83e91f2dfcc8f1310de0b997caa2 | 2025-11-27 | 2024-11-01 |  | 655 lowel st |  | Peabody | MA | United States | Home owner complained of occasional tripping. Now gfci trips upon connection. Checked connections, ok. Appliance guy checked appliance and said everything is ok. They recommended removal of gfci. | Kitchenaid | KFED500ESS |  | Single family home | Electric range in kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2F17652062606768297683759586047372.jpg&form-id=2&field-id=42&hash=d7c57361ca4eafc1a2da2633dbd1708e0ba7214c7f8799454c499a9850467914 , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2F17652062264522693363947200853564.jpg&form-id=2&field-id=42&hash=71701e70cda5a9aee92b183728c88de24db8d999446b9e39ace8076280b31f3d | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | James K Kane Jr
2025-12-08 17:24 | Timothy | Kent | 23633A | 220 Foster rd |  | Tewksbury | Massachusetts | 1876 | United States | 978 604 2857 | Electrical Supervisor | tkent@netrinc.com | BRN50GF | Breaker |  | 50 |  | 2 Poles | Eaton | Residence |  | 2025-12-02 | 2025-11-20 | 25 Keans Rd |  | Burlington | Massachusetts | 1803 | United States | We installed a new Stove line as part of a service upgrade and the GFCI breaker for the stove kept tripping. We tested all of the connections at the stove and at the breaker itself. we even replace the breaker and still the breaker would trip upon heating of the stove. | General Electric | JBP66W0H1WW |  | Single family home | Kitchen Stove | No | Yes | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Timothy Kent
2025-12-10 12:38 | Tyler | Daniels | 1971 | 895 Salem Street 2A |  | Groveland | MA | 1834 | United States | 9783731393 | Electrician | office@danielsel.com | Siemens | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-10-03 | 2025-11-05 | 52 Brook St Unit 9 |  | Haverhill | MA | 1832 | United States | Trips while stove is heating | GE | JB256DM2BB |  | Apartment | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Tyler Daniels
2025-12-11 12:45 | Anthony | Triolo | 54913-B | 29 Howland Trail |  | Hanson | MA | 2341 | United States | 5088136244 | Electrical Contractor | atrioloelectric@gmail.com | AD-910 | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence |  | 2025-12-11 | 2024-10-24 | [6 empty] | Stove breaker trips when using oven only | Electrolux | GCRE3060BFC |  | Kitchen | Stove in kitchen | No | No | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG_4381.jpeg&form-id=2&field-id=42&hash=aca20643d1e3cae8849578220ff5add89bba402125b7c8b0beb8d7e57166367b , https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG_4382.jpeg&form-id=2&field-id=42&hash=a827be1b82b57a76b2584ae0fed80e0671da959cfcb511c075cd78f595d84a9b | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Anthony Triolo
2025-12-11 15:56 | Anthony | Triolo | 54913-B | 10 Hayford Trail |  | Hanson | Massachusetts | 2341 | United States | 5088136244 | Electrical Contractor | atrioloelectric@gmail.com | AD-910 | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-12-11 | 2025-12-11 | [6 empty] | Trips immediately. | Electrolux | FCRE3062ABC |  | Duplex | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Anthony Triolo
2025-12-12 13:02 | Ryan | Donohue | 6?2?0?5?7 | 14 Jennings Pond Rd |  | Natick | Ma | 1760 | United States | 5085057522 | Journeyman Electrician on site | rydons88@gmail.com | Eaton GFTCB230 | Breaker |  | 30 |  | 2 Poles | Eaton | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2Ftripping-GFCI.png&form-id=2&field-id=22&hash=bd3282e612902520d9edaf4997f60135d5e78f4bb80233d88dc464d832692f80 | 2025-12-12 | 2021-09-03 | [6 empty] | Breaker has been tripping frequently since the original installation. I tested the amperage while running the dryer and everything was fine. it didn't go over 20 amps on either pole. Then I got the company (Eaton) to send me a new breaker and they did. However the issue still persists. | LG | MFL70442676 | nothing | House | It's only the dryer, in a dedicated laundry space in her house | Yes | No | No | Yes | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2Fgfci-trippp.png&form-id=2&field-id=42&hash=5a69ba06d8146d2f7bafdb2ee7bb71a0b642267c9ccda7fa4d76f28f6ddc83be | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Ryan Donohue
2025-12-15 07:05 | seth | Anderholm | 60028-B | 141 bragg hill road |  | Westminster | Massachusetts | 1473 | United States | 9786025291 | Electrician | anderholmseth@gmail.com | HOM250GFICP | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-10-22 | 2025-10-22 | 5 rydal st |  | worcester | Massachusetts | 1602 | United States | updated range wiring to be properly sized for demand factor from the panel to the range. then installed the required 50amp gfci breaker. i tested the range for about 5 minutes to make sure all burners turn on and oven operates in all functions. then after running the bake mode past 15 minutes it trips with no know fault of the range. 4 wire install, ground and neutral are not bonded on the casing of the range. everytime the range runs past 10-15 minutes it trips and the oven is unable to be used. cooktop works fine. and previously there was no gfci protection until the 2023 code required such. (Images would not upload "Error: illegal_extension, Message: Sorry, this file extension is not permitted for security reasons.") | kitchenaid | KFEG500ESS3 | none | single family | kitchen range only | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Seth Anderholm
2025-12-16 14:07 | Scott | McLoud | 33374E | 419 Summer st | n/a | East Bridgewater | MA | 2333 | United States | 6179300708 | manager | scott.mcloud@callkuhlman.com | Square D Homeline | Breaker |  | 50 |  | 2 Poles | Schneider Electric | Residence |  | 2025-06-04 | 2025-06-02 | 30 Davenport Rd | n/a | Plymouth | MA | 2360 | United States | GFCI Breaker tripping during preheat cycle | GE | GRF500 |  | single family | Kitchen | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Scott McLoud
2025-12-16 14:14 | scott | mcloud | 33374E | 419 Summer st | n/a | East Bridgewater | MA | 2333 | United States | 6179300708 | manager | scott.mcloud@callkuhlman.com | Square D Homeline | Breaker |  | 30 |  | 2 Poles | Schneider Electric | Residence |  | 2025-06-04 | 2025-06-03 | 30 Davenport Rd | n/a | Plymouth | MA | 2360 | United States | Tripping Breaker for dryer | samsung | DVE47CG |  | single family | Electric dryer in basement | No | No | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | Scott McLoud
2025-12-16 15:10 | Motti Electric | CO | 8424A | 471 Page St. #2A |  | Stoughton | MA | 2072 | United States | 781-344-8950 | Electrician | avi@mottielectric.com | HOM240GFCI | Breaker |  | 40 |  | 2 Poles | Schneider Electric | Residence |  | 2025-12-08 | 2025-08-20 | 1079 Commonwealth Ave #449 |  | Boston | MA | 2111 | United States | Trips upon using oven. | GE | GRS500PV1SS |  | Apartment | Kitchen range | Yes | No | Yes | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | M Pupkin
2025-12-16 22:12 | Willians | Alvarado | 55823B | 132 walpole st |  | NORWOOD | MA | 2062 | United States | 8572499062 | electrician | williansal10.wa@gmail.com | M2510270362 | Breaker |  | 50 |  | 2 Poles | Siemens | Residence | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG-20251215-WA0028.jpg&form-id=2&field-id=22&hash=1bda978ed81b0fbd20695516c3a55780658e8822cb5ac27ca568981f13845074 | 2025-12-15 | 2025-12-15 | 8 arlington ter |  | malden | MA | 2148 | United States | electric vehicle charger not compatible, is built in gfci, and tripped as soon turn on. | Solar Edge | SJ3722-063003758-F5 |  | SINGLE FAMILY HOUSE. | EV CHARGER ON DRIVEWAY. | No | Yes | No | No | https://forms.mass.gov/eopss-dfs/index.php?gf-download=2025%2F12%2FIMG-20251215-WA0031.jpg&form-id=2&field-id=42&hash=336195e2685e2fdc4a5e1ae17080c8a04c16fd184c6bb120fbe612d479765be9 | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | willians alvarado
2025-12-16 22:13 | Willians | Alvarado | 55823B | 132 walpole st |  | NORWOOD | MA | 2062 | United States | 8572499062 | electrician | williansal10.wa@gmail.com | M2510270362 | Breaker |  | 50 |  | 2 Poles | Siemens | Residence |  | 2025-12-15 | 2025-12-15 | 8 arlington ter |  | malden | MA | 2148 | United States | electric vehicle charger not compatible, is built in gfci, and tripped as soon turn on. | Solar Edge | SJ3722-063003758-F5 |  | SINGLE FAMILY HOUSE. | EV CHARGER ON DRIVEWAY. | No | Yes | No | No |  | Checked |  | I hereby affirm that I have notified the inspector of wires as required in 527 CMR 12.00, Rule 11 and acknowledge that my review included, but was not limited to, field cord connections and equipment grounding return paths. Further, I hereby affirm that all information provided on this form is true and accurate to the best of my knowledge and is submitted under the pains and penalties of perjury. | willians alvarado