## Overall Takeaways
Grid Modernization Advisory Council ESMP Review Aggregated Recommendations
Feedback Pertaining to Review Meeting #1: September 14, 2023 (Sections 3, 4, and 5). Submitted September 22, 2023
These recommendations are submitted in accordance with current GMAC process, reserving the right to add, amend, or withdraw recommendations based on further review and other developments, including but not limited to GMAC review and meetings and other members’ recommendations.
3 - Stakeholder Engagement | Editorial guidelines | Definitions of equity and discrimination must be revisited and incorporated throughout the plan(s). | The general consensus was that the ESMPs should include more specific definitions of equity, as well as quantifiable metrics and a detailed explanation of the stakeholder engagement process (timeline, stakeholder groups, potential trainings, desired outcomes). Several members identified inconsistencies on the definitions of equity, inequity, and discrimination.
3 - Stakeholder Engagement | Environmental justice community outreach | Establish a robust accountability and decision-making system with specifics on definitions and processes.
3 - Stakeholder Engagement | Equity | Create a quantifiable set of equity metrics and definitions.
3 - Stakeholder Engagement | Misc. | Include demographic information on the customer base.
3 - Stakeholder Engagement | Stakeholder engagement | Create working group for stakeholder / community engagement Establish a system to collect customer feedback Create a timeline for eductional efforts with the community Compensation for CESAG members
4 - Current State of the DS | Alignment with state goals | Connect plans to the Commonwealth's goals | Members generally noted that the ESMPs were lacking in data tables and graphics in a couple places (as well as proper data sourcing). Multiple members pointed out a couple missing topics from the ESMPs: data and metrics on power quality, new metrics for EJCs and for electrification growth reporting, benefits of smart inverter controls, and estimates for peak demand reduction. Members also wanted the EDCs to explicitly connect their content to the Commonwealth's goals and suggest more technical / policy solutions.
4 - Current State of the DS | Battery energy storage systems | Discuss benefits of smart inverter controls
4 - Current State of the DS | Demand response
4 - Current State of the DS | Distributed energy resources | Suggest more technical / policy solutions Include estimates for peak demand reduction
4 - Current State of the DS | Dx systems
4 - Current State of the DS | Editorial guidelines | Add a summary table with data sources
4 - Current State of the DS | Electric vehicle charging | Consider creating a map with existing utility-supported charging infrastructure
4 - Current State of the DS | Electrification | Create new metrics for EJC as well as electrification growth reporting
4 - Current State of the DS | Energy storage systems
4 - Current State of the DS | Forecasting
4 - Current State of the DS | Grid capacity
4 - Current State of the DS | Infrastructure
4 - Current State of the DS | Misc. | The ESMPs should provide data and metrics on power quality
4 - Current State of the DS | Resilience
4 - Current State of the DS | Stakeholder engagement
4 - Current State of the DS | Transformer ratings
5 - 5-and 10-year demand forecast | Alignment with state goals |  | There was general consensus that the EDCs should be more transparent in how different factors (such as policies, mass transit, climate change impacts, EV charging infrastructure, etc.) were factored into the demand forecasts. Many members also wanted documentation of the assumptions made in the models and their uncertainties, and requested that this information be provided in detail from all companies (preferably with a copy of the model itself). Several members pointed out inconsistencies across the three ESMPs, both in methodology/content and in formatting. This was particularly notable in the lack of citations in some of the ESMPs. Members also agreed that there is not much forecasting of BESS growth or sensitivity analysis incorporated into this section, and the EDCs should provide more detail there. A point of disagreement was how heat pump demand was forecasted; some members felt that the demand was overestimated and others felt that the demand estimate was too conservative.
5 - 5-and 10-year demand forecast | Battery energy storage systems | There is not much forecasting of BESS growth incorporated in this section; the EDCs should provide more detail
5 - 5-and 10-year demand forecast | Demand response
5 - 5-and 10-year demand forecast | Distributed energy resources
5 - 5-and 10-year demand forecast | Dx systems
5 - 5-and 10-year demand forecast | Editorial guidelines | There are inconsistencies across the three ESMPs -- they should have a consistent methodology and should all cite their data sources
5 - 5-and 10-year demand forecast | Electric vehicle charging
5 - 5-and 10-year demand forecast | Electrification
5 - 5-and 10-year demand forecast | Energy storage systems
5 - 5-and 10-year demand forecast | Forecasting | Several members commented that EDCs should provide sensitivity analyses and specificatin of uncertainty levels in their demand forecasts Members also generally wanted more transparency in how different factors like policies, mass transit, climate change impacts, EV charging infrastructure, etc. were factored into the demand forecasts. Many members also wanted documentation of the assumptions made in the model, the uncertainties it has, and requested that this information be provided in detail from all companies (preferably with a copy of the model itself). A point of disagreement was the heat pump forecasting, some members felt it was overestimated and some felt the goals were too conservative
5 - 5-and 10-year demand forecast | Grid capacity
5 - 5-and 10-year demand forecast | Infrastructure
5 - 5-and 10-year demand forecast | Misc.
5 - 5-and 10-year demand forecast | Stakeholder engagement

## Cleaned Data
Grid Modernization Advisory Council ESMP Review Aggregated Recommendations
Feedback Pertaining to Review Meeting #1: September 14, 2023 (Sections 3, 4, and 5). Submitted September 22, 2023
These recommendations are submitted in accordance with current GMAC process, reserving the right to add, amend, or withdraw recommendations based on further review and other developments, including but not limited to GMAC review and meetings and other members’ recommendations.
EDC ESMP | Section | Subsection | Page Number | Area of Concern | Issue Area | Guiding Question | Recommendation or Question | Additional Comment | GMAC Member | Date Added | Additional Information Attachments
Unitil | 2 - Compliance with 2022 Climate Law | 2 | 22 | Stakeholdering | Stakeholder engagement |  | What is the purpose and audience for the Technical conference in November? |  | Sarah Bresolin Silver
Eversource | 3 - Stakeholder Engagement | 3.1 | 35 | Stakeholder Engagement | Editorial guidelines | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | To ensure true equity, Eversource and all the ESMPs must relook at their definitons of equity. | There is a definition of equity provided, which all EDC ESMPs should address directly in their plans. Howveer the provided definition in the Eversource plan does not address issues of equity in terms of the acknowledgment of the issues that have histrorically created a disproporation and negative inpact on certain communities, nor does the defiition address a need to balance decisionmaking power and resources toward a reality where communities are impacting wholly by their own decsions and working with utilties on accountable outcomes. The impacts of discrimination and inequity must be addressed acknowledged first to fairly address them from the point of root causes. This includes the adoption of new policies, practices, attitudes, and cultural messages that affirm race, class, and gender justice. | Marybeth Campbell | 2023-09-24
Eversource | 3 - Stakeholder Engagement |  | 63 | EJ Customer Mapping | Environmental justice community outreach | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Each of the utilities has a differing approach to talking about which different stakeholders should be engaged. Can their be uniformity across the sub-sections (e.g. consistently outlining how certain sub-segments will be reached and mapping EJC customers across the territory)? This will make it easier to compare across plans. Eversource maps their EJC customers on page 63. |  | Kathryn Wright | 2023-09-18
All | 3 - Stakeholder Engagement | 3.6.2 |  | Community Engagement Stakeholder Advisory Group | Environmental justice community outreach | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | First, I would like to say I appreciate the spirit of designing a space to help the utilities define a framework by which they can engage communities on projects before they are proposed to the EFSB. I think this early engagement will be an improvement over the status quo. However, the group is set to meet during a time where the EJ and climate community is constrained. The group is set to meet through Q2 2024 and there are many other state working groups and process ongoing that are requiring the same stakeholders. Can the utilities collect feedback on their engagement framework in any of these other forums? |  | Kathryn Wright | 2023-09-18
| 3 - Stakeholder Engagement | 3.4 | NG - 56 Eversource - 38 Unitil - 25 | Stakeholder Outreach Metrics | Environmental justice community outreach | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Metrics related to outreach and involvement of stakeholders, including EJCs, municipal leaders, and customers, need to be established and reported on. | Each plan describes best practices, and how the EDCs think about outreach, but doesn't describe specific engagements or how feedback from the public is being incorporated. What kind of process or reporting can be set up so stakeholders know how their feedback is being incorporated? In the metrics reporting, it will be important to include EJ metrics (perhaps relating to siting considerations, location of new infrastructure, condition and age of assets in EJCs, low-income rate enrollment, etc.) | Elizabeth Mahony | 2023-09-20
National Grid | 3 - Stakeholder Engagement |  |  | Outreach | Environmental justice community outreach | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | More detail is needed on outreach and EJ overall | This is for all the companies. I think we need more specifics on outreach and EJ. For example, specific, concrete actions that the companies plan to take, hard timelines being set, consistent definitions on terms like "equity" being used across territories. A uniform approach on most things across territories would be helpful. | Kyle Murray
National Grid | 3 - Stakeholder Engagement | 3.3 | 55 | EJ Population Engagement | Environmental justice community outreach | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | National Grid's Environmental Justice Community outreach and engagement strategies rely on "trusted community partners," such as community- or faith-based organizations. Does National Grid have a plan for hiring or compensating these partners or other arrangements that are not extractive, but mutually beneficial and collaborative? |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
National Grid | 3 - Stakeholder Engagement | 3.8 | 59-61 | Stakeholder Engagement | Environmental justice community outreach | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | None of the three ESPM plans address the use or power of leveraging localized decision making or accountability processes in their community and stakeholder engaging process. The plans acknowledge the need for education, shared understanding, and output of information with acknowledgment of language and culture needs but the plans do not go far enough to have a truly equitable approach that allows for local decision making among the most impacted people- customers, EJ and LMI. The plans should be pushed deeper and further to allow for local control of decisions around the impact of transmission plans, siting, procurement sourcing of contracts, and hiring goals. The plans should establish a robust accountability system that prioritizes the interests of the most vulnerable and historically and disproportionally impacted people by listening to and directly addressing their concerns from the beginning of the planning process to the end. The CESAG groups should bee formed as shared accountability committee that is empowered to oversee decisions and hold plans accountable to equitable outcomes that are defined by the communities. |  | Marybeth Campbell | 2023-09-24
| 3 - Stakeholder Engagement | 3.5 | NG - 53 Eversource - 41 Unitil - No maps | Environmental Justice Communities Data | Environmental justice community outreach | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should improve data reporting for Environmental Justice Communities (EJCs) in EDC territories. This includes having uniform mapping across all EDCs, customer counts by type of EJC by subregion, and also SAIDI/SAIFI (or perhaps CKAIDI/CKAIFI) for EJCs versus the general territory. |  | Elizabeth Mahony | 2023-09-20
Unitil | 3 - Stakeholder Engagement | 3.1 and 3.3 | 23-24 | Customer Outreach Municipal and EJC Outreach | Environmental justice community outreach | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The Unitil plan is doesn't offer much detail on what "expanded engagement and customer education for communities impacted by infrastructure projects" means. This makes this section very difficult to evaluate. On a practical level: Is Unitil planning on hiring additional engagement staff or working with external partners? Will the utility staffed be trained in culturally competent engagement? | I have these same questions for all the utilities - this is significantly more community engagement than has been in other plans and there is a level a community trust that will need to be built with the utilities for any future relationships to be productive. | Kathryn Wright | 2023-09-18
Unitil | 3 - Stakeholder Engagement | 3.3 |  | EJ Population Engagement | Environmental justice community outreach | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Unitil should add a map of EJ service territories, document which community groups it has collaborated with in the past, and the process it plans to use to identify necessary CBOs and other stakeholders moving forward (not only limited to the two workshops). |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
National Grid | 3 - Stakeholder Engagement | 3.1 | 46 | Definitions | Equity | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Eversource's ESMP provides a set of definitions of equity and environmental justice terms, setting a framework for the discussion in the rest of section 3 and the ESMP. Should the EDCs coalesce around a common set of definitions for these terms as the ESMPs are being created? Should these definitions wait until after there is time for feedback from the EWG and/or the CESAG? |  | Alex Worsley | 2023-09-22
Eversource | 3 - Stakeholder Engagement | 3.1 | 46 |  | Equity | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Eversource's section 3.10 builds off many concepts that were introduced as best practices in the Overly Impacted, Rarely Heard report from the AGO. The other ESMPs should contain a similar section with similar commitments on parameters for community meetings. |  | Kathryn Wright | 2023-09-18
National Grid | 3 - Stakeholder Engagement | 3.1 |  | Metrics for equity | Equity | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | I would like to see some quantifiable metrics on how the proposed plan can improve equity. |  | Andy Sun
Eversource | 3 - Stakeholder Engagement | 3.1 |  | Metrics for equity | Equity | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | I would like to see some quantifiable metrics on how the proposed plan can improve equity. |  | Andy Sun
Unitil | 3 - Stakeholder Engagement |  |  | Equity Definitions | Equity | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | National Grid and Eversource have defined equity and environmental justice within their ESMPs. Unitil does not currently define these terms in the text and needs to add a definition. |  | Kathryn Wright | 2023-09-18
All | 3 - Stakeholder Engagement |  |  | Equity Definitions | Equity | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | National Grid's equity definition currently includes procedural and distributional equity. These terms are commonly used in the public sector/planning space alongside a third component, structural equity. Structural equity is currently missing from the National Grid definition. Structural equity which involves creating systems of accountability to prevent disparities from continuing. Given the level of infrastructure build-out being proposed, accountability through metrics and public/community oversight will be crucial. I believe that all the ESMPs need to explore these three aspects of equity in their explanations of how the ESMPs will advance equity. (I also would like to see National Grid complete their definition of equity in the text) |  | Kathryn Wright | 2023-09-18 | Examples of definition being used in planning context: https://www.changelabsolutions.org/sites/default/files/2020-12/ThePlannersPlaybook_FINAL_20201207.pdf; https://northamptonma.gov/936/Equity; https://www.usdn.org/uploads/cms/documents/usdn_equity_scan_sept_2014_final.pdf
Unitil | 3 - Stakeholder Engagement | 3.1 |  | Metrics for equity | Equity | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | I would like to see some quantifiable metrics on how the proposed plan can improve equity. |  | Andy Sun
National Grid | 3 - Stakeholder Engagement | 3.1 | 50 |  | Misc. | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | For uniformity, all ESMPs should include basic demographic information on their customer base similar to National Grid's. |  | Kathryn Wright | 2023-09-18
Eversource | 3 - Stakeholder Engagement | 3.8-3.10 | 45-48 | Stakeholder Engagement | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | All educational materials planned for distribution in the community should prioritize using nontechnical language and should feature culturally competent, accessible, and transparent Information. Local meetings should always allow sufficient time for direct public input or offer an opportunity for public comment to be submitted beforehand and registered into the record. Community meetings should be scheduled to accommodate impacted community members and be accessibly located- and all plans should follow what is suggested by Eversource to allow for childcare. Community meetings should include translation services, flexible times, and childcare options. Means for remote engagement that allow for public commenting and viewing of meetings should be provided. Utility funds should be set aside in a dedicated account from which impacted communities engaging in the CESAG can draw to hire experts and representation to inform their members and represent their interests in technical matters requiring expertise. This funding should be sufficient to cover communities' entire costs of participation including paid stipends to CESAG and community members being asked to take local leadership role. |  | Marybeth Campbell | 2023-09-24
All | 3 - Stakeholder Engagement |  |  | Community Engagement Stakeholder Advisory Group | Stakeholder engagement | 5.Does the ESMP section minimize or mitigate impacts on ratepayers and reduce impacts on and provide benefits to low-income ratepayers? | All ESMPs say the purpose of the group is to collect feedback on the utilities Community Engagement Framework. However, only Eversource and National Grid, mention they also want the group to establish a framework for community benefits agreements for infrastructure projects. How are the utilities defining community benefit agreements? Were the costs resulting from the agreements reflected in the ESMP budget and if so how? Will these be ratebased or from the companies directly? |  | Kathryn Wright | 2023-09-18
Eversource | 3 - Stakeholder Engagement | 3.6.2 |  | CESAG leadership | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | CESAG should have a co-lead that is not utility-based, such as DOER or community-based groups | For all companies | Kyle Murray
| 3 - Stakeholder Engagement | 3.8 |  | CESAG leadership and governance | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Creating a stakeholder group dedicated to developing a community engagement framework will be vital for the development and implementation of the ESMPs; however, the design and makeup of this group must be balanced. In order to ensure that community voices and priorities are addressed throughout the process, I would reccomend expanding the leadership of the CESAG to beyond the EDCs. I would also reccomend considering what efficiency could be gained from the newly created Equity Working Group established by the GMAC. |  | Alex Worsley | 2023-09-22
Eversource | 3 - Stakeholder Engagement | 3.3 | 37 | Figure 7 | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Figure 7 is in the text to illustrate Eversource's overall engagement approach, but the figure itself unclear. I'm not sure what "traditional" versus "non-traditional outreach" means or why the boxes are different sizes. I think it would be helpful to have a figure that shows how information will flow to and from Eversource through different engagement methods. I'm really not sure what the image is trying to say. |  | Kathryn Wright | 2023-09-18
Eversource | 3 - Stakeholder Engagement | 3.4 | 38 | Stakeholdering | Stakeholder engagement |  | Figure 8: Aren't developers customers? |  | Sarah Bresolin Silver
Eversource | 3 - Stakeholder Engagement |  |  |  | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Focus on Boston & Gateway Cities, working with local officials and front-line groups (look for those who have received support from Empower and Mass Save's community program). |  | Larry Chretien
National Grid | 3 - Stakeholder Engagement |  |  |  | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Focus on the Gateway Cities, working with local officials and front-line groups (look for those who have received support from Empower and Mass Save's community program). |  | Larry Chretien
All | 3 - Stakeholder Engagement | 3 |  |  | Stakeholder engagement | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Given the importance of DER and NWA to the future of the grid, it seems like an oversight that the DER developers and technology customers are not included as a stakeholder group that needs to be consulted. They deserve a subsection like municipal customers and EJCs. They are currently not specifically referenced in Section 3 of any ESMP. |  | Kathryn Wright | 2023-09-18
Unitil | 3 - Stakeholder Engagement | 3.4 | 24 | Stakeholdering | Stakeholder engagement |  | How technical can these sessions be if there are non-technical/EJ folks there? |  | Sarah Bresolin Silver
All | 3 - Stakeholder Engagement |  |  | Community Engagement Stakeholder Advisory Group | Stakeholder engagement |  | In other instances in Massachusetts, equity and community-focused working groups tend to have a model where the public sector and community-based organizations are part of leadership (e.g. the Equity Working Group of the EEAC, the Environmental Justice Council.) The CESAG should not be solely EDC-led and should follow the model of other groups by having a co-chair and shared leadership. As with other groups, meetings and meeting materials should be made available to the public. |  | Kathryn Wright | 2023-09-18
Eversource | 3 - Stakeholder Engagement | 3.4.1 | 39 | VOC | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | It is helpful that Eversource described the work that its Voice of the Customer team has started, but their role and capacity is unclear for the rest of the engagement work. Is this primarily a market research team or do they have capacity to do in-person, in-depth community engagement as is proposed by the plan? Who is Eversource planning to work with on its community engagement strategy? | I am not clear if Eversource has the in-house capacity to build relationships with community-based groups and design impactful engagement in EJCs. Trust has been damaged in metro Boston with the East Boston substation process. Eversource will need to dedicate resources to repairing relationships before they can start meaningful engagement. I would like to understand how all of the utilities are thinking about training or hiring staff to pursue the propsoed community engagement framrwork. | Kathryn Wright | 2023-09-18
National Grid | 3 - Stakeholder Engagement | exhibit 3 and 3.6 | 415 and 57 |  | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | National Grid has an Appendix with all the parties they spoke with to prepare their ESMP. It would be helpful if Eversource and Unitil could also publish their list so the GMAC can understand which perspectives have been incorporated into this and subsequent drafts. The section summarizing takeaways from these conversations should also be in each ESMP (section 3.6) to help readers understand the feedback the utilities received before beginning the EDC process. |  | Kathryn Wright | 2023-09-18
National Grid | 3 - Stakeholder Engagement | 3.6 | 59 | Ongoing & Newly Proposed Stakeholder WGs | Stakeholder engagement | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | National grid has made reference to leveraging existing groups such as the TSRG, ESIRG, IIRG. These existing working groups are a good venue for the EDCs to provide insight and engage with technical DER stakeholders during the development of technical programs, services, operating requirements and standards that impact Distributed Energy Resources. In order for this engagement to be meaningfuland to enhance two way collaborationb of ideas and feedback the EDC's should identify specific topics for presentation to these working groups, create stakeholder feedback opportunities in these sessions or in comment periods following, and memorialize feedback and responses. | While this was raised in the NG ESMPs the recommendation applies to all the EDCs | Kathryn Cox-Arslan | 2023-09-19
Eversource | 3 - Stakeholder Engagement | 3.6.2 |  | Compensation | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Participants in CESAG should receive compensation for their work | For all companies | Kyle Murray
All | 3 - Stakeholder Engagement |  |  | Timeline | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Please lay out engagement plans on a timeline. Engagement timelines should ideally be aligned across the three utilities. The ESMPs have content about engagement that will occur both before and after the ESMPs are reviewed by the DPU, but this often has to be inferred. As a reader, I was sometimes unclear if what was being proposed was for 2023, 2024 and beyond, or both. Based on this, it is hard to evaluate if what is being proposed is reasonable based on other the timelines of other policy and regulatory efforts (e.g. the EEAC). | In addition, it is not always clear what feedback the utilities are trying to collect at different stages of the process. I do not fully understand what the expectations are for the GMAC and the public. Also, when will the utilities begin public education efforts within their territories? | Kathryn Wright | 2023-09-18
Unitil | 3 - Stakeholder Engagement | 3.8 | 25-27 | Stakeholder Engagement | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Strong encourgae Unitil plan to expand on its approach to an equitabel framework of community engagment. This section require much more attention to detial, and greater specificity. It is greatly lacking compared to the other plans, which also don’t got far enough |  | Marybeth Campbell | 2023-09-24
Eversource | 3 - Stakeholder Engagement | 3.6.2 |  | Feedback | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The CESAG should be providing regular updates to the GMAC on progress | For all companies | Kyle Murray
| 3 - Stakeholder Engagement | 3.8 | NG - 56 Eversource - 42 (3.6.2) Unitil - 26 | Community Engagement Stakeholder Advisory Group (CESAG) | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The Community Engagment Stakeholder Advisory Group (CESAG) should be hosted within the GMAC instead of establishing a new advisory group. The DPU should also review the proposed CESAG framework before a working group is established. | Considering the number of working groups that community and EJ stakeholders are asked to participate in, could the GMAC (or GMAC EWG) provide input and revisions to a Community Engagement Framework and Community Benefits Frameworks instead of the proposed new advisory group? The GMAC could help by providing feedback and suggesting ways to incorporate it into the EDCs planning structures. Also, the EDCs write about their ongoing stakeholder engagement effortsin the ESMPs – is there a way they could use those existing touchpoints to gain feedback on the frameworks? | Elizabeth Mahony | 2023-09-20
| 3 - Stakeholder Engagement | 3.8 | NG - 60 Eversource - 43 (3.6.2) Unitil - 26 | Community Engagement Stakeholder Advisory Group (CESAG) | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should consider broadening the Community Engagement Framework mission. The scope of the framework should encompass existing activities outside of infrastructure siting. | Currently, the EDCs envision the CESAG helping create frameworks for them to apply to infrastructure projects that need to be submitted to DPU/EFSB. Could the scope be broaden to grid infrastructure more generally? Eversource in particular writes about sharing benefits and burdens, but only in the context of major projects. Could stakeholder engagement efforts around other infrastructure like EV infrastructure/make ready and others be included? | Elizabeth Mahony | 2023-09-20
Eversource | 3 - Stakeholder Engagement |  |  | Stakeholder Engagement - Procedures and Metrics | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should develop standardized procedures, including metrics, to track the impacts and outcomes of their stakeholder engagement efforts. As part of the tracking effort, the EDCs should develop standardized ways to summarize stakeholder input/feedback and the EDC's response to any such stakeholder input/feedback, including explanations regarding why feedback was or was not integrated. | The EDCs have proposed to establish a Community Engagement Stakeholder Advisory Group, which would develop a Community Engagement Framework. Regardless of the specific process, this recommendation is for standardized procedures to track EDC stakeholder engagement efforts, which should include metrics and feedback loops. | Kelly Caiazzo | 2023-09-22
National Grid | 3 - Stakeholder Engagement |  |  | Stakeholder Engagement - Procedures and Metrics | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should develop standardized procedures, including metrics, to track the impacts and outcomes of their stakeholder engagement efforts. As part of the tracking effort, the EDCs should develop standardized ways to summarize stakeholder input/feedback and the EDC's response to any such stakeholder input/feedback, including explanations regarding why feedback was or was not integrated. | The EDCs have proposed to establish a Community Engagement Stakeholder Advisory Group, which would develop a Community Engagement Framework. Regardless of the specific process, this recommendation is for standardized procedures to track EDC stakeholder engagement efforts, which should include metrics and feedback loops. | Kelly Caiazzo | 2023-09-22
Unitil | 3 - Stakeholder Engagement |  |  | Stakeholder Engagement - Procedures and Metrics | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should develop standardized procedures, including metrics, to track the impacts and outcomes of their stakeholder engagement efforts. As part of the tracking effort, the EDCs should develop standardized ways to summarize stakeholder input/feedback and the EDC's response to any such stakeholder input/feedback, including explanations regarding why feedback was or was not integrated. | The EDCs have proposed to establish a Community Engagement Stakeholder Advisory Group, which would develop a Community Engagement Framework. Regardless of the specific process, this recommendation is for standardized procedures to track EDC stakeholder engagement efforts, which should include metrics and feedback loops. | Kelly Caiazzo | 2023-09-22
| 3 - Stakeholder Engagement |  |  | Accessible Language | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should ensure that plain and accessible language is used when communicating with stakeholders. | Communication with stakeholders should not only be plain and easily understood, but also translated appropriately for communities. The National Grid ESMP has laid this aspect of stakeholder engagement out more clearly than the other EDC ESMPs. | Elizabeth Mahony | 2023-09-20
Eversource | 3 - Stakeholder Engagement | 3.6.1 | 42 | Feedback Loop | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The Eversource ESMP mentions a formalized feedback loop for fall stakeholder workshops. What will the formalized feedback loop look like for the CESAG and the community engagement that results from the ESMP projects? The fall workshops should not be the only time recommendations and the EDC responses are formally tracked and made public. | This note is relevant for all EDCs. I noticed this line in Eversource's plan but I suspect all three agreed upon it for the Fall meetings. | Kathryn Wright | 2023-09-18
All | 3 - Stakeholder Engagement |  |  | Community Engagement Stakeholder Advisory Group | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The utilities are proposing a significant work schedule with no mention of compensation for CESAG members. Compensation needs to be addressed in the next draft. It is unreasonable to expect community members to be able to participate in such a time intensive process without support. |  | Kathryn Wright | 2023-09-18
Unitil | 3 - Stakeholder Engagement | 3.4 | 24 | Stakeholder Meetings and Information Exchange | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | This section could merit a timeline for customer engagement and additional edits to increase clarity. Broad stakeholder education sessions are mentioned within the same sentence as a stakeholder group which is not clearly defined. Is this group different than the CESAG? What will Unitil and the other utilities do to prepare the public to participate in these sessions? |  | Kathryn Wright | 2023-09-18
Eversource | 3 - Stakeholder Engagement | 3.7 |  | Future Stakeholder / Community engagement process | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | This section lacks any discussion of stakeholder feedback associated with forecasting of DER and solutions or alternatives. In the 20-75 proceeding the EDCs identified and stakeholders proposed stakeholder input opportunities at several stages of the planning process. The EDCs made proposals in their Long term DG Planning analysis in Docket 20-75 and feedback was provided in the form of stakeholder comment to the analysis proposals submitted by the EDCs and in technical conference materials where this was discussed. In the DPU Order closing the investigation the Department stated: "As evidenced by the diverse comments and proposals provided by stakeholders, long-term system planning, even just for enabling distributed generation, is a complex undertaking due to diverse, complex and evolving needs of customers. The Department deeply values the multitude of perspectives and issues of stakeholders. The Department urges the Distribution Companies to consider the concerns and proposals raised throughout this proceeding as they develop their electric-sector modernization plans in order to achieve the Commonwealth’s energy and climate goals." (Order 20-75-C) Opportunities for future input and feedback should be reflected in Section 3.7 Future Stakeholder Process. | Alternatively the EDCs could refer to specific Long Term DG Planning Process proposed as an Appendix to the ESMP and could be referenced in several sections including Section 3 and Section 6 | Kathryn Cox-Arslan | 2023-09-19 | Yes, attachment(s) emailed with Excel sheet.
National Grid | 3 - Stakeholder Engagement | 3.7 | 58 | Future Stakeholder / Community engagement process | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | This section lacks any discussion of stakeholder feedback associated with forecasting of DER and solutions or alternatives. In the 20-75 proceeding the EDCs identified and stakeholders proposed stakeholder input opportunities at several stages of the planning process. The EDCs made proposals in their Long term DG Planning analysis in Docket 20-75 and feedback was provided in the form of stakeholder comment to the analysis proposals submitted by the EDCs and in technical conference materials where this was discussed. In the DPU Order closing the investigation the Department stated: "As evidenced by the diverse comments and proposals provided by stakeholders, long-term system planning, even just for enabling distributed generation, is a complex undertaking due to diverse, complex and evolving needs of customers. The Department deeply values the multitude of perspectives and issues of stakeholders. The Department urges the Distribution Companies to consider the concerns and proposals raised throughout this proceeding as they develop their electric-sector modernization plans in order to achieve the Commonwealth’s energy and climate goals." (Order 20-75-C) Opportunities for future input and feedback should be reflected in Section 3.7 Future Stakeholder Process. | This section could also refer to specific Long Term DG Planning Process proposed as an Appendix to the ESMP and could be referenced in several sections including Section 3 and Section 6 | Kathryn Cox-Arslan | 2023-09-19 | Yes, attachment(s) emailed with Excel sheet.
Unitil | 3 - Stakeholder Engagement |  |  |  | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | To set the tone for the chapter and expectations for equity and stakeholder engagement, Unitil should build out an introduction section with definitions of equity and community engagement (similar to Eversource’s approach) and any internal approach the company has to equity, include demographics (race, language, income, %residential, etc.) of its customers, reference the EDC Community Engagement Framework, and outline common points during Unitil's work where stakeholder engagement will be most relevant (e.g. siting of distribution system, etc.) Alternatively, Unitil could provide more detailed demographics within "4.1.2 Customer Demographics," though the data would be useful in both sections. |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
| 3 - Stakeholder Engagement |  |  | Direct Benefits to Communities Hosting Energy Infrastructure | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | We would like to see more description and a clear definition of the "direct benefits" that the EDCs expect the communities hosting energy infrastructure will receive. It seems that the EDCs are planning on state policy & incentives to drive electrification technologies and DERs to communities with available capacity. What actions/role do the EDCs foresee for themselves in improving interconnection outcomes and sharing information about policies or incentives? |  | Elizabeth Mahony | 2023-09-20
Eversource | 3 - Stakeholder Engagement | 3.6.1 | 42 | Stakeholdering | Stakeholder engagement |  | What does "pre-determined" mean with reference to stakeholder attendees? How will stakeholders be predetermined? |  | Sarah Bresolin Silver
National Grid | 3 - Stakeholder Engagement | 3 |  | Stakeholdering | Stakeholder engagement |  | What does "pre-determined" mean with reference to stakeholder attendees? How will stakeholders be predetermined? |  | Sarah Bresolin Silver
Unitil | 3 - Stakeholder Engagement | 3 |  | Stakeholdering | Stakeholder engagement |  | What does "pre-determined" mean with reference to stakeholder attendees? How will stakeholders be predetermined? |  | Sarah Bresolin Silver
Unitil | 3 - Stakeholder Engagement | 3 |  | Stakeholdering | Stakeholder engagement |  | What is the purpose and audience for the Technical conference in November? Recommend that the Technical Conference be open to the public but that it should specfifically be an opportunity for customers to address technical questions with EDC technical staff. |  | Sarah Bresolin Silver
Eversource | 3 - Stakeholder Engagement | 3 |  | Stakeholdering | Stakeholder engagement |  | What is the purpose and audience for the Technical conference in November? Recommend that the Technical Conference be open to the public but that it should specfifically be an opportunity for customers to address technical questions with EDC technical staff. |  | Sarah Bresolin Silver
National Grid | 3 - Stakeholder Engagement | 3.4 | 56 | Stakeholdering | Stakeholder engagement |  | What is the purpose and audience for the Technical conference in November? Recommend that the Technical Conference be open to the public but that it should specfifically be an opportunity for customers to address technical questions with EDC technical staff. |  | Sarah Bresolin Silver
Eversource | 3 - Stakeholder Engagement | 3.6.1 | 42 | Stakeholdering | Stakeholder engagement |  | Why did the EDCs not offer initial in person sessions? |  | Sarah Bresolin Silver
Unitil | 3 - Stakeholder Engagement | 3 |  | Stakeholdering | Stakeholder engagement |  | Why did the EDCs not offer initial in person sessions? |  | Sarah Bresolin Silver
National Grid | 3 - Stakeholder Engagement | 3 |  | Stakeholdering | Stakeholder engagement |  | Why did the EDCs not offer initial in person sessions? |  | Sarah Bresolin Silver
Unitil | 3 - Stakeholder Engagement | 3.1 | 23 | Stakeholdering | Stakeholder engagement |  | Will there be one CESAG that will work on all three utilities' infrastructure projects? Or will each utility have their own CESAG? |  | Sarah Bresolin Silver
| 4 - Current State of the DS |  |  | Connection to the Commonwealth's goals | Alignment with state goals | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The EDCs should tie the current state of the system to the current Commonwealth’s goals. It’s difficult to understand if the state is on track to meeting its goals based on the information provided in the chapter. |  | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS | 4.3.6 |  | Smart inverter controls | Battery energy storage systems |  | Discuss benefits of smart inverter controls as demonstrated at BESS-based microgrid in Provincetown and plans for expansion throughout Commonwealth. (Ref = 4.3.6.2) |  | Elizabeth Mahony | 2023-09-20
National Grid | 4 - Current State of the DS |  | 74 |  | Demand response |  | Please elaborate on your plants to scale existing ConnectedSolutions DR program. |  | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS | 4 | 51 | Cost of interconnecting DG | Distributed energy resources |  | Eversource (and Ngrid's) ESMP acknowledge that interconecting DER, particularly large solar plus storage systems in low load areas of the grid, requires signficant Dx system upgrades and related costs. What specific policy recommendations does Eversource have wrt solar policy (and related incentives) that would mitigate these costs? | relevant language from ESMP: "significant upgrades to the EPS must be constructed to facilitate the transmission of clean energy from where it is produced to where it is consumed" | Galen Nelson | 2023-09-13
Eversource | 4 - Current State of the DS | 4.3.5 | 91 | Solar/DER in Boston | Distributed energy resources |  | Eversource states: "because of the unique characteristics of the network circuits, the requirements for secure protection, and existing limitations for control of, and communication with network protectors and associated equipment, the hosting capacity of the network portion of the system is currently very limited for DER interconnections." It occurs to me that this deserves more detail. with regard to the "unique characteristics of the network circuits" is Eversource referring to the area network in downtown Boston/back bay? Given the substantial latent interest in installing more DERS, particularly solar, in Boston and considerable roof area, can Eversource suggest technical or policy solutions to address this challenge? |  | Galen Nelson | 2023-09-13
National Grid | 4 - Current State of the DS | 4.5.5 | 126 | NWAs vs. Substations | Distributed energy resources | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | I am using National Grid as an example, but this applies to all sections. In the section on the North Shore, National Grid describes the cost of 3 additional substations to meet the demand in the DER interconnection queue. Why is the cost of a potential NWA solution not projected or mentioned? In addition, can the utilities say for some of these constrained projects, how EE, DER and other technologies are acting to reduce load currently? I feel there is limited discussion of the contribution of renewables and DER to the current functionality of the system. |  | Kathryn Wright | 2023-09-18
Eversource | 4 - Current State of the DS |  |  | Clarification | Distributed energy resources |  | In the regional sections on DER adoption (i.e., 4.x.5), confirm peak demand reduction calculations of solar + storage is purely based off solar production, as is implied. | If so, please also include estimates for storage’s contribution to peak demand reduction. Since Eversource is using historical data to estimate solar’s contribution to peak demand reduction, a similar approach should be taken for storage. National Grid provided such estimates for they system in their ESMP (i.e., National Grid Fig. 5.3-5.5) | Elizabeth Mahony | 2023-09-20
| 4 - Current State of the DS |  |  | Scale of interconnection challenge is not accurately defined | Distributed energy resources | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The challenges around the current state of interconnection are not detailed to their full extent. The EDCs should include data on projects that have dropped out of the queue in the section on DER in Chapter 4, and the number of interconnection requests they may have received but have not gone forward due to interconnection cost or timeline. | The interconnection challenge is significant for DER and electrification needs. Many DERs are behind the queue that aren’t referenced here, and building developers and others aren’t electrifying as quickly as they might because interconnecting to the grid is a major barrier. Quantifying this problem as much as possible is important in this "Current State" section. | Elizabeth Mahony | 2023-09-20
National Grid | 4 - Current State of the DS | 4.1 | 70 | Dx system upgrade impacts on Tx system | Dx systems |  | with regard to voltage increase and related substation upgrade references on page 70, will the ESMPs include information re. Tx system upgrades necessary to enable Dx system upgrades? |  | Galen Nelson | 2023-09-21
Eversource | 4 - Current State of the DS |  |  | Summary table | Editorial guidelines |  | Eversource should make a summary table with key characteristics of each sub-region. Please refer to the National Grid ESMP Exhibit 4.4 as an example. |  | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS |  |  | Missing data | Editorial guidelines |  | Please provide breakouts of the stages of the queue in which various projects are in as National Grid gave in their ESMP (e.g., pre-study, post-ISA, study phase, pending withdraw, Fig. 4.78 is an example) |  | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS |  |  | Missing data | Editorial guidelines |  | Please provide capacity breakouts of solar and storage pieces with storage+solar projects in the queue (Ref = 4.x.5) |  | Elizabeth Mahony | 2023-09-20
| 4 - Current State of the DS |  |  | Navigating EDC Data | Editorial guidelines | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should create a list of data sources and and maintain a centralized source of them. We would like to see this provided as a table in each EDC ESMP, at minimum. The EDCs should host a single website that brings together all data. | Throughout the ESMPs, many existing systems and processes for reporting are referenced. There needs to be a centralized place where stakeholders can access the variety of available system data, from metrics reports, system studies, hosting capacity maps, and more. A starting list aggregated from reading just the Eversource ESMP Chapter 4 is below: a. Annual Reliability Report (ARR) – see page 71 - footnote 27 for link) b. Distribution System Resiliency Report (annual report – page 74) c. Service Quality Index (SQI) filing (23-SW-13) – page 75 d. Eversource 2022 Annual Report (page 80) e. Electric Franchises 2021 Report (page 83) f. Electric Tariffs and Rules (page 94) g. Long-range Plan (Pg 95- but no link to where this can be found) h. Outage website (not explicitly mentioned but ref on page 183) i. MassSave data j. EV adoption numbers and EVSE Make Ready projects completed | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS | 4.1 |  | Power quality | Editorial guidelines | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report does not mention power quality. Can the company provide data and metrics on power quality and any plan on improving power quality? |  | Andy Sun
All | 4 - Current State of the DS |  |  | EV Charging Infrastructure | Electric vehicle charging | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The utilities each provide figures on electric vehicles but to provide context and transparency, it would be helpful to map the existing utility-supported charging infrastructure to understand the current distribution across sub-regions and the Commonwealth. |  | Kathryn Wright | 2023-09-18
National Grid | 4 - Current State of the DS |  |  | EVs in reference to 4.1 | Electric vehicle charging | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? |  | NG refers to building off the current off-peak charging program. The current program is weak and we need something far more substantial in several respects to both manage load and incentivize EV adoption. | Larry Chretien
| 4 - Current State of the DS |  |  | Metrics | Electrification | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Existing metrics should be centralized in the ESMP reporting process to the greatest extent possible, and new metrics for EJC as well as electrification growth reporting should be created. Further, there should be a strategy proposed to enable reporting on heating electrification (which the EDCs note that they cannot report on because of the LDC non-overlapping territory issues). |  | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS | 4.1 | 73 | reliability criteria | Energy storage systems | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | I would like to see more economic justification for the reliability criteria that are now being used, especially in light of more storage, real time information, and a more networked distribution grid. What are the implied value of lost load that these criteria imply? How does more storage and more flexible load impact system reliability? |  | Andy Sun
Unitil | 4 - Current State of the DS |  |  |  | Energy storage systems |  | Discuss if Unitil is considering or has started a program similar to National Grid’s Active Resource Integration (ARI) pilot, which is testing flexible connections for storage. If such a program is not being contemplated, explain why. |  | Elizabeth Mahony | 2023-09-20
Unitil | 4 - Current State of the DS |  |  |  | Energy storage systems |  | Please break down queue numbers of storage projects, both standalone and paired with solar, regionally, as was done in National Grid and Eversource’s ESMPs. | Would also like to see breakouts of the stages of the queue in which various projects are in as National Grid gave in their ESMP (e.g., pre-study, post-ISA, study phase, pending withdraw, Fig. 4.78 is an example) | Elizabeth Mahony | 2023-09-20
| 4 - Current State of the DS |  |  | Storage | Energy storage systems |  | Please provide discussion that compares how the EDCs study the interconnection of storage in Massachusetts with how other utilities in states that are actively deploying storage (i.e., California, Texas, New York) are studying the interconnection of storage on their distribution systems. |  | Elizabeth Mahony | 2023-09-20
Unitil | 4 - Current State of the DS |  |  |  | Energy storage systems |  | Please provide discussion that compares how Unitil studies the interconnection of storage in Massachusetts with how other utilities in states that are actively deploying storage (i.e., California, Texas, New York) are studying the interconnection of storage on their distribution systems. |  | Elizabeth Mahony | 2023-09-20
National Grid | 4 - Current State of the DS | 4.5 |  |  | Energy storage systems |  | Please resolve discrepancy between Exhibit 4.54, which shows 5.0 MW storage adoption, and Exhibit 4.55, which shows 9.1 MW of storage adoption. |  | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS | 4.3.2.3 | 87 | Demand Forecasting | Forecasting | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | Additional detail on how customer propensity modeling was conducted and how it guides electrification adoption forecasting would be valuable. How is Eversource accounting for electrification adoption outstripping these propensity modeling forecasts? How does the demographically-driven propensity modeling integrate low and moderate income adoption given priorities from Mass Save? |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Unitil | 4 - Current State of the DS |  |  | Demand Forecasting | Forecasting | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Unitil reports the design weather for the demand forecast is based on "more than a decade of historical weather data." Does the model take into account climate change dynamics that may result in weather patterns different from historical averages? |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
National Grid | 4 - Current State of the DS |  |  |  | Grid capacity | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Daymark has done a study about the system issues on Cape Ann. Does National Grid have a response? https://towngreen2025.org/newsletters/july-2023-newsletter.. |  | Larry Chretien
National Grid | 4 - Current State of the DS | 4.1 | 92 | reliability criteria | Grid capacity | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | I would like to see more economic justification for the reliability criteria that are now being used, especially in light of more storage, real time information, and a more networked distribution grid. What are the implied value of lost load that these criteria imply? How does more storage and more flexible load impact system reliability? |  | Andy Sun
National Grid | 4 - Current State of the DS | 4.1 |  | AMI | Grid capacity | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report mentions the plan to increase deployment of AMI. However, not much details are given. More importantly, how does the company plan to use AMI with new pricing and load control options to smooth out load peaks? |  | Andy Sun
Eversource | 4 - Current State of the DS | 4.1 |  | AMI | Grid capacity | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report mentions the plan to increase deployment of AMI. However, not much details are given. More importantly, how does the company plan to use AMI with new pricing and load control options to smooth out load peaks? |  | Andy Sun
Eversource | 4 - Current State of the DS | 4.5 | ex. 151 | Lack of Transparency and Context in Current State Information | Infrastructure | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The EDCs should clearly explain their methodologies and data visualizations for the current state of the distribution system. For example, the aging infrastructure subsections lack substantiation against average life expectancies for different equipment or other conditions that the EDCs use to determine when equipment needs to be replaced. | Eversource has a complex pole evaluation methodology that is difficult to understand. Equipment outages are one of the largest sources of outages in Eversource sub-regions, but is not described qualitatively. The additional table on equipment outages is not explained to the reader. | Elizabeth Mahony | 2023-09-20
National Grid | 4 - Current State of the DS | 4.3.8 | 96 | Lack of Transparency and Context in Current State Information | Infrastructure | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The EDCs should clearly explain their methodologies and data visualizations for the current state of the distribution system. The aging infrastructure subsections lack substantiation against average life expectancies for different equipment. | National Grid presents a substation tiering method based on SAIDI/SAIFI values, but it looks like there is only one “Tier 4” on any map. | Elizabeth Mahony | 2023-09-20
All | 4 - Current State of the DS |  |  | Aging Infrastructure | Infrastructure | 5.Does the ESMP section minimize or mitigate impacts on ratepayers and reduce impacts on and provide benefits to low-income ratepayers? | Each of the ESMPs provides varying levels of detail on the age of existing distribution system assets. However, it is not clear if these are mentioned for context or if these replacement costs are going into the ESMP budget. How much of this general operating versus grid modernization related? |  | Kathryn Wright | 2023-09-18
National Grid | 4 - Current State of the DS | 4.1 | N/A | Infrastructure Siting | Infrastructure | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | National Grid does not have a stand-alone section under 4.1 to discuss the current state, processes, and challenges of Siting and Permitting (as Eversource does in Section 4.1.10.). Can National Grid elaborate on these topics, and specifically address how municipalities and residents are engaged during siting and permitting processes? |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
| 4 - Current State of the DS |  |  | Capital Investment Projects (CIPs) | Infrastructure | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The EDCs should consider other ways to increase substation capacity beyond individual CIPs. The CIPs docket process is very time and resource intensive. |  | Elizabeth Mahony | 2023-09-20
National Grid | 4 - Current State of the DS | Exhibit 4.65 | 132 | North Shore Outages | Infrastructure | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The ESMP offered explanations for outages in other sections (e.g. trees, overhead v undergroudn wires). However in the North Shore graphs, unlike other regions, trees are not the primary driver for outages. Instead its equipment. Can the utilities explain why deteroriated equipment has such a higher contribution to outages in the North Shore to the GMAC and in the text?
Unitil | 4 - Current State of the DS | 4.1.10 | 46 | Infrastructure Siting | Infrastructure | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Unitil should add a map of EJ communities with substations and other equipment to illustrate where physical infrastructure already exists (similar to National Grid) and should include additional information and context about the siting process and relevant regulatory bodies (similar to Eversource) |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Eversource | 4 - Current State of the DS | 4.1.10 | 75 | Infrastructure Siting | Infrastructure | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | While enabling utilities to be more flexible and responsive to rapidly evolving infrastructure needs is critical, given the challenges Eversource has encountered with stakeholder and public engagement with recent infrastructure siting, Eversource must clarify how it will maintain and improve upon its stakeholder engagement processes in parallel with a request for expedited review and approval for infrastructure. |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
| 4 - Current State of the DS | 4.1 | Section-Wide | Power Quality | Misc. | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | Are there current metrics that can be represented graphically or geographically related to power quality, or does this require the investments set forth in AMI? | Attached Meeting Minutes from 6.15.23 GMAC Meetingm, specifically comments made during public comment session by The Energy Consortium (TEC). | Jonathan Stout | 2023-09-14 | Yes, attachment(s) emailed with Excel sheet.
| 4 - Current State of the DS |  |  | Load density by circuit | Misc. |  | Can the EDCs include information or a map about load density in the sub-regions? |  | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS |  |  | Storage | Misc. |  | Please discuss if Eversource is considering or has started a program similar to National Grid’s Active Resource Integration (ARI) pilot, which is testing flexible connections for storage. If such a program is not being contemplated, explain why. |  | Elizabeth Mahony | 2023-09-20
National Grid | 4 - Current State of the DS |  | 74 |  | Misc. |  | Please discuss scope, goals, and timeline of Active Resource Integration (ARI) pilot for storage, what success looks like, and if successful, plans for wider deployment. |  | Elizabeth Mahony | 2023-09-20
National Grid | 4 - Current State of the DS | 4.1 |  | Power quality | Misc. | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report does not mention power quality. Can the company provide data and metrics on power quality and any plan on improving power quality? |  | Andy Sun
Unitil | 4 - Current State of the DS | 4.1 |  | Power quality | Misc. | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report does not mention power quality. Can the company provide data and metrics on power quality and any plan on improving power quality? |  | Andy Sun
Eversource | 4 - Current State of the DS | 4.5 | 155 |  | Misc. | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The section on segmentation of customers by cluster needs more explanation and detail. |  | Larry Chretien
All | 4 - Current State of the DS |  |  | Resilience and reliability | Resilience | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | Each ESMP provides slightly different reliability metrics for each of the sub-regions making apples to apples comparisons challenging. It would be helpful to see key metrics - SAIDI, SAIFI CAIDI and CAIFI for each sub-region. Please also disclose the reason for outages in a consistent categorization, if possible to help enable comparisons. Each utility should also map the locations of substations alongside projected SLR and floodplains for 2030 and 2050 to help readers better understand current vulnerability. If this information is sensitive, perhaps the utilities can provide a figure for the number of substations, feeders and other assets currently located (or planned to be located for pending projects) in a climate vulnerable area. |  | Kathryn Wright | 2023-09-18
Eversource | 4 - Current State of the DS | 4.1 |  | Planning process | Stakeholder engagement | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Can the utility provide more details on the planning process, any use of system-wide least-cost optimization? What other expansion/hardening options are considered before reaching the current plan? |  | Andy Sun
National Grid | 4 - Current State of the DS | 4.1 |  | Planning process | Stakeholder engagement | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Can the utility provide more details on the planning process, any use of system-wide least-cost optimization? What other expansion/hardening options are considered before reaching the current plan? |  | Andy Sun
Unitil | 4 - Current State of the DS | 4.1 |  | Planning process | Stakeholder engagement | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Can the utility provide more details on the planning process, any use of system-wide least-cost optimization? What other expansion/hardening options are considered before reaching the current plan? |  | Andy Sun
Eversource | 4 - Current State of the DS | 4.1.5 | 66 | transformer ratings | Transformer ratings |  | Eversource states that "substation transformer loads should not exceed 75% of the normal rating." Per MassCEC's EPRI study, the EDCs may be able to realize greater capacity from transformers and other critical Dx system components if they adhere to winter ratings, as lower ambient temperaturs allow for greater loading. How soon could such limits be adopted and what if any regulatory approval would be required? |  | Galen Nelson | 2023-09-13
| 5 - 5-and 10-year Demand Forecast |  |  | Meeting the Commonwealth's goals and targets | Alignment with state goals | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The EDCs should clearly state if and how overall state goals and targets from the Clean Energy and Climate Plan (CECP) are being met. | It is currently unclear to what extent each of the forecasts is aligning with state goals. National Grid plans do cite to CECP forecasts, but Eversource seems to cite to Roadmap data, which is outdated and has lower targets. Would like the EDCs to be clear if overall state goals and targets from the CECP are being met. | Elizabeth Mahony | 2023-09-20
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1.6 | 227 | DER Growth - Impact of BESS | Battery energy storage systems |  | Figure 99: Can Eversource segment BESS in these graphs for a better understanding of the impact of BESS? |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.2-5.7 | Section 5 Generally | Sub-regional demand forecasts - Impact of BESS | Battery energy storage systems |  | National Grid should provide specificity on the impact of BESS charging load and discharging/injection to the grid on aggregate demand either in reference to battery storage in the queue or expected to be in the queue to meet state goals? |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 | 204 | Battery impact on peak load | Battery energy storage systems | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Not much forecast of battery storage is provided in 5.1, and also for each subregion in the rest of the chapter. Can Eversource provide more details? Also, can Eversource provide comment on how the company plans to promote and control storage in their territory to help reduce peak load? |  | Andy Sun
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 204 | Battery impact on peak load | Battery energy storage systems | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Not much forecast of battery storage is provided in 5.1, and also for each subregion in the rest of the chapter. Can Ngrid provide more details? Also, can Ngrid comment on how the company plan to promote and control storage in their territory to help reduce peak load? |  | Andy Sun
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1.6 | 226 | DER Growth - Impact of BESS | Battery energy storage systems |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential and very briefly, co-sited BESS. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.2.5 | 209 | DER Growth - Impact of BESS | Battery energy storage systems |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.3.2 | 213 | DER Growth - Impact of BESS | Battery energy storage systems |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.4.5 | 218 | DER Growth - Impact of BESS | Battery energy storage systems |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.5.5 | 222 | DER Growth - Impact of BESS | Battery energy storage systems |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.6.5 | 226 | DER Growth - Impact of BESS | Battery energy storage systems |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.7.5 | 230 | DER Growth - Impact of BESS | Battery energy storage systems |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.2.6 | 237 | DER Growth - Impact of BESS | Battery energy storage systems |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.3 | 238 | DER Growth - Impact of BESS | Battery energy storage systems |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.4.6 | 249 | DER Growth - Impact of BESS | Battery energy storage systems |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.5.6 | 256 | DER Growth - Impact of BESS | Battery energy storage systems |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast |  | Section 5 Generally | BESS forecast | Battery energy storage systems |  | Section 5 generally lacks information related to ESS growth in National Grid territory, including the equivalent analysis performed for solar, EV and EE. A reader would takeaway that there will be little growth in BESS installation over the ten year forecast. |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | Section overview | 214 | Advanced forecasting | Battery energy storage systems |  | Table 34: does not segment out information related to BESS. Can Eversource be specific about BESS? |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.2 | 208-212 | DER Growth - Impact of BESS | Battery energy storage systems |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.3 | 212-216 | DER Growth - Impact of BESS | Battery energy storage systems |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.4 | 216-220 | DER Growth - Impact of BESS | Battery energy storage systems |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.5 | 220-224 | DER Growth - Impact of BESS | Battery energy storage systems |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.6 | 224-228 | DER Growth - Impact of BESS | Battery energy storage systems |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.7 | 228-232 | DER Growth - Impact of BESS | Battery energy storage systems |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 | 218 | DER Growth - Impact of BESS | Battery energy storage systems |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.2 | 231 | DER Growth - Impact of BESS | Battery energy storage systems |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.3.6 | 244 | DER Growth - Impact of BESS | Battery energy storage systems |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.4 | 245 | DER Growth - Impact of BESS | Battery energy storage systems |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.5 | 252 | DER Growth - Impact of BESS | Battery energy storage systems |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | Section overview | 208 | BESS forecasting | Battery energy storage systems |  | What downward corrections in peak load is Eversource making as a result of company-owned BESS? Please explain in the ESMP. |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 208 | BESS Assumptions | Battery energy storage systems | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | What percentage of BESS installations (existing and future) are asumed to have import "reserved capacity" during peak load hours? | Eversource States: "This means system capacity for import at the BESS site, is “reserved capacity”, meaning the Company will hold this capacity available, at all times, for the BESS operation. A BESS installation that has reserved import capacity during peak load hours will therefore show up as a step load at that reserved import capacity level in the forecast." This is a worst case scenario for determining the impact of ESS on system peaks. The EDC provides no information about how much storage they are assuming has this property | Alex Worsley | 2023-09-22
Eversource | 5 - 5-and 10-year Demand Forecast | Section overview | 208 | BESS forecasting | Battery energy storage systems |  | With reference to the statement "Customer-owned and controlled BESS, whether stand alone or co-sited, are therefor not considered to be naturally occurring NWA solutions…): will Eversource's consideration change once Eversource implements DERMS? If yes, and given that DERMS is likely to be implemented before 2030, how does this change Eversource's consideration of how customer-owned BESS can be seen as a solution instead of imposing a "significant challenge..."? What downward corrections in the forecast will Eversource see as a result of customer-owned BESS? Please explain in the ESMP. |  | Sarah Bresolin Silver
| 5 - 5-and 10-year Demand Forecast |  |  | DR and EE Assumptions | Demand response | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Each EDC forecasts Demand Response and EE differently. Should the EDC's treat these technologies the same across ESMPs? | Eversource states that it cannot rely on new customer sited and owned DR as a reliable alternative transmission because of opt-out provisions. Existing programs have proved successful in incenting customers to reduce load during peak load hours, what programatic changes makes the EDCs less confident that these programs will continue to incent performance? | Alex Worsley | 2023-09-22
| 5 - 5-and 10-year Demand Forecast |  |  |  | Demand response |  | Eversource and National Grid should include growth analysis for storage in all regional sections. |  | Elizabeth Mahony | 2023-09-20
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1.5 | 205 | Emissions | Demand response | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | To ensure achievement of the statewide GHG emissions limits, the EDC's should reduce the depdendency and promotion of C&I entities utilizing fossil-fuel burning generators as a means of Demand Response to reduce peak load. | N/A | Jonathan Stout | 2023-09-14
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 227 | DER Target | Distributed energy resources | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Eversource references the 2050 Decarbonization Roadmap as the source of policy targets for forecasts, but their projected deployment target for 2033 falls far short of what is projected in the 2050 Roadmap. The Energy Pathways to Deep Decarbonization Report of the 2050 Roadmap cites a total installed capacity of ground-mounted solar and rooftop solar combined at approximately 8,280MW in 2033 (conversion of TWh to MW and extrapolation of a 2033 target from the published 2030/2035 targets, see Table 22 in Appendix 2 of the report for original figures). If Eversource serves approximately 55% of load in Massachusetts we should expect the solar target to be closer to 4500 MW, rather than the 2,776 MW that they cite as the projected 2033 total. Ground Mount Solar and Rooftop solar installed capacity as compared to a deployment target for 2033 to meet the Commonwealth's 2050 goal should be reevaluated. Technical Report of the Massachusetts 2050 Decarbonization Roadmap Study: https://www.mass.gov/doc/energy-pathways-for-deep-decarbonization-report/download |  | Kathryn Cox-Arslan | 2023-09-19
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 196 | DER Target | Distributed energy resources | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Eversource states on page 196 that the "annual ground mounted solar deployment in Massachusetts as set out in the state level projections is applied, with adjustments in the near term for planned projects," however the state level projections are not cited so it is unclear what topline numbers they are using. As noted below, the topline numbers cited on page 227 are approximately half of what is called for in the 2050 Decarbonization Roadmap. Eversource should clarify which state level projections they are referencing, and demonstrate that they are aligned with the 2050 Roadmap. Equally important, Eversource's approach to forecasting ground mounted solar deployment is fundamentally at odds with the statutory mandate for the ESMPs to "proactively upgrade the distribution and, where applicable, transmission systems to...enable increased, timely adoption of renewable energy and distributed energy resources" (Section 53 of Chapter 179 of the Acts of 2022). Current interconnection capacity and costs are treated as an input into ground mounted solar deployment models (P196); that is, the existing grid is treated as a constraint on solar deployment, whereas the intent of the ESMP process is to determine what investments in the distribution system are needed to facilitate, rather than constrain, clean energy deployment. Instead of treating existing interconnection capacity and costs as a constraint, the ESMP should identify the areas that could host ground mounted solar development that is feasible and cost effective with respect to non-interconnection factors, and then evaluate which of those areas require additional interconnection capacity and which of those potential upgrades are most cost-effective. | This recommendation applies to all EDCs. The EDCs should have a consistent methodology. | Kathryn Cox-Arslan | 2023-09-19
| 5 - 5-and 10-year Demand Forecast | 5.2 | 210, 215, 219, 227 | DER Target | Distributed energy resources | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Most of the subregional forecasts for ground-mounted PV deployment do not reflect a smooth pace, but instead include large jumps in nameplate capacity in some years and flatlining capacity in other years. The reasons for this are not explained, nor are the ways in which the variable pace of deployment might effect the development of planning solutions. |  | Kathryn Cox-Arslan | 2023-09-19
National Grid | 5 - 5-and 10-year Demand Forecast | 5.2.5 | 210 | DER Target | Distributed energy resources | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | National Grid implies at the top of page 210 that they are only considering parcels that qualify for SMART under the existing land use criteria in developing their PV forecast. This may be overly constraining potential PV deployment, given that SMART land use criteria have changed in the past and may change again, especially in light of DOER's recently published Technical Potential of Solar Study Technical Potetnial of Solar Report: https://www.mass.gov/info-details/technical-potential-of-solar-study |  | Kathryn Cox-Arslan | 2023-09-19
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1 | 52, 61 | DER Target | Distributed energy resources | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Similar to Eversource and National Grid, Unitil states that "additional Photovoltaic (“PV”) adoption/installations has little impact on the reduction of winter or summer peak load." This ignores the fact that since 2020 the SMART program has required that all new solar, with limited exceptions, be paired with energy storage, and that these paired resources are incentivized by the Clean Peak program to export during peak hours. |  | Kathryn Cox-Arslan | 2023-09-19
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1.1 | 200-202 | DER Target | Distributed energy resources | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Similar to Eversource, National Grid states that "the shift to a later peak hour when PV has limited impact mean that DERs (excluding EV and EH) are not projected to offset the underlying growth in electricity demand in the future.” This ignores the fact that since 2020 the SMART program has required that all new solar, with limited exceptions, be paired with energy storage, and that these paired resources are incentivized by the Clean Peak program to export during peak hours. |  | Kathryn Cox-Arslan | 2023-09-19
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.4 | 55 | DER Target | Distributed energy resources | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Unitil states that "DER forecasts are established based on the five year and three year historical slope of DER capacity growth." This methodology is at odds with the statutory mandate to propose "improvements to the transmission or distribution system to facilitate achievement of the statewide greenhouse gas emissions limits under chapter 21N" - that is, the achievement of statewide greenhouse gas emissions should be the benchmark for DER adoption rates, not the historical rates of adoption before those GHG limits were established. Unitil should use National Grid's methodology and plan for its proportional share of the PV deployment forecasted in the 2050 Roadmap. |  | Kathryn Cox-Arslan | 2023-09-19
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1.5 | 204 | DER Target | Distributed energy resources | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Unlike Eversource (see comment above), National Grid's forecast for PV deployment appears to be more in alignment with the 2050 Roadmap (assuming that Exhibit 5.8 is showing forecasted PV for National Grid territory only). The EDCs should use consistent methodology for forecasting PV deployment; I recommend that Eversource adopt National Grid's methodology. |  | Kathryn Cox-Arslan | 2023-09-19
| 5 - 5-and 10-year Demand Forecast |  |  |  | Dx systems |  | Building on the question posed in row 7 above, The EDCs, particularly Eversource, repeatedly cite policy and technology adoption uncertainty as a key Dx system build out cost drivers including but not limited to: smart/controllable EVSE adoption, the location and cadence of vehicle and building electrification, solar PV incentive structures, smart/"DR ready" applicance adoption, the pace and location of larger commercial real estate development, etc. Acknowledging the EDCs exercise little control over consumer behavior and even less over policy, have the EDCs contemplated proposing policy changes that would result in lower Dx system build out costs? (e.g. solar incentives that would discourage PV development in low load areas) |  | Galen Nelson | 2023-09-21
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 187 | coordinating Dx system upgrades with electrification programs | Dx systems |  | On this: "This information now equips city planners and policy makers to drive electrification programs into these communities to maximize clean energy deployment while also aligning with the capacity of the grid in those local distribution systems. With this information, city planners and policy makers can target electrification in areas that are electrification ready." how precisely could electrification be coordinated with Dx system upgrades and related capacity increases? Do the MassSave PAs have the latitude to tailor building EE and electrification incentives to certain neighborhoods? (should they?) |  | Galen Nelson | 2023-09-13
| 5 - 5-and 10-year Demand Forecast |  |  | substation lens vs. regional lens | Dx systems |  | While I found the discussions of 5 and 10 year demand forecasts by service territory sub- region interesting, it occurs to me that feeder A serving a single family residential neighborhood on the south shore has more in common with feeder B serving a single family residential circuit in the Pioneer Valley than feeder C, serving a mixed use area, located 1 mile from feeder A. In other words, might it be helpful to characterize Dx system grid challenges - and related strategies to mitigate challenges and costs - in terms of some number of feeder/circuit typologies/load profiles, vs. applying a regional lens? |  | Galen Nelson | 2023-09-21
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1.1 | 201-202 | Graph Clarity | Editorial guidelines |  | Exhibits 5.2, 5.3, 5.4, 5.5: recommend labelling graph by spelling out resource type instead of using "ES" and "HE" for increased access to material. |  | Sarah Bresolin Silver
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.8 | 62 | Mislabeled table | Editorial guidelines |  | It seems like the 2nd base and PV titles need to be changed on Table 13 |  | Elizabeth Mahony | 2023-09-20
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.5 | 56 | EV adoption rates | Editorial guidelines |  | Please provide outputs of modeling for High Rate and Baseline Rate |  | Elizabeth Mahony | 2023-09-20
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 198 | Modeling | Editorial guidelines | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The company should consistently use the "All Options" scenario from the CECP instead of "Phased." | The company alternates between using the "All Options" scenario and the "Phased" scenario from the CECP. First, it should be noted that "All Options" comes from the state's decarbonization roadmap, not the CECP. The CECP equivalent is referred to as "High Electrificiation." The company should clarify if they mean the roadmap or the CECP. Further, the company should utilize the "All Options" scenario outlined by the roadmap instead of "Phased" because "All Options" contemplates "Under the most likely assumptions, what is the least-cost deployment of energy system technologies that achieves deep decarbonization?" | Kyle Murray
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 201 | Unclear Data | Editorial guidelines | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | There are unexplained assumptions in this chapter. National Grid show assumptions and process that led to Figures 5.3 – 5.5: storage decreasing peak load by 115 MW in 2022, increasing peak load by 9 MW in 2029, increasing peak load by 10 MW in 2030, respectively. |  | Elizabeth Mahony | 2023-09-20
Eversource | 5 - 5-and 10-year Demand Forecast |  | 214 | Unclear Data | Editorial guidelines | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | There is a lack of citations to data. For example, Eversource notes they use “adoption files that contain state-wide projections for each technology (EV, PV, heat pump, etc.) broken down by annual adoption…from trend models, or data supporting reports such as the 2050 Decarbonization Roadmap” (Page 215). Eversource should provide these projections and data sources. |  | Elizabeth Mahony | 2023-09-20
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | Unclear Data | Editorial guidelines | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | There is inconsistent information in this chapter. Eversource should provide historical data around storage’s contribution to reducing peak load, as National Grid has done in their ESMP (Fig. 5.3), as well as Eversource's projections going forward (e.g., National Grid Fig. 5.4, 5.5). For Eversource's projections, include assumptions and process to arrive at the numbers. |  | Elizabeth Mahony | 2023-09-20
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.5 | 57 | Workplace/fleet charging | Electric vehicle charging |  | Does "workplace" include fleet or fleet depot charging? |  | Elizabeth Mahony | 2023-09-20
National Grid | 5 - 5-and 10-year Demand Forecast | 5.2.6 | 210-211 | EV adoption rates | Electric vehicle charging |  | Elaborate on source(s) of adoption projection(s); include both estimated number of vehicles and relative % of vehicles that will be EVs in the service territory, for LDVs and MDVs/HDVs. Add assumptions about types of charging by use type, and correlating amount of demand for charging. |  | Elizabeth Mahony | 2023-09-20
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1.3 | 221-223 | EV adoption rates | Electric vehicle charging |  | Elaborate on source(s) of adoption projection(s); include both estimated number of vehicles and relative % of vehicles that will be EVs in the service territory, for LDVs and MDVs/HDVs; add assumptions about types of charging by use type. |  | Elizabeth Mahony | 2023-09-20
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.5 | 56-58 | EV adoption rates | Electric vehicle charging |  | Include both estimated number of vehicles and relative % of vehicles that will be EVs in the service territory, for LDVs and MDVs/HDVs, and correlating amount of demand for charging. What assumptions is the company using about number of EVs by LDV vs. MDV and HDV? |  | Elizabeth Mahony | 2023-09-20
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 | 221 | EV forecast | Electric vehicle charging | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Similar to the load forecast, the plan does not provide discussion on the uncertainty associated with EV adoption. The current plan states "by 2033, the company expects that 29.2% of light duty vehicles in the statewide market will have been replace by electric vehicles." The projections may be viewed as "aspirational" rather than likely outcome. At least, some scenarios of EV adoption levels should be given. Also, does the forecast consider the time of charge variations and potential charging programs that can shift charging impacts on peak load? |  | Andy Sun
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 |  | Bi-directional charging | Electric vehicle charging | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report does not have much discussion on bi-directional charging of EV (V2G) and its impact on future grid. Can the company provide any comment on plans to promote/pilot such efforts? |  | Andy Sun
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 |  | Bi-directional charging | Electric vehicle charging | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report does not have much discussion on bi-directional charging of EV (V2G) and its impact on future grid. Can the company provide any comment on plans to promote/pilot such efforts? |  | Andy Sun
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1 |  | Bi-directional charging | Electric vehicle charging | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report does not have much discussion on bi-directional charging of EV (V2G) and its impact on future grid. Can the company provide any comment on plans to promote/pilot such efforts? |  | Andy Sun
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.5 | 56-58 | DCFC installations | Electric vehicle charging |  | Though using the ISO-NE projections, why are there so few DCFC projected per year in the territory? (0-2) |  | Elizabeth Mahony | 2023-09-20
Eversource | 5 - 5-and 10-year Demand Forecast |  |  |  | Electric vehicle charging | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Would like further explanation of how the model is predicting EV charging behavior. |  | Larry Chretien
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 205 |  | Electric vehicle charging | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. |  | 5.1.6 talks about methodology based upon the # of EVs at various dates. What are assumptions of on-peak vs. off-peak charging? | Larry Chretien
| 5 - 5-and 10-year Demand Forecast | 5 | Section-Wide | Retirement / Electrification of CHP | Electrification | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | Have the EDC's considered the retirement / electrification of CHP Plants, predominantely driven by local climate ordinances (i.e. BERDO) that will transition from providing power to the grid to requiring power from the grid? | Attached Vicinity Electrification Whitepaper. | Jonathan Stout | 2023-09-14 | Yes, attachment(s) emailed with Excel sheet.
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.6 | 58 | Appliance Electrification | Electrification | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Unitil's ESMP references electrification of appliances (e.g. dryers, stoves etc.) in their electrification projections for residential. Eversource and National Grid's projections are focused on heating electrification. Its not clear if other appliances are included in the demand forecasts. All ESMPs should include appliance electrification in their forecast. NESCAUM would be a good resource to discuss appliance standards with to inform projections. |  | Kathryn Wright | 2023-09-18
Unitil | 5 - 5-and 10-year Demand Forecast |  |  |  | Energy storage systems |  | Provide historical data around storage’s contribution to reducing peak load, as National Grid has done in their ESMP (Fig. 5.3), as well as your projections going forward (e.g., National Grid Fig. 5.4, 5.5). For your projections, include your assumptions and process to arrive at your numbers. |  | Elizabeth Mahony | 2023-09-20
Unitil | 5 - 5-and 10-year Demand Forecast | 5 | 51 | ESS forecasting, generally | Energy storage systems |  | Section 5 generally lacks information related to ESS growth in Unitil territory, including the equivalent analysis performed for solar, EV and EE. |  | Sarah Bresolin Silver
Unitil | 5 - 5-and 10-year Demand Forecast |  |  |  | Energy storage systems |  | Specify storage assumptions in DER forecast (i.e,. Top of p. 56): How much energy storage installed to level load curve? How much storage charging during peak load? How much storage discharging during minimum load? |  | Elizabeth Mahony | 2023-09-20
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.4 | 56 | DER Growth - Impact of BESS | Energy storage systems |  | What portion of installed ESS is Unitil assuming will charge during peak load? Current tariff rates for charging during peak are prohibitively costly. It is unlikely that ESS will charge during peak. |  | Sarah Bresolin Silver
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.8 | 62 | 10-Yr Peak Load forecast - BESS impact | Energy storage systems |  | Why is Unitil only assuming a consistent 0.5 contribution from ESS each year from 2025-2023? Is this based on Unitil' s current queue? |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | Demand Forecasting | Forecasting | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Additonal sensitivity analysis is needed on differing levels of electrification and DER integration |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
| 5 - 5-and 10-year Demand Forecast |  |  | Incorporation of impacts of DERMS and other gird enabling platforms | Forecasting | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | All three EDCs speak to increasing their DERMS capabilities in Section 4, however there is no mention of how this technology or any grid optimizing technology impacts forecasted demand and load shapes in section 5. How do the EDCs account for operational enhancements in their forecasts? |  | Alex Worsley | 2023-09-22
| 5 - 5-and 10-year Demand Forecast | 5.1 |  | DER, ESS, and PV Forecasts | Forecasting | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | All three EDCs state that MA state climate goals are driving their DER Forecasts and have stated that their forecasts meet state climate goals. I would recommend that the EDCs include in their plans additional explanation for how these forecasts meet state climate goals and comparatively track through visuals the forecasts used in the ESMPs to the forecasts in the Massachusetts Decarbonization Roadmap and Clean Energy and Climate Plan |  | Alex Worsley | 2023-09-22
Eversource | 5 - 5-and 10-year Demand Forecast | Section overview | 190 | Econometric forecast BESS assumptions | Forecasting |  | Can Eversource qualitatively explain how its forecast includes BESS? For example, Eversource notes that the "forecast includes a significate penetration of electric light duty passenger vehicles." |  | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | N/A | Demand Forecasting | Forecasting | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Chapter 5 lacks a lot of detail and transparency about assumptions that were made to forecast future demand - National Grid should include at the very least a detailed guide of all assumptions and calculations and preferably, should attach the demand forecast model. |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 227 | Forecast Methodology | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Consistent with the incorrect assumption (noted above in the comment referencing page 199) that solar is not paired with storage, Eversource states on page 227 that "the incremental 1,600 MW of solar have an ever-fading impact on the peak as it shifts more and more to the evening hours, resulting in only 176 MW of deferral." As noted above, this ignores the fact that nearly all recent and forthcoming ground mounted solar participating in the SMART program will be paired with storage. | This recommendation applies to all EDCs. The EDCs should have a consistent methodology. | Kathryn Cox-Arslan | 2023-09-19
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 208 | Forecast Methodology | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Eversource identifies their methodology for adjustments to peak load forecasts for Front-of-Meter resources and makes reference to making no "downward corrections" for resources not considered utility-owned Non-Wires Alternatives. This is contrary to the Commonwealth's policy as implemented in the Clean Peak program, which incentivizes both standalone storage and storage co-located with PV to discharge during peak load hours. I request that the GMAC consultant review the demand assessment methodology and inclusion of DER and other resources is appropriately considered in the deferral or addition of distribution investments. | This recommendation applies to all EDCs. The EDCs should have a consistent methodology. | Kathryn Cox-Arslan | 2023-09-19
Eversource | 5 - 5-and 10-year Demand Forecast | Section overview | 189 | Econometric forecast adjusted for BESS | Forecasting |  | Eversource should more specifically or transparently show the adjustments made to the econometric forecast model due to BESS impacts on its distribution system. |  | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 199/200 | Forecast Methodology | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Eversource's Weather Adjusted Firm Solar Capacity Model appears to assume that none of the installed or forecasted PV is co-located with storage, and therefore significantly discounts the extent to which solar acts as a capacity resource. However, the SMART program has since 2020 required that all new solar, with limited exceptions, be paired with energy storage. Furthermore, these paired resources are incentivized by the Clean Peak program to export during peak hours. | This recommendation applies to all EDCs. The EDCs should have a consistent methodology. | Kathryn Cox-Arslan | 2023-09-19
All | 5 - 5-and 10-year Demand Forecast |  |  | Step Loads - Transit Authorities | Forecasting |  | For National Grid and Eversource who are including RTAs and the MBTA in their step loads/projections, is it possible to have more transparency on how mass transit is being treated? Are the assumptions in line with the electrification targets for these agencies or are they more conservative? |  | Kathryn Wright | 2023-09-18
Eversource | 5 - 5-and 10-year Demand Forecast | Section overview | 209 | Advanced forecasting | Forecasting |  | How is Eversource's Advanced Forecasting funding awarded in DPU 20-74 helping to provide forecasting for BESS? Will the tool be deployed to assist in elaborating on BESS impacts on forecasting prior to the finalization of the ESMP? |  | Sarah Bresolin Silver
All | 5 - 5-and 10-year Demand Forecast |  |  | Sensitivity Analysis | Forecasting | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | I found each of the ESMPs to have limited sensitivity analysis for the demand forecast. I'm not sure these forecasts are also accounting for the impact of changes to demand for electrification, energy efficiency and EVs due to the IRA. Is it possible to see a range of forecasts in the next draft? |  | Kathryn Wright | 2023-09-18
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | Modeling | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Load forecasts need to better explain forecasts. Many claims appear unsubstantiated | For all companies | Kyle Murray
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 199 | Demand Forecasting | Forecasting | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | National Grid reports the design weather for the demand forecast is based on "more than a decade of historical weather data." Does the model take into account climate change dynamics that may result in weather patterns different from historical averages? |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
| 5 - 5-and 10-year Demand Forecast | 5.1 |  | DER, ESS, and DR Forecasts | Forecasting |  | None of the ESMP's explicitly break out the year-over-year ESS forecasts from the step load forecasts included in their base load forecasts. The ESMPs should explicitly break out the components of the step load increases. |  | Alex Worsley | 2023-09-22
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 205 | EV forecast | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Similar to the load forecast, the plan does not provide discussion on the uncertainty associated with EV adoption. The current projects may be viewed as "aspirational" rather than likely outcome. At least, some scenarios of EV adoption levels should be given. Also, does the forecast consider the time of charge variations and potential charging programs that can shift charging impacts on peak load? |  | Andy Sun
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 206-207 | Heat Pump uncertainty | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Similar to the load forecast, the plan does not seem to provide discussion on the uncertainty associated with heat pump penetration. Regarding heat pump, most of the switching so far has been from customers using oil and propane for heating. Conversion from gas heating is much more challenging. If this is right, then demand forecast from heating electrification could be too high. Can Ngrid provide data on the breakdown of the heat pump conversion that has happened so far? |  | Andy Sun
National Grid | 5 - 5-and 10-year Demand Forecast |  |  | Senstivity analysis | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The companies should perform/demonstrate sensitivity analysis to show potential results from different scenarios | For all companies | Kyle Murray
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1.7 | 206 | Heat pump figures | Forecasting | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The company should adopt greater goals for heat pump adoption | This likely is more a EEAC issue than GMAC, but I have major concerns about the pace of load growth expected from heat pumps. These heat pump adoption figures do not seem like they will get us to the deep decarbonization we will need to hit our greenhouse gas requirements | Kyle Murray
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | 5-and 10-year Demand Forecast - Policy | Forecasting | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The Company should provide a summary (in, for example, table or list form) of any State, Federal, or other policies, programs, or policy plans or analyses (for example, the Company’s Energy Efficiency Plan or the Commonwealth’s All Options Scenario) that are utilized, incorporated in, or otherwise reflected in its demand forecast. The summary should identify the policy, program, or policy plan or analysis and should provide a high-level explanation of how that policy, program, or policy plan is translated into the demand forecast. | The goal of this recommendation is to provide an overview of how policy is incorporated into the Company's demand forecast. | Kelly Caiazzo | 2023-09-22
National Grid | 5 - 5-and 10-year Demand Forecast |  |  | 5-and 10-year Demand Forecast - Policy | Forecasting | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The Company should provide a summary (in, for example, table or list form) of any State, Federal, or other policies, programs, or policy plans or analyses (for example, the Company’s Energy Efficiency Plan or the Commonwealth’s All Options Scenario) that are utilized, incorporated in, or otherwise reflected in its demand forecast. The summary should identify the policy, program, or policy plan or analysis and should provide a high-level explanation of how that policy, program, or policy plan is translated into the demand forecast. | The goal of this recommendation is to provide an overview of how policy is incorporated into the Company's demand forecast. | Kelly Caiazzo | 2023-09-22
Unitil | 5 - 5-and 10-year Demand Forecast |  |  | 5-and 10-year Demand Forecast - Policy | Forecasting | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The Company should provide a summary (in, for example, table or list form) of any State, Federal, or other policies, programs, or policy plans or analyses (for example, the Company’s Energy Efficiency Plan or the Commonwealth’s All Options Scenario) that are utilized, incorporated in, or otherwise reflected in its demand forecast. The summary should identify the policy, program, or policy plan or analysis and should provide a high-level explanation of how that policy, program, or policy plan is translated into the demand forecast. | The goal of this recommendation is to provide an overview of how policy is incorporated into the Company's demand forecast. | Kelly Caiazzo | 2023-09-22
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | N/A | Demand Forecasting | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The demand growth projections do not take into account demand reduction/shifting policies and programs, including time of use rates. This leads to a vast overestimation of new capacity needed, which will unecessarily increase costs to ratepayers. National Grid should examine and include alternate scenarios of demand reduction and load shifting. |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
All | 5 - 5-and 10-year Demand Forecast |  |  | District Geothermal | Forecasting | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The DPU approved utility district geothermal pilots, but geothermal doesn't seem to be part of the demand projections for heating electrification for any of the utilities. This is an electrification solution, particularly for denser areas. Can the forecasts incorporate ground sourced heat pumps? How does this change projected revenue, ratepayer impacts and capital costs? |  | Kathryn Wright | 2023-09-18
| 5 - 5-and 10-year Demand Forecast |  |  | Forecasts | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The EDCs should include sensitivities and uncertainties in their forecasts included in Chapter 5. Currently, each subsector contributing to the forecast represents a maximum peak load in a worst case scenario. | What uncertainties are there in the different forecast elements? If this information is provided in subsequent chapters, the EDCs should be clear about that. If it's not possible to add quantitative uncertainties, qualitative descriptions of uncertainty should be added at minimum. | Elizabeth Mahony | 2023-09-20
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 199-203 | Forecast scenarios | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The forecast given in the plan does not seem to include any specification of the uncertainty level. Instead of having one forecast level, it should provide some scenarios of forecast demand, e.g. of high, medium, low level of future peak load. |  | Andy Sun
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 | 219 | Forecast scenarios | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The forecast given in the plan does not seem to include any specification of the uncertainty level. Instead of having one forecast level, it should provide some scenarios of forecast demand, e.g. of high, medium, low level of future peak load. |  | Andy Sun
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | 5-and 10-year Demand Forecast - Sensitivity Analyses | Forecasting | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The September 14 GMAC meeting summary states under Section 5: Five- to Ten-Year Demand Forecast, "This section would benefit from sensitivity analyses to factor in such variables as energy storage, heat pumps, EV adoption, technological advances, and other electrification transitions." The Company should provide sensitivity analyses (with additional detail to be developed by GMAC and the GMAC consultants) that factor in the variables such as those described, as well as additional variables (as identified by GMAC and the GMAC consultants). | Several members expressed support for the EDCs to provide sensitivity analyses for their demand forecasts. This recommendation would have the GMAC (with the GMAC consultants) provide to the EDCs a set of scenarios/ sensitivities for which the EDCs should provide results. | Kelly Caiazzo | 2023-09-22
National Grid | 5 - 5-and 10-year Demand Forecast |  |  | 5-and 10-year Demand Forecast - Sensitivity Analyses | Forecasting | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The September 14 GMAC meeting summary states under Section 5: Five- to Ten-Year Demand Forecast, "This section would benefit from sensitivity analyses to factor in such variables as energy storage, heat pumps, EV adoption, technological advances, and other electrification transitions." The Company should provide sensitivity analyses (with additional detail to be developed by GMAC and the GMAC consultants) that factor in the variables such as those described, as well as additional variables (as identified by GMAC and the GMAC consultants). | Several members expressed support for the EDCs to provide sensitivity analyses for their demand forecasts. This recommendation would have the GMAC (with the GMAC consultants) provide to the EDCs a set of scenarios/ sensitivities for which the EDCs should provide results. | Kelly Caiazzo | 2023-09-22
Unitil | 5 - 5-and 10-year Demand Forecast |  |  | 5-and 10-year Demand Forecast - Sensitivity Analyses | Forecasting | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The September 14 GMAC meeting summary states under Section 5: Five- to Ten-Year Demand Forecast, "This section would benefit from sensitivity analyses to factor in such variables as energy storage, heat pumps, EV adoption, technological advances, and other electrification transitions." The Company should provide sensitivity analyses (with additional detail to be developed by GMAC and the GMAC consultants) that factor in the variables such as those described, as well as additional variables (as identified by GMAC and the GMAC consultants). | Several members expressed support for the EDCs to provide sensitivity analyses for their demand forecasts. This recommendation would have the GMAC (with the GMAC consultants) provide to the EDCs a set of scenarios/ sensitivities for which the EDCs should provide results. | Kelly Caiazzo | 2023-09-22
Unitil | 5 - 5-and 10-year Demand Forecast |  |  | Batteries | Forecasting | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | Treating batteries solely as a source of demand seems like a conservative way of modeling them for the purposes of a demand forecast. Batteries can provide grid services and demand response now. Is there a way to model their impact on peak demand based on their participation in the Mass Save DR programs? NREL has some advanced battery models that they keep in-house. Perhaps, we can reach back out to them as the GMAC for assistance with this question. |  | Kathryn Wright
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 202, 204 | Solar PV impact on peak load | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Why is PV's impact on peak load 0 in Exhibits 5.4 and 5.5? How is it consistent with the forecast of 2000MW increase of PV solar in Exhibit 5.8? |  | Andy Sun
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 211 | Forecasting | Forecasting | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Will these forecasting models be available for analysis by outside parties? |  | Kyle Murray
Eversource | 5 - 5-and 10-year Demand Forecast |  |  |  | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? |  | I concur with Synapse, slide #59 from 9/14. • “The load forecasts include many unsubstantiated assumptions. • The EDCs do not appear to seriously consider sensitivities over the 10-year forecast period. • The EDCs could better explain dependencies between proposed investments and projected growth. In many instances, the projected load growth for given end uses would be contingent on utility actions, including, potentially, both grid investments and programmatic inducements.” | Larry Chretien
Unitil | 5 - 5-and 10-year Demand Forecast |  |  |  | Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? |  | I concur with Synapse, slide #59 from 9/14. • “The load forecasts include many unsubstantiated assumptions. • The EDCs do not appear to seriously consider sensitivities over the 10-year forecast period. • The EDCs could better explain dependencies between proposed investments and projected growth. In many instances, the projected load growth for given end uses would be contingent on utility actions, including, potentially, both grid investments and programmatic inducements.” | Larry Chretien
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 | 227-228 | Heat Pump uncertainty | Grid capacity | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Similar to the load forecast, the plan does not seem to provide discussion on the uncertainty associated with heat pump penetration. Regarding heat pump, most of the switching so far has been from customers using oil and propane for heating. Conversion from gas heating is much more challenging. If this is right, then demand forecast from heating electrification could be too high. Can the Eversource provide data on the breakdown of the heat pump conversion that has happened so far? Can Eversource provide an estimation of how likely is the All Options Scenario which predicts 3.4GW of winter peak addition of heating load by 2035? |  | Andy Sun
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 | 226-227 | Solar PV impact on peak load | Grid capacity | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The forecast of load deferral from PV is based on the assumption of large increase in space heating (20% conversion and 1.96GW on page 227). However, if heat pump adoption is slower (given the concern above for heat pump), the impact of solar PV on load deferral could be underestimated, leading to overestimation of need in upgrading infrastructure. Eversource should provide more scenarios for heat pump adoption and the associated peak load deferral from PV solar. |  | Andy Sun
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | Overarching | Infrastructure | 5.Does the ESMP section minimize or mitigate impacts on ratepayers and reduce impacts on and provide benefits to low-income ratepayers? | Absent from this section is discussion of any changes to how individual feeder-level infrastructure improvements are to be paid for. While discussion has occurred about interconnection-related infrastructure costs and cost-sharing for DERs, presently many customers in larger than single-family homes have had electrical service upgrades denied unless they cover the cost of transformer upgrades. A small 8-unit condo building cannot alone bear the cost of a $150,000 transformer upgrade! Failure to address this approach inherently creates barriers to electrification. |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1.6. | 226 | PV installed capacity | Misc. |  | Estimating only ~1.4GW of installed solar capacity in 2033, this seems low |  | Elizabeth Mahony | 2023-09-20
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1.6. | 204 | PV installed capacity | Misc. |  | Estimating only ~4GW of installed solar capacity in 2034, this seems low |  | Elizabeth Mahony | 2023-09-20
All | 5 - 5-and 10-year Demand Forecast |  |  | Revenue Assumption | Misc. | 5.Does the ESMP section minimize or mitigate impacts on ratepayers and reduce impacts on and provide benefits to low-income ratepayers? | The utilities are projecting increased demand from heating and transportation electrification. This has implications for their revenue, particularly if rates remain volumetric. What is the projected change to revenue and how will this revenue interact with the ESMP capital costs presented in the plan? |  | Kathryn Wright | 2023-09-18
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | Overarching | Misc. | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | We appreciate acknowledgement by Eversource of the tension between a broader open market push for electrification/DERs and the conventional approach to targeted sequenced planning. However, we cannot afford to miss opportunities to electrify due to lack of headroom. While select types of electrification plans and policies can be targeted and planned more locally, community-based electrification is expected to happen more organically. Historical data should not be overly relied upon. |  | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 206 |  | Misc. | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. |  | 5.1.7 refers to # of HE pursuant to CECP. How should we consider potential policy changes that might increase # of EH (i.e. gas bans, BPS, CHS)? | Larry Chretien
| 5 - 5-and 10-year Demand Forecast |  |  |  | Stakeholder engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | In future ESMPs the Grid Modernization Advisory Council should identify the scenarios, sensitivities, and policy targets underlying the analysis for the ESMP planning period. A specific step to obtain stakeholder input and Grid Modernization Advisory Council approval should be recognized in the ESMP framework going forward. This was supported by the EDCs in Docket 20-75 (see technical conference notes and EDC planning proposals) | This recommendation applies to all EDCs. | Kathryn Cox-Arslan | 2023-09-19
National Grid | 5 - 5-and 10-year Demand Forecast | [7 empty] | Larry Chretien
|  |  |  | Contingency ratings | Contingency ratings |  | Do the EDCs adhere to the same contingency ratings (N-1)? Do they differ depending on the load zone? (on page 95, Eversource states: "In high load density areas, such as the EMA-North Metro Boston Sub-Region, a higher degree of reliability is ensured by maintaining sufficient capacity such that the system can be operated without the loss of power to bulk distribution buses following the loss of the largest bulk distribution transformer at a substation – also known as N-1 Contingency Design" |  | Galen Nelson
|  |  |  | transformer ratings | Transformer ratings |  | Are assumptions re. transformer loading/ratings consistent across all EDCs? |  | Galen Nelson | 2023-09-13

## Attachments
Grid Modernization Advisory Council ESMP Review Aggregated Recommendations
Feedback Pertaining to Review Meeting #1: September 14, 2023 (Sections 3, 4, and 5). Submitted September 22, 2023
These recommendations are submitted in accordance with current GMAC process, reserving the right to add, amend, or withdraw recommendations based on further review and other developments, including but not limited to GMAC review and meetings and other members’ recommendations.
Some GMAC members supplemented their ESMP recommendations and feedback with written attachments. Please see the attached zipfile containing all submitted attachments. File names begin with the cell number they correspond to in the "Cleaned Data" tab.

## Raw Data
Grid Modernization Advisory Council ESMP Review
Instructions: |  | Review Meeting #1: September 14, 2023 (Sections 3, 4, and 5) Excel Sheet Due: September 22, 2023
Please add feedback and/or recommendations pertaining to individual sections in each row. Use the dropdown arrows within the column to select specific EDCs, sections, subsections, etc. Dropdown selections can be made in Columns A, B, C, F, G, I, and K. Row 7 serves as an example entry. Optionally, if there are additional written comments, feedback, or documents that supplement a row entry, please indicate in Column K that additional document(s) will be emailed to MA-GMAC@mass.gov along with your completed Excel sheet. Please send completed Excel sheets with recommendations on the sections corresponding to the GMAC ESMP review schedule. See the "Schedule" sheet for more information on feedback deadlines.
EDC ESMP | Section | Subsection | Page Number | Area of Concern | Guiding Question | Recommendation or Question | Additional Comment | Issue Area | GMAC Member | Date Added | Additional Information Attachments
National Grid | 3 - Stakeholder Engagement |  |  |  | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Focus on the Gateway Cities, working with local officials and front-line groups (look for those who have received support from Empower and Mass Save's community program). |  | Stakeholder engagement | Larry Chretien
National Grid | 4 - Current State of the DS |  |  |  | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Daymark has done a study about the system issues on Cape Ann. Does National Grid have a response? https://towngreen2025.org/newsletters/july-2023-newsletter.. |  | Grid capacity | Larry Chretien
National Grid | 4 - Current State of the DS |  |  | EVs in reference to 4.1 | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? |  | NG refers to building off the current off-peak charging program. The current program is weak and we need something far more substantial in several respects to both manage load and incentivize EV adoption. | Electric vehicle charging | Larry Chretien
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 205 |  | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. |  | 5.1.6 talks about methodology based upon the # of EVs at various dates. What are assumptions of on-peak vs. off-peak charging? | Electric vehicle charging | Larry Chretien
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 206 |  | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. |  | 5.1.7 refers to # of HE pursuant to CECP. How should we consider potential policy changes that might increase # of EH (i.e. gas bans, BPS, CHS)? | Misc. | Larry Chretien
National Grid | 5 - 5-and 10-year Demand Forecast | [7 empty] | Larry Chretien
Eversource | 3 - Stakeholder Engagement |  |  |  | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Focus on Boston & Gateway Cities, working with local officials and front-line groups (look for those who have received support from Empower and Mass Save's community program). |  | Stakeholder engagement | Larry Chretien
Eversource | 4 - Current State of the DS | 4.5 | 155 |  | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The section on segmentation of customers by cluster needs more explanation and detail. |  | Misc. | Larry Chretien
Eversource | 5 - 5-and 10-year Demand Forecast |  |  |  | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Would like further explanation of how the model is predicting EV charging behavior. |  | Electric vehicle charging | Larry Chretien
Eversource | 5 - 5-and 10-year Demand Forecast |  |  |  | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? |  | I concur with Synapse, slide #59 from 9/14. • “The load forecasts include many unsubstantiated assumptions. • The EDCs do not appear to seriously consider sensitivities over the 10-year forecast period. • The EDCs could better explain dependencies between proposed investments and projected growth. In many instances, the projected load growth for given end uses would be contingent on utility actions, including, potentially, both grid investments and programmatic inducements.” | Forecasting | Larry Chretien
Unitil | 5 - 5-and 10-year Demand Forecast |  |  |  | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? |  | I concur with Synapse, slide #59 from 9/14. • “The load forecasts include many unsubstantiated assumptions. • The EDCs do not appear to seriously consider sensitivities over the 10-year forecast period. • The EDCs could better explain dependencies between proposed investments and projected growth. In many instances, the projected load growth for given end uses would be contingent on utility actions, including, potentially, both grid investments and programmatic inducements.” | Forecasting | Larry Chretien
Eversource | 4 - Current State of the DS | 4 | 51 | Cost of interconnecting DG |  | Eversource (and Ngrid's) ESMP acknowledge that interconecting DER, particularly large solar plus storage systems in low load areas of the grid, requires signficant Dx system upgrades and related costs. What specific policy recommendations does Eversource have wrt solar policy (and related incentives) that would mitigate these costs? | relevant language from ESMP: "significant upgrades to the EPS must be constructed to facilitate the transmission of clean energy from where it is produced to where it is consumed" | Distributed energy resources | Galen Nelson | 2023-09-13
Eversource | 4 - Current State of the DS | 4.1.5 | 66 | transformer ratings |  | Eversource states that "substation transformer loads should not exceed 75% of the normal rating." Per MassCEC's EPRI study, the EDCs may be able to realize greater capacity from transformers and other critical Dx system components if they adhere to winter ratings, as lower ambient temperaturs allow for greater loading. How soon could such limits be adopted and what if any regulatory approval would be required? |  | Transformer ratings | Galen Nelson | 2023-09-13
|  |  |  | transformer ratings |  | Are assumptions re. transformer loading/ratings consistent across all EDCs? |  | Transformer ratings | Galen Nelson | 2023-09-13
Eversource | 4 - Current State of the DS | 4.3.5 | 91 | Solar/DER in Boston |  | Eversource states: "because of the unique characteristics of the network circuits, the requirements for secure protection, and existing limitations for control of, and communication with network protectors and associated equipment, the hosting capacity of the network portion of the system is currently very limited for DER interconnections." It occurs to me that this deserves more detail. with regard to the "unique characteristics of the network circuits" is Eversource referring to the area network in downtown Boston/back bay? Given the substantial latent interest in installing more DERS, particularly solar, in Boston and considerable roof area, can Eversource suggest technical or policy solutions to address this challenge? |  | Distributed energy resources | Galen Nelson | 2023-09-13
|  |  |  | Contingency ratings |  | Do the EDCs adhere to the same contingency ratings (N-1)? Do they differ depending on the load zone? (on page 95, Eversource states: "In high load density areas, such as the EMA-North Metro Boston Sub-Region, a higher degree of reliability is ensured by maintaining sufficient capacity such that the system can be operated without the loss of power to bulk distribution buses following the loss of the largest bulk distribution transformer at a substation – also known as N-1 Contingency Design" |  | Contingency ratings | Galen Nelson
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 187 | coordinating Dx system upgrades with electrification programs |  | On this: "This information now equips city planners and policy makers to drive electrification programs into these communities to maximize clean energy deployment while also aligning with the capacity of the grid in those local distribution systems. With this information, city planners and policy makers can target electrification in areas that are electrification ready." how precisely could electrification be coordinated with Dx system upgrades and related capacity increases? Do the MassSave PAs have the latitude to tailor building EE and electrification incentives to certain neighborhoods? (should they?) |  | Dx systems | Galen Nelson | 2023-09-13
National Grid | 4 - Current State of the DS | 4.1 | 70 | Dx system upgrade impacts on Tx system |  | with regard to voltage increase and related substation upgrade references on page 70, will the ESMPs include information re. Tx system upgrades necessary to enable Dx system upgrades? |  | Dx systems | Galen Nelson | 2023-09-21
| 5 - 5-and 10-year Demand Forecast |  |  |  |  | Building on the question posed in row 7 above, The EDCs, particularly Eversource, repeatedly cite policy and technology adoption uncertainty as a key Dx system build out cost drivers including but not limited to: smart/controllable EVSE adoption, the location and cadence of vehicle and building electrification, solar PV incentive structures, smart/"DR ready" applicance adoption, the pace and location of larger commercial real estate development, etc. Acknowledging the EDCs exercise little control over consumer behavior and even less over policy, have the EDCs contemplated proposing policy changes that would result in lower Dx system build out costs? (e.g. solar incentives that would discourage PV development in low load areas) |  | Dx systems | Galen Nelson | 2023-09-21
| 5 - 5-and 10-year Demand Forecast |  |  | substation lens vs. regional lens |  | While I found the discussions of 5 and 10 year demand forecasts by service territory sub- region interesting, it occurs to me that feeder A serving a single family residential neighborhood on the south shore has more in common with feeder B serving a single family residential circuit in the Pioneer Valley than feeder C, serving a mixed use area, located 1 mile from feeder A. In other words, might it be helpful to characterize Dx system grid challenges - and related strategies to mitigate challenges and costs - in terms of some number of feeder/circuit typologies/load profiles, vs. applying a regional lens? |  | Dx systems | Galen Nelson | 2023-09-21
Unitil | 2 - Compliance with 2022 Climate Law | 2 | 22 | Stakeholdering |  | What is the purpose and audience for the Technical conference in November? |  | Stakeholder engagement | Sarah Bresolin Silver
Eversource | 3 - Stakeholder Engagement | 3.4 | 38 | Stakeholdering |  | Figure 8: Aren't developers customers? |  | Stakeholder engagement | Sarah Bresolin Silver
Eversource | 3 - Stakeholder Engagement | 3.6.1 | 42 | Stakeholdering |  | What does "pre-determined" mean with reference to stakeholder attendees? How will stakeholders be predetermined? |  | Stakeholder engagement | Sarah Bresolin Silver
National Grid | 3 - Stakeholder Engagement | 3 |  | Stakeholdering |  | What does "pre-determined" mean with reference to stakeholder attendees? How will stakeholders be predetermined? |  | Stakeholder engagement | Sarah Bresolin Silver
Unitil | 3 - Stakeholder Engagement | 3 |  | Stakeholdering |  | What does "pre-determined" mean with reference to stakeholder attendees? How will stakeholders be predetermined? |  | Stakeholder engagement | Sarah Bresolin Silver
Eversource | 3 - Stakeholder Engagement | 3.6.1 | 42 | Stakeholdering |  | Why did the EDCs not offer initial in person sessions? |  | Stakeholder engagement | Sarah Bresolin Silver
Unitil | 3 - Stakeholder Engagement | 3 |  | Stakeholdering |  | Why did the EDCs not offer initial in person sessions? |  | Stakeholder engagement | Sarah Bresolin Silver
National Grid | 3 - Stakeholder Engagement | 3 |  | Stakeholdering |  | Why did the EDCs not offer initial in person sessions? |  | Stakeholder engagement | Sarah Bresolin Silver
Unitil | 3 - Stakeholder Engagement | 3 |  | Stakeholdering |  | What is the purpose and audience for the Technical conference in November? Recommend that the Technical Conference be open to the public but that it should specfifically be an opportunity for customers to address technical questions with EDC technical staff. |  | Stakeholder engagement | Sarah Bresolin Silver
Eversource | 3 - Stakeholder Engagement | 3 |  | Stakeholdering |  | What is the purpose and audience for the Technical conference in November? Recommend that the Technical Conference be open to the public but that it should specfifically be an opportunity for customers to address technical questions with EDC technical staff. |  | Stakeholder engagement | Sarah Bresolin Silver
National Grid | 3 - Stakeholder Engagement | 3.4 | 56 | Stakeholdering |  | What is the purpose and audience for the Technical conference in November? Recommend that the Technical Conference be open to the public but that it should specfifically be an opportunity for customers to address technical questions with EDC technical staff. |  | Stakeholder engagement | Sarah Bresolin Silver
Unitil | 3 - Stakeholder Engagement | 3.1 | 23 | Stakeholdering |  | Will there be one CESAG that will work on all three utilities' infrastructure projects? Or will each utility have their own CESAG? |  | Stakeholder engagement | Sarah Bresolin Silver
Unitil | 3 - Stakeholder Engagement | 3.4 | 24 | Stakeholdering |  | How technical can these sessions be if there are non-technical/EJ folks there? |  | Stakeholder engagement | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast |  | Section 5 Generally | BESS forecast |  | Section 5 generally lacks information related to ESS growth in National Grid territory, including the equivalent analysis performed for solar, EV and EE. A reader would takeaway that there will be little growth in BESS installation over the ten year forecast. |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1.1 | 201-202 | Graph Clarity |  | Exhibits 5.2, 5.3, 5.4, 5.5: recommend labelling graph by spelling out resource type instead of using "ES" and "HE" for increased access to material. |  | Editorial guidelines | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.2-5.7 | Section 5 Generally | Sub-regional demand forecasts - Impact of BESS |  | National Grid should provide specificity on the impact of BESS charging load and discharging/injection to the grid on aggregate demand either in reference to battery storage in the queue or expected to be in the queue to meet state goals? |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.2.5 | 209 | DER Growth - Impact of BESS |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.2 | 208-212 | DER Growth - Impact of BESS |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.3.2 | 213 | DER Growth - Impact of BESS |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.3 | 212-216 | DER Growth - Impact of BESS |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.4 | 216-220 | DER Growth - Impact of BESS |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.4.5 | 218 | DER Growth - Impact of BESS |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.5 | 220-224 | DER Growth - Impact of BESS |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.5.5 | 222 | DER Growth - Impact of BESS |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.6 | 224-228 | DER Growth - Impact of BESS |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.6.5 | 226 | DER Growth - Impact of BESS |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.7 | 228-232 | DER Growth - Impact of BESS |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.7.5 | 230 | DER Growth - Impact of BESS |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Battery energy storage systems | Sarah Bresolin Silver
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.4 | 56 | DER Growth - Impact of BESS |  | What portion of installed ESS is Unitil assuming will charge during peak load? Current tariff rates for charging during peak are prohibitively costly. It is unlikely that ESS will charge during peak. |  | Energy storage systems | Sarah Bresolin Silver
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.8 | 62 | 10-Yr Peak Load forecast - BESS impact |  | Why is Unitil only assuming a consistent 0.5 contribution from ESS each year from 2025-2023? Is this based on Unitil' s current queue? |  | Energy storage systems | Sarah Bresolin Silver
Unitil | 5 - 5-and 10-year Demand Forecast | 5 | 51 | ESS forecasting, generally |  | Section 5 generally lacks information related to ESS growth in Unitil territory, including the equivalent analysis performed for solar, EV and EE. |  | Energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | Section overview | 189 | Econometric forecast adjusted for BESS |  | Eversource should more specifically or transparently show the adjustments made to the econometric forecast model due to BESS impacts on its distribution system. |  | Forecasting | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | Section overview | 190 | Econometric forecast BESS assumptions |  | Can Eversource qualitatively explain how its forecast includes BESS? For example, Eversource notes that the "forecast includes a significate penetration of electric light duty passenger vehicles." |  | Forecasting | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | Section overview | 208 | BESS forecasting |  | With reference to the statement "Customer-owned and controlled BESS, whether stand alone or co-sited, are therefor not considered to be naturally occurring NWA solutions…): will Eversource's consideration change once Eversource implements DERMS? If yes, and given that DERMS is likely to be implemented before 2030, how does this change Eversource's consideration of how customer-owned BESS can be seen as a solution instead of imposing a "significant challenge..."? What downward corrections in the forecast will Eversource see as a result of customer-owned BESS? Please explain in the ESMP. |  | Battery energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | Section overview | 208 | BESS forecasting |  | What downward corrections in peak load is Eversource making as a result of company-owned BESS? Please explain in the ESMP. |  | Battery energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | Section overview | 209 | Advanced forecasting |  | How is Eversource's Advanced Forecasting funding awarded in DPU 20-74 helping to provide forecasting for BESS? Will the tool be deployed to assist in elaborating on BESS impacts on forecasting prior to the finalization of the ESMP? |  | Forecasting | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | Section overview | 214 | Advanced forecasting |  | Table 34: does not segment out information related to BESS. Can Eversource be specific about BESS? |  | Battery energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1.6 | 226 | DER Growth - Impact of BESS |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential and very briefly, co-sited BESS. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Battery energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1.6 | 227 | DER Growth - Impact of BESS |  | Figure 99: Can Eversource segment BESS in these graphs for a better understanding of the impact of BESS? |  | Battery energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 | 218 | DER Growth - Impact of BESS |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Battery energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.2.6 | 237 | DER Growth - Impact of BESS |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Battery energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.2 | 231 | DER Growth - Impact of BESS |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Battery energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.3 | 238 | DER Growth - Impact of BESS |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Battery energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.3.6 | 244 | DER Growth - Impact of BESS |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Battery energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.4 | 245 | DER Growth - Impact of BESS |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Battery energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.4.6 | 249 | DER Growth - Impact of BESS |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Battery energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.5 | 252 | DER Growth - Impact of BESS |  | There is no subsection dedicated to BESS adoption and impacts like there is for solar, Heat Electrification and EVs. Recommend specifically forecasting and discussing BESS opportunity. |  | Battery energy storage systems | Sarah Bresolin Silver
Eversource | 5 - 5-and 10-year Demand Forecast | 5.5.6 | 256 | DER Growth - Impact of BESS |  | Paragraph heading references "Battery Storage" and "Grid Services" but only speaks to the solar potential. What is the potential for BESS and Grid Services? Graphs depicting forecasted BESS growth would be helpful. |  | Battery energy storage systems | Sarah Bresolin Silver
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1.5 | 205 | Emissions | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | To ensure achievement of the statewide GHG emissions limits, the EDC's should reduce the depdendency and promotion of C&I entities utilizing fossil-fuel burning generators as a means of Demand Response to reduce peak load. | N/A | Demand response | Jonathan Stout | 2023-09-14 | None
| 4 - Current State of the DS | 4.1 | Section-Wide | Power Quality | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | Are there current metrics that can be represented graphically or geographically related to power quality, or does this require the investments set forth in AMI? | Attached Meeting Minutes from 6.15.23 GMAC Meetingm, specifically comments made during public comment session by The Energy Consortium (TEC). | Misc. | Jonathan Stout | 2023-09-14 | Yes, attachment(s) emailed with Excel sheet.
| 5 - 5-and 10-year Demand Forecast | 5 | Section-Wide | Retirement / Electrification of CHP | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | Have the EDC's considered the retirement / electrification of CHP Plants, predominantely driven by local climate ordinances (i.e. BERDO) that will transition from providing power to the grid to requiring power from the grid? | Attached Vicinity Electrification Whitepaper. | Electrification | Jonathan Stout | 2023-09-14 | Yes, attachment(s) emailed with Excel sheet.
| 3 - Stakeholder Engagement | 3.8 |  | CESAG leadership and governance | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Creating a stakeholder group dedicated to developing a community engagement framework will be vital for the development and implementation of the ESMPs; however, the design and makeup of this group must be balanced. In order to ensure that community voices and priorities are addressed throughout the process, I would reccomend expanding the leadership of the CESAG to beyond the EDCs. I would also reccomend considering what efficiency could be gained from the newly created Equity Working Group established by the GMAC. |  | Stakeholder engagement | Alex Worsley | 2023-09-22
National Grid | 3 - Stakeholder Engagement | 3.1 | 46 | Definitions | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Eversource's ESMP provides a set of definitions of equity and environmental justice terms, setting a framework for the discussion in the rest of section 3 and the ESMP. Should the EDCs coalesce around a common set of definitions for these terms as the ESMPs are being created? Should these definitions wait until after there is time for feedback from the EWG and/or the CESAG? |  | Equity | Alex Worsley | 2023-09-22
| 5 - 5-and 10-year Demand Forecast | 5.1 |  | DER, ESS, and DR Forecasts |  | None of the ESMP's explicitly break out the year-over-year ESS forecasts from the step load forecasts included in their base load forecasts. The ESMPs should explicitly break out the components of the step load increases. |  | Forecasting | Alex Worsley | 2023-09-22
| 5 - 5-and 10-year Demand Forecast | 5.1 |  | DER, ESS, and PV Forecasts | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | All three EDCs state that MA state climate goals are driving their DER Forecasts and have stated that their forecasts meet state climate goals. I would recommend that the EDCs include in their plans additional explanation for how these forecasts meet state climate goals and comparatively track through visuals the forecasts used in the ESMPs to the forecasts in the Massachusetts Decarbonization Roadmap and Clean Energy and Climate Plan |  | Forecasting | Alex Worsley | 2023-09-22
| 5 - 5-and 10-year Demand Forecast |  |  | Incorporation of impacts of DERMS and other gird enabling platforms | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | All three EDCs speak to increasing their DERMS capabilities in Section 4, however there is no mention of how this technology or any grid optimizing technology impacts forecasted demand and load shapes in section 5. How do the EDCs account for operational enhancements in their forecasts? |  | Forecasting | Alex Worsley | 2023-09-22
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 208 | BESS Assumptions | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | What percentage of BESS installations (existing and future) are asumed to have import "reserved capacity" during peak load hours? | Eversource States: "This means system capacity for import at the BESS site, is “reserved capacity”, meaning the Company will hold this capacity available, at all times, for the BESS operation. A BESS installation that has reserved import capacity during peak load hours will therefore show up as a step load at that reserved import capacity level in the forecast." This is a worst case scenario for determining the impact of ESS on system peaks. The EDC provides no information about how much storage they are assuming has this property | Battery energy storage systems | Alex Worsley | 2023-09-22
| 5 - 5-and 10-year Demand Forecast |  |  | DR and EE Assumptions | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Each EDC forecasts Demand Response and EE differently. Should the EDC's treat these technologies the same across ESMPs? | Eversource states that it cannot rely on new customer sited and owned DR as a reliable alternative transmission because of opt-out provisions. Existing programs have proved successful in incenting customers to reduce load during peak load hours, what programatic changes makes the EDCs less confident that these programs will continue to incent performance? | Demand response | Alex Worsley | 2023-09-22
Unitil | 3 - Stakeholder Engagement | 3.1 and 3.3 | 23-24 | Customer Outreach Municipal and EJC Outreach | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The Unitil plan is doesn't offer much detail on what "expanded engagement and customer education for communities impacted by infrastructure projects" means. This makes this section very difficult to evaluate. On a practical level: Is Unitil planning on hiring additional engagement staff or working with external partners? Will the utility staffed be trained in culturally competent engagement? | I have these same questions for all the utilities - this is significantly more community engagement than has been in other plans and there is a level a community trust that will need to be built with the utilities for any future relationships to be productive. | Environmental justice community outreach | Kathryn Wright | 2023-09-18
Unitil | 3 - Stakeholder Engagement | 3.4 | 24 | Stakeholder Meetings and Information Exchange | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | This section could merit a timeline for customer engagement and additional edits to increase clarity. Broad stakeholder education sessions are mentioned within the same sentence as a stakeholder group which is not clearly defined. Is this group different than the CESAG? What will Unitil and the other utilities do to prepare the public to participate in these sessions? |  | Stakeholder engagement | Kathryn Wright | 2023-09-18
Unitil | 3 - Stakeholder Engagement |  |  | Equity Definitions | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | National Grid and Eversource have defined equity and environmental justice within their ESMPs. Unitil does not currently define these terms in the text and needs to add a definition. |  | Equity | Kathryn Wright | 2023-09-18
All | 3 - Stakeholder Engagement |  |  | Equity Definitions | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | National Grid's equity definition currently includes procedural and distributional equity. These terms are commonly used in the public sector/planning space alongside a third component, structural equity. Structural equity is currently missing from the National Grid definition. Structural equity which involves creating systems of accountability to prevent disparities from continuing. Given the level of infrastructure build-out being proposed, accountability through metrics and public/community oversight will be crucial. I believe that all the ESMPs need to explore these three aspects of equity in their explanations of how the ESMPs will advance equity. (I also would like to see National Grid complete their definition of equity in the text) |  | Equity | Kathryn Wright | 2023-09-18 | Examples of definition being used in planning context: https://www.changelabsolutions.org/sites/default/files/2020-12/ThePlannersPlaybook_FINAL_20201207.pdf; https://northamptonma.gov/936/Equity; https://www.usdn.org/uploads/cms/documents/usdn_equity_scan_sept_2014_final.pdf
All | 3 - Stakeholder Engagement |  |  | Timeline | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Please lay out engagement plans on a timeline. Engagement timelines should ideally be aligned across the three utilities. The ESMPs have content about engagement that will occur both before and after the ESMPs are reviewed by the DPU, but this often has to be inferred. As a reader, I was sometimes unclear if what was being proposed was for 2023, 2024 and beyond, or both. Based on this, it is hard to evaluate if what is being proposed is reasonable based on other the timelines of other policy and regulatory efforts (e.g. the EEAC). | In addition, it is not always clear what feedback the utilities are trying to collect at different stages of the process. I do not fully understand what the expectations are for the GMAC and the public. Also, when will the utilities begin public education efforts within their territories? | Stakeholder engagement | Kathryn Wright | 2023-09-18
Eversource | 3 - Stakeholder Engagement | 3.3 | 37 | Figure 7 | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Figure 7 is in the text to illustrate Eversource's overall engagement approach, but the figure itself unclear. I'm not sure what "traditional" versus "non-traditional outreach" means or why the boxes are different sizes. I think it would be helpful to have a figure that shows how information will flow to and from Eversource through different engagement methods. I'm really not sure what the image is trying to say. |  | Stakeholder engagement | Kathryn Wright | 2023-09-18
Eversource | 3 - Stakeholder Engagement | 3.4.1 | 39 | VOC | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | It is helpful that Eversource described the work that its Voice of the Customer team has started, but their role and capacity is unclear for the rest of the engagement work. Is this primarily a market research team or do they have capacity to do in-person, in-depth community engagement as is proposed by the plan? Who is Eversource planning to work with on its community engagement strategy? | I am not clear if Eversource has the in-house capacity to build relationships with community-based groups and design impactful engagement in EJCs. Trust has been damaged in metro Boston with the East Boston substation process. Eversource will need to dedicate resources to repairing relationships before they can start meaningful engagement. I would like to understand how all of the utilities are thinking about training or hiring staff to pursue the propsoed community engagement framrwork. | Stakeholder engagement | Kathryn Wright | 2023-09-18
Eversource | 3 - Stakeholder Engagement |  | 63 | EJ Customer Mapping | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Each of the utilities has a differing approach to talking about which different stakeholders should be engaged. Can their be uniformity across the sub-sections (e.g. consistently outlining how certain sub-segments will be reached and mapping EJC customers across the territory)? This will make it easier to compare across plans. Eversource maps their EJC customers on page 63. |  | Environmental justice community outreach | Kathryn Wright | 2023-09-18
All | 3 - Stakeholder Engagement | 3 |  |  | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Given the importance of DER and NWA to the future of the grid, it seems like an oversight that the DER developers and technology customers are not included as a stakeholder group that needs to be consulted. They deserve a subsection like municipal customers and EJCs. They are currently not specifically referenced in Section 3 of any ESMP. |  | Stakeholder engagement | Kathryn Wright | 2023-09-18
Eversource | 3 - Stakeholder Engagement | 3.6.1 | 42 | Feedback Loop | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The Eversource ESMP mentions a formalized feedback loop for fall stakeholder workshops. What will the formalized feedback loop look like for the CESAG and the community engagement that results from the ESMP projects? The fall workshops should not be the only time recommendations and the EDC responses are formally tracked and made public. | This note is relevant for all EDCs. I noticed this line in Eversource's plan but I suspect all three agreed upon it for the Fall meetings. | Stakeholder engagement | Kathryn Wright | 2023-09-18
All | 3 - Stakeholder Engagement | 3.6.2 |  | Community Engagement Stakeholder Advisory Group | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | First, I would like to say I appreciate the spirit of designing a space to help the utilities define a framework by which they can engage communities on projects before they are proposed to the EFSB. I think this early engagement will be an improvement over the status quo. However, the group is set to meet during a time where the EJ and climate community is constrained. The group is set to meet through Q2 2024 and there are many other state working groups and process ongoing that are requiring the same stakeholders. Can the utilities collect feedback on their engagement framework in any of these other forums? |  | Environmental justice community outreach | Kathryn Wright | 2023-09-18
All | 3 - Stakeholder Engagement |  |  | Community Engagement Stakeholder Advisory Group | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The utilities are proposing a significant work schedule with no mention of compensation for CESAG members. Compensation needs to be addressed in the next draft. It is unreasonable to expect community members to be able to participate in such a time intensive process without support. |  | Stakeholder engagement | Kathryn Wright | 2023-09-18
All | 3 - Stakeholder Engagement |  |  | Community Engagement Stakeholder Advisory Group | 5.Does the ESMP section minimize or mitigate impacts on ratepayers and reduce impacts on and provide benefits to low-income ratepayers? | All ESMPs say the purpose of the group is to collect feedback on the utilities Community Engagement Framework. However, only Eversource and National Grid, mention they also want the group to establish a framework for community benefits agreements for infrastructure projects. How are the utilities defining community benefit agreements? Were the costs resulting from the agreements reflected in the ESMP budget and if so how? Will these be ratebased or from the companies directly? |  | Stakeholder engagement | Kathryn Wright | 2023-09-18
All | 3 - Stakeholder Engagement |  |  | Community Engagement Stakeholder Advisory Group |  | In other instances in Massachusetts, equity and community-focused working groups tend to have a model where the public sector and community-based organizations are part of leadership (e.g. the Equity Working Group of the EEAC, the Environmental Justice Council.) The CESAG should not be solely EDC-led and should follow the model of other groups by having a co-chair and shared leadership. As with other groups, meetings and meeting materials should be made available to the public. |  | Stakeholder engagement | Kathryn Wright | 2023-09-18
Eversource | 3 - Stakeholder Engagement | 3.1 | 46 |  | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Eversource's section 3.10 builds off many concepts that were introduced as best practices in the Overly Impacted, Rarely Heard report from the AGO. The other ESMPs should contain a similar section with similar commitments on parameters for community meetings. |  | Equity | Kathryn Wright | 2023-09-18
National Grid | 3 - Stakeholder Engagement | exhibit 3 and 3.6 | 415 and 57 |  | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | National Grid has an Appendix with all the parties they spoke with to prepare their ESMP. It would be helpful if Eversource and Unitil could also publish their list so the GMAC can understand which perspectives have been incorporated into this and subsequent drafts. The section summarizing takeaways from these conversations should also be in each ESMP (section 3.6) to help readers understand the feedback the utilities received before beginning the EDC process. |  | Stakeholder engagement | Kathryn Wright | 2023-09-18
National Grid | 3 - Stakeholder Engagement | 3.1 | 50 |  | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | For uniformity, all ESMPs should include basic demographic information on their customer base similar to National Grid's. |  | Misc. | Kathryn Wright | 2023-09-18
All | 4 - Current State of the DS |  |  | Aging Infrastructure | 5.Does the ESMP section minimize or mitigate impacts on ratepayers and reduce impacts on and provide benefits to low-income ratepayers? | Each of the ESMPs provides varying levels of detail on the age of existing distribution system assets. However, it is not clear if these are mentioned for context or if these replacement costs are going into the ESMP budget. How much of this general operating versus grid modernization related? |  | Infrastructure | Kathryn Wright | 2023-09-18
All | 4 - Current State of the DS |  |  | Resilience and reliability | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | Each ESMP provides slightly different reliability metrics for each of the sub-regions making apples to apples comparisons challenging. It would be helpful to see key metrics - SAIDI, SAIFI CAIDI and CAIFI for each sub-region. Please also disclose the reason for outages in a consistent categorization, if possible to help enable comparisons. Each utility should also map the locations of substations alongside projected SLR and floodplains for 2030 and 2050 to help readers better understand current vulnerability. If this information is sensitive, perhaps the utilities can provide a figure for the number of substations, feeders and other assets currently located (or planned to be located for pending projects) in a climate vulnerable area. |  | Resilience | Kathryn Wright | 2023-09-18
All | 4 - Current State of the DS |  |  | EV Charging Infrastructure | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The utilities each provide figures on electric vehicles but to provide context and transparency, it would be helpful to map the existing utility-supported charging infrastructure to understand the current distribution across sub-regions and the Commonwealth. |  | Electric vehicle charging | Kathryn Wright | 2023-09-18
National Grid | 4 - Current State of the DS | 4.5.5 | 126 | NWAs vs. Substations | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | I am using National Grid as an example, but this applies to all sections. In the section on the North Shore, National Grid describes the cost of 3 additional substations to meet the demand in the DER interconnection queue. Why is the cost of a potential NWA solution not projected or mentioned? In addition, can the utilities say for some of these constrained projects, how EE, DER and other technologies are acting to reduce load currently? I feel there is limited discussion of the contribution of renewables and DER to the current functionality of the system. |  | Distributed energy resources | Kathryn Wright | 2023-09-18
National Grid | 4 - Current State of the DS | Exhibit 4.65 | 132 | North Shore Outages | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The ESMP offered explanations for outages in other sections (e.g. trees, overhead v undergroudn wires). However in the North Shore graphs, unlike other regions, trees are not the primary driver for outages. Instead its equipment. Can the utilities explain why deteroriated equipment has such a higher contribution to outages in the North Shore to the GMAC and in the text? |  | Infrastructure
All | 5 - 5-and 10-year Demand Forecast |  |  | Sensitivity Analysis | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | I found each of the ESMPs to have limited sensitivity analysis for the demand forecast. I'm not sure these forecasts are also accounting for the impact of changes to demand for electrification, energy efficiency and EVs due to the IRA. Is it possible to see a range of forecasts in the next draft? |  | Forecasting | Kathryn Wright | 2023-09-18
All | 5 - 5-and 10-year Demand Forecast |  |  | Revenue Assumption | 5.Does the ESMP section minimize or mitigate impacts on ratepayers and reduce impacts on and provide benefits to low-income ratepayers? | The utilities are projecting increased demand from heating and transportation electrification. This has implications for their revenue, particularly if rates remain volumetric. What is the projected change to revenue and how will this revenue interact with the ESMP capital costs presented in the plan? |  | Misc. | Kathryn Wright | 2023-09-18
Unitil | 5 - 5-and 10-year Demand Forecast |  |  | Batteries | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | Treating batteries solely as a source of demand seems like a conservative way of modeling them for the purposes of a demand forecast. Batteries can provide grid services and demand response now. Is there a way to model their impact on peak demand based on their participation in the Mass Save DR programs? NREL has some advanced battery models that they keep in-house. Perhaps, we can reach back out to them as the GMAC for assistance with this question. |  | Forecasting | Kathryn Wright
All | 5 - 5-and 10-year Demand Forecast |  |  | District Geothermal | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The DPU approved utility district geothermal pilots, but geothermal doesn't seem to be part of the demand projections for heating electrification for any of the utilities. This is an electrification solution, particularly for denser areas. Can the forecasts incorporate ground sourced heat pumps? How does this change projected revenue, ratepayer impacts and capital costs? |  | Forecasting | Kathryn Wright | 2023-09-18
All | 5 - 5-and 10-year Demand Forecast |  |  | Step Loads - Transit Authorities |  | For National Grid and Eversource who are including RTAs and the MBTA in their step loads/projections, is it possible to have more transparency on how mass transit is being treated? Are the assumptions in line with the electrification targets for these agencies or are they more conservative? |  | Forecasting | Kathryn Wright | 2023-09-18
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.6 | 58 | Appliance Electrification | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Unitil's ESMP references electrification of appliances (e.g. dryers, stoves etc.) in their electrification projections for residential. Eversource and National Grid's projections are focused on heating electrification. Its not clear if other appliances are included in the demand forecasts. All ESMPs should include appliance electrification in their forecast. NESCAUM would be a good resource to discuss appliance standards with to inform projections. |  | Electrification | Kathryn Wright | 2023-09-18
Eversource | 3 - Stakeholder Engagement | 3.7 |  | Future Stakeholder / Community engagement process | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | This section lacks any discussion of stakeholder feedback associated with forecasting of DER and solutions or alternatives. In the 20-75 proceeding the EDCs identified and stakeholders proposed stakeholder input opportunities at several stages of the planning process. The EDCs made proposals in their Long term DG Planning analysis in Docket 20-75 and feedback was provided in the form of stakeholder comment to the analysis proposals submitted by the EDCs and in technical conference materials where this was discussed. In the DPU Order closing the investigation the Department stated: "As evidenced by the diverse comments and proposals provided by stakeholders, long-term system planning, even just for enabling distributed generation, is a complex undertaking due to diverse, complex and evolving needs of customers. The Department deeply values the multitude of perspectives and issues of stakeholders. The Department urges the Distribution Companies to consider the concerns and proposals raised throughout this proceeding as they develop their electric-sector modernization plans in order to achieve the Commonwealth’s energy and climate goals." (Order 20-75-C) Opportunities for future input and feedback should be reflected in Section 3.7 Future Stakeholder Process. | Alternatively the EDCs could refer to specific Long Term DG Planning Process proposed as an Appendix to the ESMP and could be referenced in several sections including Section 3 and Section 6 | Stakeholder engagement | Kathryn Cox-Arslan | 2023-09-19 | Yes, attachment(s) emailed with Excel sheet.
National Grid | 3 - Stakeholder Engagement | 3.7 | 58 | Future Stakeholder / Community engagement process | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | This section lacks any discussion of stakeholder feedback associated with forecasting of DER and solutions or alternatives. In the 20-75 proceeding the EDCs identified and stakeholders proposed stakeholder input opportunities at several stages of the planning process. The EDCs made proposals in their Long term DG Planning analysis in Docket 20-75 and feedback was provided in the form of stakeholder comment to the analysis proposals submitted by the EDCs and in technical conference materials where this was discussed. In the DPU Order closing the investigation the Department stated: "As evidenced by the diverse comments and proposals provided by stakeholders, long-term system planning, even just for enabling distributed generation, is a complex undertaking due to diverse, complex and evolving needs of customers. The Department deeply values the multitude of perspectives and issues of stakeholders. The Department urges the Distribution Companies to consider the concerns and proposals raised throughout this proceeding as they develop their electric-sector modernization plans in order to achieve the Commonwealth’s energy and climate goals." (Order 20-75-C) Opportunities for future input and feedback should be reflected in Section 3.7 Future Stakeholder Process. | This section could also refer to specific Long Term DG Planning Process proposed as an Appendix to the ESMP and could be referenced in several sections including Section 3 and Section 6 | Stakeholder engagement | Kathryn Cox-Arslan | 2023-09-19 | Yes, attachment(s) emailed with Excel sheet.
National Grid | 3 - Stakeholder Engagement | 3.6 | 59 | Ongoing & Newly Proposed Stakeholder WGs | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | National grid has made reference to leveraging existing groups such as the TSRG, ESIRG, IIRG. These existing working groups are a good venue for the EDCs to provide insight and engage with technical DER stakeholders during the development of technical programs, services, operating requirements and standards that impact Distributed Energy Resources. In order for this engagement to be meaningfuland to enhance two way collaborationb of ideas and feedback the EDC's should identify specific topics for presentation to these working groups, create stakeholder feedback opportunities in these sessions or in comment periods following, and memorialize feedback and responses. | While this was raised in the NG ESMPs the recommendation applies to all the EDCs | Stakeholder engagement | Kathryn Cox-Arslan | 2023-09-19
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 199/200 | Forecast Methodology | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Eversource's Weather Adjusted Firm Solar Capacity Model appears to assume that none of the installed or forecasted PV is co-located with storage, and therefore significantly discounts the extent to which solar acts as a capacity resource. However, the SMART program has since 2020 required that all new solar, with limited exceptions, be paired with energy storage. Furthermore, these paired resources are incentivized by the Clean Peak program to export during peak hours. | This recommendation applies to all EDCs. The EDCs should have a consistent methodology. | Forecasting | Kathryn Cox-Arslan | 2023-09-19
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 208 | Forecast Methodology | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Eversource identifies their methodology for adjustments to peak load forecasts for Front-of-Meter resources and makes reference to making no "downward corrections" for resources not considered utility-owned Non-Wires Alternatives. This is contrary to the Commonwealth's policy as implemented in the Clean Peak program, which incentivizes both standalone storage and storage co-located with PV to discharge during peak load hours. I request that the GMAC consultant review the demand assessment methodology and inclusion of DER and other resources is appropriately considered in the deferral or addition of distribution investments. | This recommendation applies to all EDCs. The EDCs should have a consistent methodology. | Forecasting | Kathryn Cox-Arslan | 2023-09-19
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 196 | DER Target | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Eversource states on page 196 that the "annual ground mounted solar deployment in Massachusetts as set out in the state level projections is applied, with adjustments in the near term for planned projects," however the state level projections are not cited so it is unclear what topline numbers they are using. As noted below, the topline numbers cited on page 227 are approximately half of what is called for in the 2050 Decarbonization Roadmap. Eversource should clarify which state level projections they are referencing, and demonstrate that they are aligned with the 2050 Roadmap. Equally important, Eversource's approach to forecasting ground mounted solar deployment is fundamentally at odds with the statutory mandate for the ESMPs to "proactively upgrade the distribution and, where applicable, transmission systems to...enable increased, timely adoption of renewable energy and distributed energy resources" (Section 53 of Chapter 179 of the Acts of 2022). Current interconnection capacity and costs are treated as an input into ground mounted solar deployment models (P196); that is, the existing grid is treated as a constraint on solar deployment, whereas the intent of the ESMP process is to determine what investments in the distribution system are needed to facilitate, rather than constrain, clean energy deployment. Instead of treating existing interconnection capacity and costs as a constraint, the ESMP should identify the areas that could host ground mounted solar development that is feasible and cost effective with respect to non-interconnection factors, and then evaluate which of those areas require additional interconnection capacity and which of those potential upgrades are most cost-effective. | This recommendation applies to all EDCs. The EDCs should have a consistent methodology. | Distributed energy resources | Kathryn Cox-Arslan | 2023-09-19
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 227 | Forecast Methodology | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Consistent with the incorrect assumption (noted above in the comment referencing page 199) that solar is not paired with storage, Eversource states on page 227 that "the incremental 1,600 MW of solar have an ever-fading impact on the peak as it shifts more and more to the evening hours, resulting in only 176 MW of deferral." As noted above, this ignores the fact that nearly all recent and forthcoming ground mounted solar participating in the SMART program will be paired with storage. | This recommendation applies to all EDCs. The EDCs should have a consistent methodology. | Forecasting | Kathryn Cox-Arslan | 2023-09-19
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 227 | DER Target | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Eversource references the 2050 Decarbonization Roadmap as the source of policy targets for forecasts, but their projected deployment target for 2033 falls far short of what is projected in the 2050 Roadmap. The Energy Pathways to Deep Decarbonization Report of the 2050 Roadmap cites a total installed capacity of ground-mounted solar and rooftop solar combined at approximately 8,280MW in 2033 (conversion of TWh to MW and extrapolation of a 2033 target from the published 2030/2035 targets, see Table 22 in Appendix 2 of the report for original figures). If Eversource serves approximately 55% of load in Massachusetts we should expect the solar target to be closer to 4500 MW, rather than the 2,776 MW that they cite as the projected 2033 total. Ground Mount Solar and Rooftop solar installed capacity as compared to a deployment target for 2033 to meet the Commonwealth's 2050 goal should be reevaluated. Technical Report of the Massachusetts 2050 Decarbonization Roadmap Study: https://www.mass.gov/doc/energy-pathways-for-deep-decarbonization-report/download |  | Distributed energy resources | Kathryn Cox-Arslan | 2023-09-19 | None
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1.5 | 204 | DER Target | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Unlike Eversource (see comment above), National Grid's forecast for PV deployment appears to be more in alignment with the 2050 Roadmap (assuming that Exhibit 5.8 is showing forecasted PV for National Grid territory only). The EDCs should use consistent methodology for forecasting PV deployment; I recommend that Eversource adopt National Grid's methodology. |  | Distributed energy resources | Kathryn Cox-Arslan | 2023-09-19
| 5 - 5-and 10-year Demand Forecast |  |  |  | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | In future ESMPs the Grid Modernization Advisory Council should identify the scenarios, sensitivities, and policy targets underlying the analysis for the ESMP planning period. A specific step to obtain stakeholder input and Grid Modernization Advisory Council approval should be recognized in the ESMP framework going forward. This was supported by the EDCs in Docket 20-75 (see technical conference notes and EDC planning proposals) | This recommendation applies to all EDCs. | Stakeholder engagement | Kathryn Cox-Arslan | 2023-09-19 | None
National Grid | 5 - 5-and 10-year Demand Forecast | 5.2.5 | 210 | DER Target | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | National Grid implies at the top of page 210 that they are only considering parcels that qualify for SMART under the existing land use criteria in developing their PV forecast. This may be overly constraining potential PV deployment, given that SMART land use criteria have changed in the past and may change again, especially in light of DOER's recently published Technical Potential of Solar Study Technical Potetnial of Solar Report: https://www.mass.gov/info-details/technical-potential-of-solar-study |  | Distributed energy resources | Kathryn Cox-Arslan | 2023-09-19
| 5 - 5-and 10-year Demand Forecast | 5.2 | 210, 215, 219, 227 | DER Target | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Most of the subregional forecasts for ground-mounted PV deployment do not reflect a smooth pace, but instead include large jumps in nameplate capacity in some years and flatlining capacity in other years. The reasons for this are not explained, nor are the ways in which the variable pace of deployment might effect the development of planning solutions. |  | Distributed energy resources | Kathryn Cox-Arslan | 2023-09-19
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1.1 | 200-202 | DER Target | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Similar to Eversource, National Grid states that "the shift to a later peak hour when PV has limited impact mean that DERs (excluding EV and EH) are not projected to offset the underlying growth in electricity demand in the future.” This ignores the fact that since 2020 the SMART program has required that all new solar, with limited exceptions, be paired with energy storage, and that these paired resources are incentivized by the Clean Peak program to export during peak hours. |  | Distributed energy resources | Kathryn Cox-Arslan | 2023-09-19
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1 | 52, 61 | DER Target | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Similar to Eversource and National Grid, Unitil states that "additional Photovoltaic (“PV”) adoption/installations has little impact on the reduction of winter or summer peak load." This ignores the fact that since 2020 the SMART program has required that all new solar, with limited exceptions, be paired with energy storage, and that these paired resources are incentivized by the Clean Peak program to export during peak hours. |  | Distributed energy resources | Kathryn Cox-Arslan | 2023-09-19
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.4 | 55 | DER Target | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Unitil states that "DER forecasts are established based on the five year and three year historical slope of DER capacity growth." This methodology is at odds with the statutory mandate to propose "improvements to the transmission or distribution system to facilitate achievement of the statewide greenhouse gas emissions limits under chapter 21N" - that is, the achievement of statewide greenhouse gas emissions should be the benchmark for DER adoption rates, not the historical rates of adoption before those GHG limits were established. Unitil should use National Grid's methodology and plan for its proportional share of the PV deployment forecasted in the 2050 Roadmap. |  | Distributed energy resources | Kathryn Cox-Arslan | 2023-09-19
National Grid | 3 - Stakeholder Engagement | 3.3 | 55 | EJ Population Engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | National Grid's Environmental Justice Community outreach and engagement strategies rely on "trusted community partners," such as community- or faith-based organizations. Does National Grid have a plan for hiring or compensating these partners or other arrangements that are not extractive, but mutually beneficial and collaborative? |  | Environmental justice community outreach | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
National Grid | 4 - Current State of the DS | 4.1 | N/A | Infrastructure Siting | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | National Grid does not have a stand-alone section under 4.1 to discuss the current state, processes, and challenges of Siting and Permitting (as Eversource does in Section 4.1.10.). Can National Grid elaborate on these topics, and specifically address how municipalities and residents are engaged during siting and permitting processes? |  | Infrastructure | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | N/A | Demand Forecasting | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Chapter 5 lacks a lot of detail and transparency about assumptions that were made to forecast future demand - National Grid should include at the very least a detailed guide of all assumptions and calculations and preferably, should attach the demand forecast model. |  | Forecasting | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | N/A | Demand Forecasting | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The demand growth projections do not take into account demand reduction/shifting policies and programs, including time of use rates. This leads to a vast overestimation of new capacity needed, which will unecessarily increase costs to ratepayers. National Grid should examine and include alternate scenarios of demand reduction and load shifting. |  | Forecasting | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 199 | Demand Forecasting | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | National Grid reports the design weather for the demand forecast is based on "more than a decade of historical weather data." Does the model take into account climate change dynamics that may result in weather patterns different from historical averages? |  | Forecasting | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Unitil | 3 - Stakeholder Engagement |  |  |  | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | To set the tone for the chapter and expectations for equity and stakeholder engagement, Unitil should build out an introduction section with definitions of equity and community engagement (similar to Eversource’s approach) and any internal approach the company has to equity, include demographics (race, language, income, %residential, etc.) of its customers, reference the EDC Community Engagement Framework, and outline common points during Unitil's work where stakeholder engagement will be most relevant (e.g. siting of distribution system, etc.) Alternatively, Unitil could provide more detailed demographics within "4.1.2 Customer Demographics," though the data would be useful in both sections. |  | Stakeholder engagement | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Unitil | 3 - Stakeholder Engagement | 3.3 |  | EJ Population Engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Unitil should add a map of EJ service territories, document which community groups it has collaborated with in the past, and the process it plans to use to identify necessary CBOs and other stakeholders moving forward (not only limited to the two workshops). |  | Environmental justice community outreach | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Unitil | 4 - Current State of the DS | 4.1.10 | 46 | Infrastructure Siting | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Unitil should add a map of EJ communities with substations and other equipment to illustrate where physical infrastructure already exists (similar to National Grid) and should include additional information and context about the siting process and relevant regulatory bodies (similar to Eversource) |  | Infrastructure | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Unitil | 4 - Current State of the DS |  |  | Demand Forecasting | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Unitil reports the design weather for the demand forecast is based on "more than a decade of historical weather data." Does the model take into account climate change dynamics that may result in weather patterns different from historical averages? |  | Forecasting | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Eversource | 4 - Current State of the DS | 4.1.10 | 75 | Infrastructure Siting | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | While enabling utilities to be more flexible and responsive to rapidly evolving infrastructure needs is critical, given the challenges Eversource has encountered with stakeholder and public engagement with recent infrastructure siting, Eversource must clarify how it will maintain and improve upon its stakeholder engagement processes in parallel with a request for expedited review and approval for infrastructure. |  | Infrastructure | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Eversource | 4 - Current State of the DS | 4.3.2.3 | 87 | Demand Forecasting | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-sca | Additional detail on how customer propensity modeling was conducted and how it guides electrification adoption forecasting would be valuable. How is Eversource accounting for electrification adoption outstripping these propensity modeling forecasts? How does the demographically-driven propensity modeling integrate low and moderate income adoption given priorities from Mass Save? |  | Forecasting | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | Overarching | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | We appreciate acknowledgement by Eversource of the tension between a broader open market push for electrification/DERs and the conventional approach to targeted sequenced planning. However, we cannot afford to miss opportunities to electrify due to lack of headroom. While select types of electrification plans and policies can be targeted and planned more locally, community-based electrification is expected to happen more organically. Historical data should not be overly relied upon. |  | Misc. | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | Overarching | 5.Does the ESMP section minimize or mitigate impacts on ratepayers and reduce impacts on and provide benefits to low-income ratepayers? | Absent from this section is discussion of any changes to how individual feeder-level infrastructure improvements are to be paid for. While discussion has occurred about interconnection-related infrastructure costs and cost-sharing for DERs, presently many customers in larger than single-family homes have had electrical service upgrades denied unless they cover the cost of transformer upgrades. A small 8-unit condo building cannot alone bear the cost of a $150,000 transformer upgrade! Failure to address this approach inherently creates barriers to electrification. |  | Infrastructure | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | Demand Forecasting | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Additonal sensitivity analysis is needed on differing levels of electrification and DER integration |  | Forecasting | Jeremy Koo (Designee of Julie Curti) | 2023-09-22
Eversource | 3 - Stakeholder Engagement |  |  | Stakeholder Engagement - Procedures and Metrics | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should develop standardized procedures, including metrics, to track the impacts and outcomes of their stakeholder engagement efforts. As part of the tracking effort, the EDCs should develop standardized ways to summarize stakeholder input/feedback and the EDC's response to any such stakeholder input/feedback, including explanations regarding why feedback was or was not integrated. | The EDCs have proposed to establish a Community Engagement Stakeholder Advisory Group, which would develop a Community Engagement Framework. Regardless of the specific process, this recommendation is for standardized procedures to track EDC stakeholder engagement efforts, which should include metrics and feedback loops. | Stakeholder engagement | Liz Anderson | 2023-09-22 | None
National Grid | 3 - Stakeholder Engagement |  |  | Stakeholder Engagement - Procedures and Metrics | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should develop standardized procedures, including metrics, to track the impacts and outcomes of their stakeholder engagement efforts. As part of the tracking effort, the EDCs should develop standardized ways to summarize stakeholder input/feedback and the EDC's response to any such stakeholder input/feedback, including explanations regarding why feedback was or was not integrated. | The EDCs have proposed to establish a Community Engagement Stakeholder Advisory Group, which would develop a Community Engagement Framework. Regardless of the specific process, this recommendation is for standardized procedures to track EDC stakeholder engagement efforts, which should include metrics and feedback loops. | Stakeholder engagement | Liz Anderson | 2023-09-22 | None
Unitil | 3 - Stakeholder Engagement |  |  | Stakeholder Engagement - Procedures and Metrics | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should develop standardized procedures, including metrics, to track the impacts and outcomes of their stakeholder engagement efforts. As part of the tracking effort, the EDCs should develop standardized ways to summarize stakeholder input/feedback and the EDC's response to any such stakeholder input/feedback, including explanations regarding why feedback was or was not integrated. | The EDCs have proposed to establish a Community Engagement Stakeholder Advisory Group, which would develop a Community Engagement Framework. Regardless of the specific process, this recommendation is for standardized procedures to track EDC stakeholder engagement efforts, which should include metrics and feedback loops. | Stakeholder engagement | Liz Anderson | 2023-09-22 | None
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | 5-and 10-year Demand Forecast - Policy | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The Company should provide a summary (in, for example, table or list form) of any State, Federal, or other policies, programs, or policy plans or analyses (for example, the Company’s Energy Efficiency Plan or the Commonwealth’s All Options Scenario) that are utilized, incorporated in, or otherwise reflected in its demand forecast. The summary should identify the policy, program, or policy plan or analysis and should provide a high-level explanation of how that policy, program, or policy plan is translated into the demand forecast. | The goal of this recommendation is to provide an overview of how policy is incorporated into the Company's demand forecast. | Forecasting | Liz Anderson | 2023-09-22 | None
National Grid | 5 - 5-and 10-year Demand Forecast |  |  | 5-and 10-year Demand Forecast - Policy | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The Company should provide a summary (in, for example, table or list form) of any State, Federal, or other policies, programs, or policy plans or analyses (for example, the Company’s Energy Efficiency Plan or the Commonwealth’s All Options Scenario) that are utilized, incorporated in, or otherwise reflected in its demand forecast. The summary should identify the policy, program, or policy plan or analysis and should provide a high-level explanation of how that policy, program, or policy plan is translated into the demand forecast. | The goal of this recommendation is to provide an overview of how policy is incorporated into the Company's demand forecast. | Forecasting | Liz Anderson | 2023-09-22 | None
Unitil | 5 - 5-and 10-year Demand Forecast |  |  | 5-and 10-year Demand Forecast - Policy | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The Company should provide a summary (in, for example, table or list form) of any State, Federal, or other policies, programs, or policy plans or analyses (for example, the Company’s Energy Efficiency Plan or the Commonwealth’s All Options Scenario) that are utilized, incorporated in, or otherwise reflected in its demand forecast. The summary should identify the policy, program, or policy plan or analysis and should provide a high-level explanation of how that policy, program, or policy plan is translated into the demand forecast. | The goal of this recommendation is to provide an overview of how policy is incorporated into the Company's demand forecast. | Forecasting | Liz Anderson | 2023-09-22 | None
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | 5-and 10-year Demand Forecast - Sensitivity Analyses | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The September 14 GMAC meeting summary states under Section 5: Five- to Ten-Year Demand Forecast, "This section would benefit from sensitivity analyses to factor in such variables as energy storage, heat pumps, EV adoption, technological advances, and other electrification transitions." The Company should provide sensitivity analyses (with additional detail to be developed by GMAC and the GMAC consultants) that factor in the variables such as those described, as well as additional variables (as identified by GMAC and the GMAC consultants). | Several members expressed support for the EDCs to provide sensitivity analyses for their demand forecasts. This recommendation would have the GMAC (with the GMAC consultants) provide to the EDCs a set of scenarios/ sensitivities for which the EDCs should provide results. | Forecasting | Liz Anderson | 2023-09-22 | None
National Grid | 5 - 5-and 10-year Demand Forecast |  |  | 5-and 10-year Demand Forecast - Sensitivity Analyses | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The September 14 GMAC meeting summary states under Section 5: Five- to Ten-Year Demand Forecast, "This section would benefit from sensitivity analyses to factor in such variables as energy storage, heat pumps, EV adoption, technological advances, and other electrification transitions." The Company should provide sensitivity analyses (with additional detail to be developed by GMAC and the GMAC consultants) that factor in the variables such as those described, as well as additional variables (as identified by GMAC and the GMAC consultants). | Several members expressed support for the EDCs to provide sensitivity analyses for their demand forecasts. This recommendation would have the GMAC (with the GMAC consultants) provide to the EDCs a set of scenarios/ sensitivities for which the EDCs should provide results. | Forecasting | Liz Anderson | 2023-09-22 | None
Unitil | 5 - 5-and 10-year Demand Forecast |  |  | 5-and 10-year Demand Forecast - Sensitivity Analyses | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The September 14 GMAC meeting summary states under Section 5: Five- to Ten-Year Demand Forecast, "This section would benefit from sensitivity analyses to factor in such variables as energy storage, heat pumps, EV adoption, technological advances, and other electrification transitions." The Company should provide sensitivity analyses (with additional detail to be developed by GMAC and the GMAC consultants) that factor in the variables such as those described, as well as additional variables (as identified by GMAC and the GMAC consultants). | Several members expressed support for the EDCs to provide sensitivity analyses for their demand forecasts. This recommendation would have the GMAC (with the GMAC consultants) provide to the EDCs a set of scenarios/ sensitivities for which the EDCs should provide results. | Forecasting | Liz Anderson | 2023-09-22 | None
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 198 | Modeling | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The company should consistently use the "All Options" scenario from the CECP instead of "Phased." | The company alternates between using the "All Options" scenario and the "Phased" scenario from the CECP. First, it should be noted that "All Options" comes from the state's decarbonization roadmap, not the CECP. The CECP equivalent is referred to as "High Electrificiation." The company should clarify if they mean the roadmap or the CECP. Further, the company should utilize the "All Options" scenario outlined by the roadmap instead of "Phased" because "All Options" contemplates "Under the most likely assumptions, what is the least-cost deployment of energy system technologies that achieves deep decarbonization?" | Editorial guidelines | Kyle Murray
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1.7 | 206 | Heat pump figures | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The company should adopt greater goals for heat pump adoption | This likely is more a EEAC issue than GMAC, but I have major concerns about the pace of load growth expected from heat pumps. These heat pump adoption figures do not seem like they will get us to the deep decarbonization we will need to hit our greenhouse gas requirements | Forecasting | Kyle Murray
Eversource | 5 - 5-and 10-year Demand Forecast | 5 | 211 | Forecasting | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | Will these forecasting models be available for analysis by outside parties? |  | Forecasting | Kyle Murray
National Grid | 3 - Stakeholder Engagement |  |  | Outreach | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | More detail is needed on outreach and EJ overall | This is for all the companies. I think we need more specifics on outreach and EJ. For example, specific, concrete actions that the companies plan to take, hard timelines being set, consistent definitions on terms like "equity" being used across territories. A uniform approach on most things across territories would be helpful. | Environmental justice community outreach | Kyle Murray
National Grid | 5 - 5-and 10-year Demand Forecast |  |  | Senstivity analysis | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The companies should perform/demonstrate sensitivity analysis to show potential results from different scenarios | For all companies | Forecasting | Kyle Murray
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | Modeling | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Load forecasts need to better explain forecasts. Many claims appear unsubstantiated | For all companies | Forecasting | Kyle Murray
Eversource | 3 - Stakeholder Engagement | 3.6.2 |  | Feedback | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The CESAG should be providing regular updates to the GMAC on progress | For all companies | Stakeholder engagement | Kyle Murray
Eversource | 3 - Stakeholder Engagement | 3.6.2 |  | CESAG leadership | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | CESAG should have a co-lead that is not utility-based, such as DOER or community-based groups | For all companies | Stakeholder engagement | Kyle Murray
Eversource | 3 - Stakeholder Engagement | 3.6.2 |  | Compensation | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Participants in CESAG should receive compensation for their work | For all companies | Stakeholder engagement | Kyle Murray
| 3 - Stakeholder Engagement | 3.8 | NG - 56 Eversource - 42 (3.6.2) Unitil - 26 | Community Engagement Stakeholder Advisory Group (CESAG) | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The Community Engagment Stakeholder Advisory Group (CESAG) should be hosted within the GMAC instead of establishing a new advisory group. The DPU should also review the proposed CESAG framework before a working group is established. | Considering the number of working groups that community and EJ stakeholders are asked to participate in, could the GMAC (or GMAC EWG) provide input and revisions to a Community Engagement Framework and Community Benefits Frameworks instead of the proposed new advisory group? The GMAC could help by providing feedback and suggesting ways to incorporate it into the EDCs planning structures. Also, the EDCs write about their ongoing stakeholder engagement effortsin the ESMPs – is there a way they could use those existing touchpoints to gain feedback on the frameworks? | Stakeholder engagement | Elizabeth Mahony | 2023-09-20
| 3 - Stakeholder Engagement | 3.8 | NG - 60 Eversource - 43 (3.6.2) Unitil - 26 | Community Engagement Stakeholder Advisory Group (CESAG) | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should consider broadening the Community Engagement Framework mission. The scope of the framework should encompass existing activities outside of infrastructure siting. | Currently, the EDCs envision the CESAG helping create frameworks for them to apply to infrastructure projects that need to be submitted to DPU/EFSB. Could the scope be broaden to grid infrastructure more generally? Eversource in particular writes about sharing benefits and burdens, but only in the context of major projects. Could stakeholder engagement efforts around other infrastructure like EV infrastructure/make ready and others be included? | Stakeholder engagement | Elizabeth Mahony | 2023-09-20
| 3 - Stakeholder Engagement | 3.5 | NG - 53 Eversource - 41 Unitil - No maps | Environmental Justice Communities Data | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should improve data reporting for Environmental Justice Communities (EJCs) in EDC territories. This includes having uniform mapping across all EDCs, customer counts by type of EJC by subregion, and also SAIDI/SAIFI (or perhaps CKAIDI/CKAIFI) for EJCs versus the general territory. |  | Environmental justice community outreach | Elizabeth Mahony | 2023-09-20
| 3 - Stakeholder Engagement | 3.4 | NG - 56 Eversource - 38 Unitil - 25 | Stakeholder Outreach Metrics | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Metrics related to outreach and involvement of stakeholders, including EJCs, municipal leaders, and customers, need to be established and reported on. | Each plan describes best practices, and how the EDCs think about outreach, but doesn't describe specific engagements or how feedback from the public is being incorporated. What kind of process or reporting can be set up so stakeholders know how their feedback is being incorporated? In the metrics reporting, it will be important to include EJ metrics (perhaps relating to siting considerations, location of new infrastructure, condition and age of assets in EJCs, low-income rate enrollment, etc.) | Environmental justice community outreach | Elizabeth Mahony | 2023-09-20
| 3 - Stakeholder Engagement |  |  | Direct Benefits to Communities Hosting Energy Infrastructure | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | We would like to see more description and a clear definition of the "direct benefits" that the EDCs expect the communities hosting energy infrastructure will receive. It seems that the EDCs are planning on state policy & incentives to drive electrification technologies and DERs to communities with available capacity. What actions/role do the EDCs foresee for themselves in improving interconnection outcomes and sharing information about policies or incentives? |  | Stakeholder engagement | Elizabeth Mahony | 2023-09-20
| 3 - Stakeholder Engagement |  |  | Accessible Language | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should ensure that plain and accessible language is used when communicating with stakeholders. | Communication with stakeholders should not only be plain and easily understood, but also translated appropriately for communities. The National Grid ESMP has laid this aspect of stakeholder engagement out more clearly than the other EDC ESMPs. | Stakeholder engagement | Elizabeth Mahony | 2023-09-20
| 4 - Current State of the DS |  |  | Capital Investment Projects (CIPs) | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The EDCs should consider other ways to increase substation capacity beyond individual CIPs. The CIPs docket process is very time and resource intensive. |  | Infrastructure | Elizabeth Mahony | 2023-09-20
National Grid | 4 - Current State of the DS | 4.3.8 | 96 | Lack of Transparency and Context in Current State Information | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The EDCs should clearly explain their methodologies and data visualizations for the current state of the distribution system. The aging infrastructure subsections lack substantiation against average life expectancies for different equipment. | National Grid presents a substation tiering method based on SAIDI/SAIFI values, but it looks like there is only one “Tier 4” on any map. | Infrastructure | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS | 4.5 | ex. 151 | Lack of Transparency and Context in Current State Information | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The EDCs should clearly explain their methodologies and data visualizations for the current state of the distribution system. For example, the aging infrastructure subsections lack substantiation against average life expectancies for different equipment or other conditions that the EDCs use to determine when equipment needs to be replaced. | Eversource has a complex pole evaluation methodology that is difficult to understand. Equipment outages are one of the largest sources of outages in Eversource sub-regions, but is not described qualitatively. The additional table on equipment outages is not explained to the reader. | Infrastructure | Elizabeth Mahony | 2023-09-20
| 4 - Current State of the DS |  |  | Navigating EDC Data | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | The EDCs should create a list of data sources and and maintain a centralized source of them. We would like to see this provided as a table in each EDC ESMP, at minimum. The EDCs should host a single website that brings together all data. | Throughout the ESMPs, many existing systems and processes for reporting are referenced. There needs to be a centralized place where stakeholders can access the variety of available system data, from metrics reports, system studies, hosting capacity maps, and more. A starting list aggregated from reading just the Eversource ESMP Chapter 4 is below: a. Annual Reliability Report (ARR) – see page 71 - footnote 27 for link) b. Distribution System Resiliency Report (annual report – page 74) c. Service Quality Index (SQI) filing (23-SW-13) – page 75 d. Eversource 2022 Annual Report (page 80) e. Electric Franchises 2021 Report (page 83) f. Electric Tariffs and Rules (page 94) g. Long-range Plan (Pg 95- but no link to where this can be found) h. Outage website (not explicitly mentioned but ref on page 183) i. MassSave data j. EV adoption numbers and EVSE Make Ready projects completed | Editorial guidelines | Elizabeth Mahony | 2023-09-20
| 4 - Current State of the DS |  |  | Metrics | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Existing metrics should be centralized in the ESMP reporting process to the greatest extent possible, and new metrics for EJC as well as electrification growth reporting should be created. Further, there should be a strategy proposed to enable reporting on heating electrification (which the EDCs note that they cannot report on because of the LDC non-overlapping territory issues). |  | Electrification | Elizabeth Mahony | 2023-09-20
| 4 - Current State of the DS |  |  | Scale of interconnection challenge is not accurately defined | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The challenges around the current state of interconnection are not detailed to their full extent. The EDCs should include data on projects that have dropped out of the queue in the section on DER in Chapter 4, and the number of interconnection requests they may have received but have not gone forward due to interconnection cost or timeline. | The interconnection challenge is significant for DER and electrification needs. Many DERs are behind the queue that aren’t referenced here, and building developers and others aren’t electrifying as quickly as they might because interconnecting to the grid is a major barrier. Quantifying this problem as much as possible is important in this "Current State" section. | Distributed energy resources | Elizabeth Mahony | 2023-09-20
| 4 - Current State of the DS |  |  | Connection to the Commonwealth's goals | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The EDCs should tie the current state of the system to the current Commonwealth’s goals. It’s difficult to understand if the state is on track to meeting its goals based on the information provided in the chapter. |  | Alignment with state goals | Elizabeth Mahony | 2023-09-20
| 5 - 5-and 10-year Demand Forecast |  |  | Forecasts | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The EDCs should include sensitivities and uncertainties in their forecasts included in Chapter 5. Currently, each subsector contributing to the forecast represents a maximum peak load in a worst case scenario. | What uncertainties are there in the different forecast elements? If this information is provided in subsequent chapters, the EDCs should be clear about that. If it's not possible to add quantitative uncertainties, qualitative descriptions of uncertainty should be added at minimum. | Forecasting | Elizabeth Mahony | 2023-09-20
Eversource | 5 - 5-and 10-year Demand Forecast |  | 214 | Unclear Data | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | There is a lack of citations to data. For example, Eversource notes they use “adoption files that contain state-wide projections for each technology (EV, PV, heat pump, etc.) broken down by annual adoption…from trend models, or data supporting reports such as the 2050 Decarbonization Roadmap” (Page 215). Eversource should provide these projections and data sources. |  | Editorial guidelines | Elizabeth Mahony | 2023-09-20
| 5 - 5-and 10-year Demand Forecast |  |  | Meeting the Commonwealth's goals and targets | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? | The EDCs should clearly state if and how overall state goals and targets from the Clean Energy and Climate Plan (CECP) are being met. | It is currently unclear to what extent each of the forecasts is aligning with state goals. National Grid plans do cite to CECP forecasts, but Eversource seems to cite to Roadmap data, which is outdated and has lower targets. Would like the EDCs to be clear if overall state goals and targets from the CECP are being met. | Alignment with state goals | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS | 4.3.6 |  | Smart inverter controls |  | Discuss benefits of smart inverter controls as demonstrated at BESS-based microgrid in Provincetown and plans for expansion throughout Commonwealth. (Ref = 4.3.6.2) |  | Battery energy storage systems | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS |  |  | Missing data |  | Please provide capacity breakouts of solar and storage pieces with storage+solar projects in the queue (Ref = 4.x.5) |  | Editorial guidelines | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS |  |  | Missing data |  | Please provide breakouts of the stages of the queue in which various projects are in as National Grid gave in their ESMP (e.g., pre-study, post-ISA, study phase, pending withdraw, Fig. 4.78 is an example) |  | Editorial guidelines | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS |  |  | Clarification |  | In the regional sections on DER adoption (i.e., 4.x.5), confirm peak demand reduction calculations of solar + storage is purely based off solar production, as is implied. | If so, please also include estimates for storage’s contribution to peak demand reduction. Since Eversource is using historical data to estimate solar’s contribution to peak demand reduction, a similar approach should be taken for storage. National Grid provided such estimates for they system in their ESMP (i.e., National Grid Fig. 5.3-5.5) | Distributed energy resources | Elizabeth Mahony | 2023-09-20
| 4 - Current State of the DS |  |  | Storage |  | Please provide discussion that compares how the EDCs study the interconnection of storage in Massachusetts with how other utilities in states that are actively deploying storage (i.e., California, Texas, New York) are studying the interconnection of storage on their distribution systems. |  | Energy storage systems | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS |  |  | Storage |  | Please discuss if Eversource is considering or has started a program similar to National Grid’s Active Resource Integration (ARI) pilot, which is testing flexible connections for storage. If such a program is not being contemplated, explain why. |  | Misc. | Elizabeth Mahony | 2023-09-20
| 4 - Current State of the DS |  |  | Load density by circuit |  | Can the EDCs include information or a map about load density in the sub-regions? |  | Misc. | Elizabeth Mahony | 2023-09-20
Eversource | 4 - Current State of the DS |  |  | Summary table |  | Eversource should make a summary table with key characteristics of each sub-region. Please refer to the National Grid ESMP Exhibit 4.4 as an example. |  | Editorial guidelines | Elizabeth Mahony | 2023-09-20
Eversource | 5 - 5-and 10-year Demand Forecast |  |  | Unclear Data | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | There is inconsistent information in this chapter. Eversource should provide historical data around storage’s contribution to reducing peak load, as National Grid has done in their ESMP (Fig. 5.3), as well as Eversource's projections going forward (e.g., National Grid Fig. 5.4, 5.5). For Eversource's projections, include assumptions and process to arrive at the numbers. |  | Editorial guidelines | Elizabeth Mahony | 2023-09-20
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 201 | Unclear Data | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | There are unexplained assumptions in this chapter. National Grid show assumptions and process that led to Figures 5.3 – 5.5: storage decreasing peak load by 115 MW in 2022, increasing peak load by 9 MW in 2029, increasing peak load by 10 MW in 2030, respectively. |  | Editorial guidelines | Elizabeth Mahony | 2023-09-20
National Grid | 4 - Current State of the DS |  | 74 |  |  | Please discuss scope, goals, and timeline of Active Resource Integration (ARI) pilot for storage, what success looks like, and if successful, plans for wider deployment. |  | Misc. | Elizabeth Mahony | 2023-09-20
National Grid | 4 - Current State of the DS |  | 74 |  |  | Please elaborate on your plants to scale existing ConnectedSolutions DR program. |  | Demand response | Elizabeth Mahony | 2023-09-20
National Grid | 4 - Current State of the DS | 4.5 |  |  |  | Please resolve discrepancy between Exhibit 4.54, which shows 5.0 MW storage adoption, and Exhibit 4.55, which shows 9.1 MW of storage adoption. |  | Energy storage systems | Elizabeth Mahony | 2023-09-20
Unitil | 4 - Current State of the DS |  |  |  |  | Please break down queue numbers of storage projects, both standalone and paired with solar, regionally, as was done in National Grid and Eversource’s ESMPs. | Would also like to see breakouts of the stages of the queue in which various projects are in as National Grid gave in their ESMP (e.g., pre-study, post-ISA, study phase, pending withdraw, Fig. 4.78 is an example) | Energy storage systems | Elizabeth Mahony | 2023-09-20
Unitil | 4 - Current State of the DS |  |  |  |  | Discuss if Unitil is considering or has started a program similar to National Grid’s Active Resource Integration (ARI) pilot, which is testing flexible connections for storage. If such a program is not being contemplated, explain why. |  | Energy storage systems | Elizabeth Mahony | 2023-09-20
Unitil | 4 - Current State of the DS |  |  |  |  | Please provide discussion that compares how Unitil studies the interconnection of storage in Massachusetts with how other utilities in states that are actively deploying storage (i.e., California, Texas, New York) are studying the interconnection of storage on their distribution systems. |  | Energy storage systems | Elizabeth Mahony | 2023-09-20
| 5 - 5-and 10-year Demand Forecast |  |  |  |  | Eversource and National Grid should include growth analysis for storage in all regional sections. |  | Demand response | Elizabeth Mahony | 2023-09-20
Unitil | 5 - 5-and 10-year Demand Forecast |  |  |  |  | Specify storage assumptions in DER forecast (i.e,. Top of p. 56): How much energy storage installed to level load curve? How much storage charging during peak load? How much storage discharging during minimum load? |  | Energy storage systems | Elizabeth Mahony | 2023-09-20
Unitil | 5 - 5-and 10-year Demand Forecast |  |  |  |  | Provide historical data around storage’s contribution to reducing peak load, as National Grid has done in their ESMP (Fig. 5.3), as well as your projections going forward (e.g., National Grid Fig. 5.4, 5.5). For your projections, include your assumptions and process to arrive at your numbers. |  | Energy storage systems | Elizabeth Mahony | 2023-09-20
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1.3 | 221-223 | EV adoption rates |  | Elaborate on source(s) of adoption projection(s); include both estimated number of vehicles and relative % of vehicles that will be EVs in the service territory, for LDVs and MDVs/HDVs; add assumptions about types of charging by use type. |  | Electric vehicle charging | Elizabeth Mahony | 2023-09-20
National Grid | 5 - 5-and 10-year Demand Forecast | 5.2.6 | 210-211 | EV adoption rates |  | Elaborate on source(s) of adoption projection(s); include both estimated number of vehicles and relative % of vehicles that will be EVs in the service territory, for LDVs and MDVs/HDVs. Add assumptions about types of charging by use type, and correlating amount of demand for charging. |  | Electric vehicle charging | Elizabeth Mahony | 2023-09-20
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.5 | 56-58 | EV adoption rates |  | Include both estimated number of vehicles and relative % of vehicles that will be EVs in the service territory, for LDVs and MDVs/HDVs, and correlating amount of demand for charging. What assumptions is the company using about number of EVs by LDV vs. MDV and HDV? |  | Electric vehicle charging | Elizabeth Mahony | 2023-09-20
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.5 | 57 | Workplace/fleet charging |  | Does "workplace" include fleet or fleet depot charging? |  | Electric vehicle charging | Elizabeth Mahony | 2023-09-20
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.5 | 56-58 | DCFC installations |  | Though using the ISO-NE projections, why are there so few DCFC projected per year in the territory? (0-2) |  | Electric vehicle charging | Elizabeth Mahony | 2023-09-20
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1.6. | 204 | PV installed capacity |  | Estimating only ~4GW of installed solar capacity in 2034, this seems low |  | Misc. | Elizabeth Mahony | 2023-09-20
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1.6. | 226 | PV installed capacity |  | Estimating only ~1.4GW of installed solar capacity in 2033, this seems low |  | Misc. | Elizabeth Mahony | 2023-09-20
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.8 | 62 | Mislabeled table |  | It seems like the 2nd base and PV titles need to be changed on Table 13 |  | Editorial guidelines | Elizabeth Mahony | 2023-09-20
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1.5 | 56 | EV adoption rates |  | Please provide outputs of modeling for High Rate and Baseline Rate |  | Editorial guidelines | Elizabeth Mahony | 2023-09-20
National Grid | 3 - Stakeholder Engagement | 3.8 | 59-61 | Stakeholder Engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | None of the three ESPM plans address the use or power of leveraging localized decision making or accountability processes in their community and stakeholder engaging process. The plans acknowledge the need for education, shared understanding, and output of information with acknowledgment of language and culture needs but the plans do not go far enough to have a truly equitable approach that allows for local decision making among the most impacted people- customers, EJ and LMI. The plans should be pushed deeper and further to allow for local control of decisions around the impact of transmission plans, siting, procurement sourcing of contracts, and hiring goals. The plans should establish a robust accountability system that prioritizes the interests of the most vulnerable and historically and disproportionally impacted people by listening to and directly addressing their concerns from the beginning of the planning process to the end. The CESAG groups should bee formed as shared accountability committee that is empowered to oversee decisions and hold plans accountable to equitable outcomes that are defined by the communities. |  | Environmental justice community outreach | Marybeth Campbell | 9.24
Eversource |  | 3.8-3.10 | 45-48 | Stakeholder Engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | All educational materials planned for distribution in the community should prioritize using nontechnical language and should feature culturally competent, accessible, and transparent Information. Local meetings should always allow sufficient time for direct public input or offer an opportunity for public comment to be submitted beforehand and registered into the record. Community meetings should be scheduled to accommodate impacted community members and be accessibly located- and all plans should follow what is suggested by Eversource to allow for childcare. Community meetings should include translation services, flexible times, and childcare options. Means for remote engagement that allow for public commenting and viewing of meetings should be provided. Utility funds should be set aside in a dedicated account from which impacted communities engaging in the CESAG can draw to hire experts and representation to inform their members and represent their interests in technical matters requiring expertise. This funding should be sufficient to cover communities' entire costs of participation including paid stipends to CESAG and community members being asked to take local leadership role. |  | Stakeholder engagement | Marybeth Campbell | 2023-09-24
Eversource | 3 - Stakeholder Engagement | 3.1 | 35 | Stakeholder Engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | To ensure true equity, Eversource and all the ESMPs must relook at their definitons of equity. | There is a definition of equity provided, which all EDC ESMPs should address directly in their plans. Howveer the provided definition in the Eversource plan does not address issues of equity in terms of the acknowledgment of the issues that have histrorically created a disproporation and negative inpact on certain communities, nor does the defiition address a need to balance decisionmaking power and resources toward a reality where communities are impacting wholly by their own decsions and working with utilties on accountable outcomes. The impacts of discrimination and inequity must be addressed acknowledged first to fairly address them from the point of root causes. This includes the adoption of new policies, practices, attitudes, and cultural messages that affirm race, class, and gender justice. | Editorial guidelines | Marybeth Campbell | 9.24
Unitil |  | 3.8 | 25-27 | Stakeholder Engagement | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | Strong encourgae Unitil plan to expand on its approach to an equitabel framework of community engagment. This section require much more attention to detial, and greater specificity. It is greatly lacking compared to the other plans, which also don’t got far enough |  | Stakeholder engagement | Marybeth Campbell
National Grid | 3 - Stakeholder Engagement | 3.1 |  | Metrics for equity | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | I would like to see some quantifiable metrics on how the proposed plan can improve equity. |  | Equity | Andy Sun
Eversource | 3 - Stakeholder Engagement | 3.1 |  | Metrics for equity | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | I would like to see some quantifiable metrics on how the proposed plan can improve equity. |  | Equity | Andy Sun
Unitil | 3 - Stakeholder Engagement | 3.1 |  | Metrics for equity | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? | I would like to see some quantifiable metrics on how the proposed plan can improve equity. |  | Equity | Andy Sun
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 199-203 | Forecast scenarios | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The forecast given in the plan does not seem to include any specification of the uncertainty level. Instead of having one forecast level, it should provide some scenarios of forecast demand, e.g. of high, medium, low level of future peak load. |  | Forecasting | Andy Sun
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 205 | EV forecast | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Similar to the load forecast, the plan does not provide discussion on the uncertainty associated with EV adoption. The current projects may be viewed as "aspirational" rather than likely outcome. At least, some scenarios of EV adoption levels should be given. Also, does the forecast consider the time of charge variations and potential charging programs that can shift charging impacts on peak load? |  | Forecasting | Andy Sun
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 206-207 | Heat Pump uncertainty | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Similar to the load forecast, the plan does not seem to provide discussion on the uncertainty associated with heat pump penetration. Regarding heat pump, most of the switching so far has been from customers using oil and propane for heating. Conversion from gas heating is much more challenging. If this is right, then demand forecast from heating electrification could be too high. Can Ngrid provide data on the breakdown of the heat pump conversion that has happened so far? |  | Forecasting | Andy Sun
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 202, 204 | Solar PV impact on peak load | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Why is PV's impact on peak load 0 in Exhibits 5.4 and 5.5? How is it consistent with the forecast of 2000MW increase of PV solar in Exhibit 5.8? |  | Forecasting | Andy Sun
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 | 204 | Battery impact on peak load | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Not much forecast of battery storage is provided in 5.1, and also for each subregion in the rest of the chapter. Can Ngrid provide more details? Also, can Ngrid comment on how the company plan to promote and control storage in their territory to help reduce peak load? |  | Battery energy storage systems | Andy Sun
National Grid | 4 - Current State of the DS | 4.1 |  | AMI | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report mentions the plan to increase deployment of AMI. However, not much details are given. More importantly, how does the company plan to use AMI with new pricing and load control options to smooth out load peaks? |  | Grid capacity | Andy Sun
National Grid | 4 - Current State of the DS | 4.1 | 92 | reliability criteria | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | I would like to see more economic justification for the reliability criteria that are now being used, especially in light of more storage, real time information, and a more networked distribution grid. What are the implied value of lost load that these criteria imply? How does more storage and more flexible load impact system reliability? |  | Grid capacity | Andy Sun
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 | 219 | Forecast scenarios | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The forecast given in the plan does not seem to include any specification of the uncertainty level. Instead of having one forecast level, it should provide some scenarios of forecast demand, e.g. of high, medium, low level of future peak load. |  | Forecasting | Andy Sun
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 | 221 | EV forecast | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Similar to the load forecast, the plan does not provide discussion on the uncertainty associated with EV adoption. The current plan states "by 2033, the company expects that 29.2% of light duty vehicles in the statewide market will have been replace by electric vehicles." The projections may be viewed as "aspirational" rather than likely outcome. At least, some scenarios of EV adoption levels should be given. Also, does the forecast consider the time of charge variations and potential charging programs that can shift charging impacts on peak load? |  | Electric vehicle charging | Andy Sun
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 | 227-228 | Heat Pump uncertainty | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Similar to the load forecast, the plan does not seem to provide discussion on the uncertainty associated with heat pump penetration. Regarding heat pump, most of the switching so far has been from customers using oil and propane for heating. Conversion from gas heating is much more challenging. If this is right, then demand forecast from heating electrification could be too high. Can the Eversource provide data on the breakdown of the heat pump conversion that has happened so far? Can Eversource provide an estimation of how likely is the All Options Scenario which predicts 3.4GW of winter peak addition of heating load by 2035? |  | Grid capacity | Andy Sun
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 | 226-227 | Solar PV impact on peak load | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | The forecast of load deferral from PV is based on the assumption of large increase in space heating (20% conversion and 1.96GW on page 227). However, if heat pump adoption is slower (given the concern above for heat pump), the impact of solar PV on load deferral could be underestimated, leading to overestimation of need in upgrading infrastructure. Eversource should provide more scenarios for heat pump adoption and the associated peak load deferral from PV solar. |  | Grid capacity | Andy Sun
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 | 204 | Battery impact on peak load | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Not much forecast of battery storage is provided in 5.1, and also for each subregion in the rest of the chapter. Can Eversource provide more details? Also, can Eversource provide comment on how the company plans to promote and control storage in their territory to help reduce peak load? |  | Battery energy storage systems | Andy Sun
Eversource | 4 - Current State of the DS | 4.1 |  | AMI | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report mentions the plan to increase deployment of AMI. However, not much details are given. More importantly, how does the company plan to use AMI with new pricing and load control options to smooth out load peaks? |  | Grid capacity | Andy Sun
Eversource | 4 - Current State of the DS | 4.1 | 73 | reliability criteria | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | I would like to see more economic justification for the reliability criteria that are now being used, especially in light of more storage, real time information, and a more networked distribution grid. What are the implied value of lost load that these criteria imply? How does more storage and more flexible load impact system reliability? |  | Energy storage system | Andy Sun
Eversource | 4 - Current State of the DS | 4.1 |  | Planning process | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Can the utility provide more details on the planning process, any use of system-wide least-cost optimization? What other expansion/hardening options are considered before reaching the current plan? |  | Stakeholder engagement | Andy Sun
National Grid | 4 - Current State of the DS | 4.1 |  | Planning process | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Can the utility provide more details on the planning process, any use of system-wide least-cost optimization? What other expansion/hardening options are considered before reaching the current plan? |  | Stakeholder engagement | Andy Sun
Unitil | 4 - Current State of the DS | 4.1 |  | Planning process | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? | Can the utility provide more details on the planning process, any use of system-wide least-cost optimization? What other expansion/hardening options are considered before reaching the current plan? |  | Stakeholder engagement | Andy Sun
Eversource | 4 - Current State of the DS | 4.1 |  | Power quality | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report does not mention power quality. Can the company provide data and metrics on power quality and any plan on improving power quality? |  | Editorial guidelines | Andy Sun
National Grid | 4 - Current State of the DS | 4.1 |  | Power quality | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report does not mention power quality. Can the company provide data and metrics on power quality and any plan on improving power quality? |  | Misc. | Andy Sun
Unitil | 4 - Current State of the DS | 4.1 |  | Power quality | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report does not mention power quality. Can the company provide data and metrics on power quality and any plan on improving power quality? |  | Misc. | Andy Sun
National Grid | 5 - 5-and 10-year Demand Forecast | 5.1 |  | Bi-directional charging | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report does not have much discussion on bi-directional charging of EV (V2G) and its impact on future grid. Can the company provide any comment on plans to promote/pilot such efforts? |  | Electric vehicle charging | Andy Sun
Eversource | 5 - 5-and 10-year Demand Forecast | 5.1 |  | Bi-directional charging | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report does not have much discussion on bi-directional charging of EV (V2G) and its impact on future grid. Can the company provide any comment on plans to promote/pilot such efforts? |  | Electric vehicle charging | Andy Sun
Unitil | 5 - 5-and 10-year Demand Forecast | 5.1 |  | Bi-directional charging | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. | The report does not have much discussion on bi-directional charging of EV (V2G) and its impact on future grid. Can the company provide any comment on plans to promote/pilot such efforts? |  | Electric vehicle charging | Andy Sun

## Review Schedule
ESMP Review Schedule
DEADLINES FOR FEEDBACK/RECOMMENDATIONS
Please email MA-GMAC@mass.gov a completed Excel sheet with recommendations pertaining to sections reviewed at each GMAC meeting. A compiled sheet will be created and maintained by the GMAC consultant.
| Excel Due Date | ESMP Section Recommendations
| 2023-09-22 | Stakeholder Engagement, Current State, 5–10-year forecast (Chapters 3, 4, 5)
| 2023-10-06 | 5–10-year solutions, Reliable & Resilient, Workforce, Economic, & Health Benefits (Chapters 6, 10, 12)
| 2023-10-20 | 2035-2050 Drivers and Solution, Gas-Electric Planning (Chapters 8, 9, 11)
| 2023-11-03 | Executive Summary, Climate Act Compliance, 5-year ESMP, Conclusion (Chapters 1, 2, 7, 13)

## Do Not Edit - Data Key
EDC ESMP | Section | Subsection | Page Number | Area of Concern | Guiding Question | Recommendation or Question | Feedback | GMAC Member | Date Added | Upload
Eversource | 1 - Executive Summary | 1.1 |  |  | 1.Does the ESMP section demonstrate equity, including increased transparency and stakeholder engagement in the grid planning process and an equitable distribution of impacts and benefits? |  |  | Kelly Caiazzo |  | Yes, attachment(s) emailed with Excel sheet.
National Grid | 2 - Compliance with 2022 Climate Law | 1.2 |  |  | 2.Does the ESMP section encourage least-cost investments in the electric distribution systems or alternative investments, such as virtual power plants (VPP) and non-wire alternatives (NWA)? |  |  | Galen Nelson |  | None
Unitil | 3 - Stakeholder Engagement | 1.3 |  |  | 3.Does the ESMP section facilitate the achievement of the statewide greenhouse gas emission limits and sublimits under chapter 21N? |  |  | Elizabeth Mahony
All EDCs | 4 - Current State of the DS | 1.4 |  |  | 4.Does the ESMP section effectively optimize net customer benefits and cost-effective investments in the distribution grid? This includes investments to enable the interconnection of and communication with distributed energy resources and transmission-scale renewable energy resources, facilitation of electrification of buildings and transportation, and increased reliability and resiliency. |  |  | Sarah Bresolin Silver
| 5 - 5-and 10-year Demand Forecast | 1.5 |  |  | 5.Does the ESMP section minimize or mitigate impacts on ratepayers and reduce impacts on and provide benefits to low-income ratepayers? |  |  | Marybeth Campbell
| 6 - 5-and 10-year Solutions | 1.6 | [5 empty] | Larry Chretien
| 7 - 5-year ESMP | 1.7 | [5 empty] | Kathryn Cox-Arslan
| 8 - 2035-2050 Policy Drivers | 1.8 | [5 empty] | Amy McGuire
| 9 - 2035-2050 Solution Set | 1.9 | [5 empty] | Kyle Murray
| 10 - Reliable and Resilient | 1.1 | [5 empty] | JS Rancourt
| 11 - Gas-Electric Planning | 3.1 | [5 empty] | Andy Sun
| 12 - Workforce, Economic, and Health | 3.2 | [5 empty] | Alex Worsley
| 13 - Conclusion | 3.3 | [5 empty] | Kathryn Wright
| 14 - Appendix | 3.4 | [5 empty] | Jeremy Koo (Designee of Julie Curti)
|  | 3.5 | [5 empty] | Jonathan Stout
|  | 3.6 | [5 empty] | Digaunto Chatterjee
|  | 3.7 | [5 empty] | Carol Sedewitz
|  | 3.8 | [5 empty] | Kevin Sprague
4.2
4.2
4.3
4.3.1
4.3.2
4.3.3
4.3.4
4.3.5
4.3.6
4.3.7
4.3.8
4.3.9
4.3.10
4.4
4.5
5.1
5.2
5.2.1
5.2.2
5.2.3
5.2.4
5.2.5
5.2.6
5.2.7
5.3
6.1
6.2
6.3
6.3.1
6.4
6.5
6.5.1
6.5.2
6.5.3
6.5.4
6.5.5
6.6
6.6.1
6.6.2
6.6.3
6.6.4
6.6.5
6.7
6.8
7.1
7.1.1
7.1.2
7.1.3
7.2
7.3
8.1
8.2
8.2.1
8.2.2
8.2.3
8.2.4
8.3
8.3.1
8.3.2
8.3.3
8.3.4
8.4
8.4.1
8.4.2
8.4.3
8.5
8.6
9.1
9.1.1
9.1.2
9.1.3
9.1.4
9.2
9.3
9.4
9.5
9.6
9.6.1
9.6.2
9.7
9.7.1
9.7.2
9.7.3
9.8
10.1
10.2
10.3
10.4
10.5
11.1
11.2
11.3
11.4
11.5
11.6
11.7
12.1
12.2
12.3
12.4
12.5
13.1
13.2
13.3
13.4
14.1
14.2