*GWR CT2 is only for PWSs that do not calculate CT on a daily basis and do not have a continuous chlorine residual analyzer.

| I. PWS INFORMATION: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PWSID#: |  |  | PWS Name: |  |  |  |  |  |  |  |  |  |  | PWS Town: |  |  |  |  |  |  |
| Treatment Plant Name1: |  |  |  |  |  |  |  |  | #### Reporting Period  |  |  |  | Month: |  |  |  |  |  | Year: |  |
| Disinfectant: |  |  |  |  |  |  |  |  |  |  | Water Temperature: |  |  |  |  |  | 52° max (USGS Standard) |  |  |  |
| DEP Approved Sample Location: |  |  |  |  |  |  |  |  |  |  | pH6: |  |  |  |  |  | 6.0-9.0 |  |  |  |
| Peak Hourly Flow2 (gpm): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| II. DAILY REPORTING: Measurements taken during peak hourly flow. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Day | Free Chlorine Residual3 C (mg/L) |  |  | MassDEP Minimum Free Chlorine Residual Required to Achieve CT and 4-log treatment for viruses (mg/L)4 |  |  |  | Was the measured free chlorine residual “C” lower than the MassDEP minimum required free chlorine residual?5 |  |  |  |  |  |  |  | If “yes” was checked in the previous column, was the residual restored to the required concentration within 4 hours? |  |  |  |  |
| 1 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 2 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 3 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 4 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 5 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 6 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 7 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 8 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 9 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 10 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 11 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 12 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 13 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 14 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 15 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 16 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 17 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 18 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 19 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 20 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 21 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 22 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 23 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 24 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 25 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 26 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 27 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 28 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 29 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 30 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| 31 |  |  |  |  |  |  |  | Yes No |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| - Use a separate form for each treatment point. - Peak hourly flow is the highest pumpage hour during the day, not the absolute peak flow at any instant. Enter peak hourly flow as reported on GWR Form D and approved by MassDEP. - The residual disinfectant concentration "C" of the water must be measured each day during peak hourly flow, before or at the first customer, after the required contact time, and at the location approved by MassDEP. - Enter the MassDEP approved minimum free chlorine residual required for your PWS to meet 4-log virus treatment; this number does not change. - If any daily measurement is below the MassDEP required minimum free chlorine residual, you must take follow-up samples every four hours until the residual concentration is restored to the MassDEP required level or greater. Failure to achieve the required CT within 4 hours is a Treatment Technique violation (Tier 2) and you must contact call your regional office within 24 hours. - pH must remain between 6.0 and 9.0; call the regional office immediately if pH is out of this range. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| I certify under penalties of law that I am the person authorized to fill out this form and the information contained herein is true, accurate and complete to the best extent of my knowledge. |  |  |  |  |  | PWS Authorized Signature: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Date: |  |  |  | Title: |  |  |  |  |  |  |  |  |  |  |
| In accordance with 310 CMR 22.15(2), if mailing paper reports, TWO copies of this report must be received by your MassDEP Regional Office no later than 10 days after the end of the month in which the results are received or no later than 10 days after the end of the monitoring period, whichever is sooner. Please note: Electronic reporting (eDEP) deadline is the same as above. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |