Massachusetts Flexible Connections Guideline & Implementation Manual

To accompany Massachusetts Standards for Interconnection of Distributed Generation Tariff

Revision History

| Version | Date | Description of Revision |
| --- | --- | --- |
| 0.1 | 3/10/26 | Draft shared amongst Flex IX Subgroup Leads |
| 1.0 | Mon Day, Yr | Original Publication |

Table of Contents

1	Introduction	2

2	Definition & Acronyms	3

3	Flexible Interconnection Offerings	8

3.1	Actively Managed Connections	10

3.1.1	Offering Overview – what it is and why it exists	10

3.1.2	Operating Model  - how functions in practice (active vs passive, etc.)	10

3.1.3	Control & Communications (how the grid and DER interact)	11

3.1.4	Applicability and Use cases (who this works for and/or targets)	12

3.1.5	Contractual Considerations (how this fits in the DG process, commitments, targets, etc.)	12

3.1.6	Benefits & Tradeoffs (why someone would choose this)	13

3.2	Scheduled (i.e. Timed) Connections	14

3.2.1	Offering Overview – what it is and why it exists	14

3.2.2	Operating Model  - how functions in practice (active vs passive, etc)	14

3.2.3	Control & Communications (how the grid and DER interact)	15

3.2.4	Applicability and Use cases (who this works for and/or targets)	15

3.2.5	Contractual Considerations (how this fits in the DG process, commitments, targets, etc.)	15

3.2.6	Benefits & Tradeoffs (why someone would choose this)	16

3.3	Flexibility as a Bridge	16

3.3.1	Offering Overview – what it is and why it exists	16

3.3.2	Operating Model  - how functions in practice (active vs passive, etc)	16

3.3.3	Control & Communications (how the grid and DER interact)	17

3.3.4	Applicability and Use cases (who this works for and/or targets)	17

3.3.5	Contractual Considerations (how this fits in the DG process, commitments, targets, etc)	18

3.3.6	Benefits & Tradeoffs (why someone would choose this)	18

3.4	Export or Import Limitation Schemes (Permanent Derating)	19

4	Flex IX Studies & Curtailment Strategy	19

4.1	Actively Managed Connections	19

4.1.1	Curtailment Target	20

4.1.2	Curtailment Allocation Methodology	21

4.1.3	Curtailment Study Analyses	25

5	Equipment and Design	27

5.1	Actively Managed Connections	27

6	Alignment to DG Interconnection Tariff	27

6.1	DG Interconnection Process Alignment	28

6.2	Group Studies	29

7	Financing & Risk Mitigation	30

7.1	Actively Managed Connections	30

8	Post-upgrade Processes	31

9	Implementation Plan	31

# Introduction

This document has been developed as a general reference guide to describe common concepts, principles, and considerations associated with flexible interconnections. It is maintained through the IIRG and will undergo an annual cycle for review and proposal of updates.  It is intended to highlight areas of shared understanding and provide high level technical context. Utility standards are expected to reflect the common understandings described herein; however, utility specific standards retain final authority. With respect to tariffs, this document is intended to identify flexible connection opportunities that operate within, and do not conflict with, the existing tariff framework. In all cases, the written tariff governs and supersedes this document.

Flexible interconnection includes any control approach that manages customer owned distributed energy resources (DERs) to operate below full nameplate capacity in order to enable interconnection within distribution system limits. This may include actively managed sites responding to real time operational signals, as well as sites operating under predefined schedules or fixed setpoints that limit import and/or export to remain below system thresholds. All such approaches—whether dynamic or scheduled—are considered flexible connections when used to avoid or defer system upgrades and/or allow DER capacity to interconnect more quickly and/or cost effectively than under a traditional firm interconnection.

In developing and applying flexibility programs, the following guiding principles apply:

- Flexibility will be primarily intended for inverter based resources.

- Program design is informed by industry experience, research, peer utility experience, and supporting studies.

- Providing a transparent and comprehensible program that can be effectively communicated to developers, financiers, and system owners.

- Enabling DER to participate across a wide range of markets and spanning both the distribution and transmission system.

- Establishing contractual arrangements that offer protection to stakeholders through estimated curtailment targets and providing protection against flexibility increases to curtailment.

# Definition & Acronyms

| Acronym | Definition |  | Acronym | Definition |
| --- | --- | --- | --- | --- |
| ACEEE | American Council for an Energy-Efficient Economy |  | FTM | Front-of--the---Meter |
| ACP | Alternative Compliance Payment |  | GHG | Greenhouse Gas |
| ADMS | Advanced Distribution Management Systems |  | GWh | Gigawatt-hour |
| AESC | Avoided Energy Supply Components |  | ICE | Interruption Cost Estimate |
| AGO | Attorney General’s Office |  | ISO-NE | Independent System Operator – New England |
| BCA | Benefit-Cost- Analysis |  | LBNL | Lawrence Berkeley National Laboratory |
| BTM | Behind-the---Meter |  | LEAP | Local Energy Action Program |
| CAIDI | Customer Average Interruption Duration Index |  | LMI | Low or Moderate Income |
| COBRA | Co-Benefits Risk Assessment |  | MW | Megawatt |
| CPEC | Clean Peak Energy Credits |  | MWh | Megawatt--hour |
| CPS | Clean Peak (Energy) Standard |  | NEM | Net Energy Metering |
| CS | Connected Solutions |  | NOx | Nitrogen Oxides |
| DER | Distributed Energy Resource |  | NPV | Net Present Value |
| DERMS | Distributed Energy Resource Management Systems |  | NREL | National Renewable Energy Laboratory |
| DOE | Department of Energy |  | NWA | Non-Wires- Alternative |
| DOER | Department of Energy Resources |  | PIMs | Performance Incentive Mechanisms |
| DPU | Department of Public Utilities |  | RMI | Rocky Mountain Institute |
| EDC | Electric Distribution Company |  | SAIDI | System Average Interruption Duration Index |
| EJ | Environmental Justice |  | SAIFI | System Average Interruption Frequency Index |
| EJC | Environmental Justice Community |  | SMART | Solar Massachusetts Renewable Target |
| EPA | Environmental Protection Agency |  | SOx | Sulfur Oxides |
| ESMP | Electric Sector Modernization Plan |  | V2G | Vehicle-to---Grid |
| EV | Electric Vehicle |  | WACC | Weighted Average Cost of Capital |
| FERC | Federal Energy Regulatory Commission |  |  |  |

ACEEE (American Council for an Energy Efficient Economy)
A nonprofit organization that conducts research and advocacy to promote energy efficiency policies and practices.

ACP (Alternative Compliance Payment)
A fee paid by an obligated entity when it does not meet a required energy or environmental compliance obligation.

ADMS (Advanced Distribution Management System)
A software platform used by electric utilities to monitor, control, and optimize distribution system operations.

AESC (Avoided Energy Supply Components)
The generation, transmission, and infrastructure costs avoided as a result of reduced energy demand or increased efficiency.

AGO (Attorney General’s Office)
The state legal authority responsible for enforcing laws, protecting consumers, and representing the public interest.

BCA (Benefit-Cost- Analysis)
A systematic evaluation comparing the economic benefits and costs of a project, program, or policy.

BTM (Behind-the---Meter)
Distributed energy resources co-located with proportionately sized local load, on the customer side of the electric meter.

CAIDI (Customer Average Interruption Duration Index)
A reliability metric representing the average duration of power outages experienced by customers.

COBRA (Co-Benefits Risk Assessment)
An analytical framework used to evaluate social, environmental, or health co-benefits alongside primary project outcomes.

CPEC (Clean Peak Energy Credits)
Tradable credits that incentivize the delivery or use of clean energy during peak demand periods.

CPS (Clean Peak Energy Standard)
A regulatory requirement that a portion of electricity consumed during peak periods come from clean energy resources.

CS (ConnectedSolutions)
A demand response program that compensates customers for reducing or shifting electric load during system peak events.

DER (Distributed Energy Resource)
An - energy resource, such as generation, storage, or controllable load, interconnected to the distribution system.

DERMS (Distributed Energy Resource Management System)
A dynamic control system operated by the EDC that issues signals to Distributed Energy Resources to operate within permissible import and/or export limits, or to perform other functions, in order to support or alleviate electric power system conditions.

DOE (Department of Energy)
The federal agency responsible for national energy policy, research, and nuclear safety.

DOER (Department of Energy Resources)
The Massachusetts state agency responsible for energy planning, policy development, and program oversight.

DPU (Department of Public Utilities)
The Massachusetts regulatory authority overseeing electric, gas, water, and telecommunications utilities.

EDC (Electric Distribution Company)
An entity responsible for the delivery of electricity to customers through the distribution system.

EJ (Environmental Justice)
The principle that all communities should receive fair treatment and meaningful involvement in environmental decision-making-.

EJC (Environmental Justice Community)
A community that experiences disproportionate environmental, health, or economic burdens.

Electric Power System (EPS)
As defined in the DG Interconnection Tariff, MDPU 1599.

Energy
Electrical energy measured in watt-hours (Wh).

Energy Storage System (ESS)
As defined in the DG Interconnection Tariff and as further proposed in the Energy Storage Operational Tariff, a commercially available technology capable of absorbing electricity, storing it for a period of time, and subsequently dispatching electricity.

ESS Planning Capacity
As proposed in the Energy Storage Operational Tariff, the capacity reserved by the Company for a specific Energy Storage System at defined times for both charging and discharging.

EV (Electric Vehicle)
A vehicle powered fully or partially by electricity rather than an internal combustion engine.

Export
The supply of electrical energy to the Electric Power System from a Facility, measured at the Point of Common Coupling.

Export Capacity
As proposed in redline recommendations within DPU 25-48, the maximum alternating current (AC) nameplate rating of a Facility, unless limited by an approved export--limiting- method, in which case Export Capacity is the limited amount measured at the Point of Common Coupling, excluding inadvertent export.

FERC (Federal Energy Regulatory Commission)
The federal agency regulating interstate transmission of electricity, natural gas, and oil.

FTM (Front-of--the-Meter)
Distributed energy resources interconnected directly to the electric grid on the utility side of the meter.

GHG (Greenhouse Gas)
A gas that traps heat in the atmosphere and contributes to climate change, such as carbon dioxide or methane.

GWh (Gigawatt-hour-)
A unit of electrical energy equal to one billion watt-hours.

ICE (Interruption Cost Estimate)
A measure of the economic impact of electric service interruptions on customers.

Import
The consumption of electrical energy supplied from the Electric Power System by a Facility, measured at the Point of Common Coupling.

Import Capacity
As proposed in redline recommendations within DPU 25-48, the maximum alternating current (AC) nameplate rating of a Facility, unless limited by an approved import-limiting method, in which case Import Capacity is the limited amount measured at the Point of Common Coupling.

Interconnection (IX)
The process by which a Facility is electrically connected to the Electric Power System in accordance with the applicable tariff.

Inverter--Based Resource
A resource whose design includes a UL 1741-listed inverter, including Solar Photovoltaic Systems and Energy Storage S-ystems.

ISO--NE (Independent System Operator – New England)
The entity responsible for operating the regional electric grid and wholesale electricity markets in New England.

LBNL (Lawrence Berkeley National Laboratory)
A U.S. Department of Energy national laboratory focused on scientific research related to energy and the environment.

LEAP (Local Energy Action Program)
A program supporting municipalities in developing and implementing clean energy and climate initiatives.

LMI (Low or Moderate Income)
A designation for households with incomes below defined thresholds, often used for program eligibility.

MW (Megawatt)
A unit of electrical power equal to one million watts.

MWh (Megawatt-hour-)
A unit of electrical energy equal to one megawatt of power supplied for one hour.

NEM (Net Energy Metering)
A billing mechanism that credits customers for excess electricity exported to the grid.

Non-Inverter-Based Resource
A resource capable of supplying energy that does not include a UL 1741-li-sted inverter in its design.

NOx (Nitrogen Oxides)
Air pollutants produced by combustion processes that contribute to smog and respiratory issues.

NPV (Net Present Value)
A financial metric representing the present value of future cash flows discounted to today’s dollars.

NREL (National Renewable Energy Laboratory)
A U.S. Department of Energy laboratory focused on renewable energy and energy efficiency research.

NWA (Non-Wires- Alternative)
A solution that uses distributed resources or operational strategies in place of traditional grid infrastructure upgrades.

Operating Agreement
As proposed in the Energy Storage Operational Tariff, the portion of the Special Operating Requirements attached to the Interconnection Service Agreement that identifies allocated ESS Planning Capacity and any applicable Dispatch Limiting Schedule.

PIMs (Performance Incentive Mechanisms)
Regulatory mechanisms that provide incentives to utilities for achieving specified performance outcomes.

Point of Common Coupling (PCC)
As defined in the DG Interconnection Tariff, MDPU 15-99.

Power
Electrical power measured in watts.

SAIDI (System Average Interruption Duration Index)
A reliability metric representing the average total duration of interruptions experienced by customers over a defined period.

SAIFI (System Average Interruption Frequency Index)
A reliability metric representing the average number of interruptions experienced by customers.

SMART (Solar Massachusetts Renewable Target)
A Massachusetts incentive program supporting the development of solar photovoltaic projects.

Solar or Photovoltaic (PV) System
A system that converts sunlight directly into electricity using photovoltaic cells.

SOx (Sulfur Oxides)
Air pollutants formed from sulfur-containing- fuels that contribute to acid rain.

Special Operating Requirements
As proposed in the Energy Storage Operational Tariff, the operating conditions attached to an Interconnection Service Agreement governing non-standard or flexible operation.

V2G (Vehicle-to-Grid)
Technology enabling electric vehicles to export electricity back to the grid.

WACC (Weighted Average Cost of Capital)
A financial metric representing a company’s average cost of debt and equity financing.

# Flexible Interconnection Offerings

This section describes the various flexible interconnection offerings available under a Flexible Interconnection (Flex IX) framework. These offerings represent a range of approaches that enable DERs to interconnect safely and efficiently by operating within defined distribution system limits.

At a foundational level, all flexible interconnection offerings are designed to do no harm to the electric grid—ensuring that customer facilities operate in a manner that does not conflict with, exceed, or degrade system thermal, voltage, or protection constraints. By managing DER output below full nameplate capacity when necessary, flexible connections can enable interconnection where traditional firm interconnection may not be immediately feasible.

Flexible offerings generally fall into two broad categories: active and passive management. Actively managed connections receive real-time grid feedback and are subject to dynamic operating limits, requiring customer facilities to respond in real time to signals from the Company. These approaches enable close alignment between DER operation and prevailing system conditions. In contrast, passive or scheduled connections operate under predefined operating profiles, such as seasonal or time-based curtailment schedules, without continuous real-time, grid-aware feedback.

The dynamic nature of actively managed offerings also creates core competencies for future grid service capabilities. Flexibility is generally intended to enable DERs to operate in a way that increases overall utilization of the distribution system. The core methodology relies on real-time monitoring and communication with DERs, which can be applied to other scenarios where facilities may help support the distribution network or participate in grid services programs to reduce congestion.

While the primary objective remains safe interconnection, these offerings can also support broader system benefits as grid needs evolve.

The specific characteristics, requirements, and use cases for each flexible interconnection offering are described in greater detail in the subsections that follow.

| Section and Offering Title | Summary Overview | Controls & communications | Contractual considerations |
| --- | --- | --- | --- |
| 3.1 Actively Managed Connections | Dynamic, real-time operating limits signaled by the Company to keep DER within system constraints. | Local equipment for real-time signals & telemetry/monitoring; automated response and fail-safe behavior. | Separate Flex Operating Agreement contractually linked to ISA . |
| 3.2 Scheduled Connections (i.e. Dispatch Limiting Schedule) | Predefined time-based import/export limits without real-time grid feedback. | Local schedule-based controls; limited comms (monitoring/verification & trip as safeguard). | DLS embedded in ISA Special Operating Requirements (no separate agreement). |
| 3.3 Export or Import Limitation Schemes | Reduce facility import/export to avoid upgrades; proceed as standard interconnection at reduced MW. | Fixed limits; no ongoing dispatch signals beyond standard interconnection monitoring/protection. | Standard DG process at reduced MW; subject to Significant vs. Moderate Change rules. |
| 3.4 Flexibility as a Bridge | Temporary flexible operation while required system upgrades are built, then transition to firm (or revised) service. | Controls driven by means of interim flex (i.e. active or scheduled flex) | Interim flex construct until upgrades complete; then transition to permanent ISA terms. |

## Actively Managed Connections

### Offering Overview – what it is and why it exists

Actively Managed Connections are a Flexible Interconnection offering in which customer DER are operated within dynamic, time-varying permissible limits communicated by the Company based on prevailing system conditions and available operating information to ensure the facility remains within distribution system constraints. The purpose of this offering is to enable interconnection that may not be feasible or may be prohibitively expensive or too long of a construction time line under a traditional firm approach—by managing DER operation below full nameplate capacity when needed—while maintaining the foundational do-no-harm requirement (i.e., the DER does not conflict with or exceed thermal, voltage, or protection limits).

This offering is enabled by the concept of dynamic control of DER to enable more customer connections within existing distribution system capability, recognizing that the amount of DER MW that can be injected (or absorbed) varies over time based on system conditions.  While static hosting capacity values reflect conservative planning assumptions, flexible connections may enable incremental interconnection capacity by leveraging time-varying operating margins through active management.  Dynamic operation does not change underlying system limits and does not guarantee availability of capacity at any given time.

In the Flex IX framework, actively managed offerings are designed to support both:

- Flexible Connection use cases, where the Company communicates boundary signals (permissible operating limits) intended to keep the site within system thresholds. A practical example is when the load profile of a circuit approaches its limits due to a solar facility’s interaction with existing EPS conditions, requiring a flexible solar site to lower its output as the circuit approaches a thermal constraint; and

- Potential future Grid Services pathways, where the Company may, subject to separate regulatory approval and program structures, communicate boundary or directional operating preferences that align DER operation with system needs . A practical example occurs when a circuit experiences a load constraint or operates under abnormal conditions, making it advantageous for an energy storage system to discharge and decrease the load on the circuit.

### Operating Model  - how it functions in practice (active vs passive, etc.)

Under an actively managed offering, the facility is expected to respond to Company operating inputs within defined performance parameters established in the applicable operating agreement. Operating inputs are intended to reflect system conditions at an operationally appropriate cadence and are not guaranteed to be continuous, instantaneous, or error-free. As an illustrative example, operating updates may occur on the order of seconds to minutes, depending on the constraint being managed and the capabilities of the communications pathway. The facility may be required to curtail export, limit import, or adjust charging/discharging behavior (for storage) to remain within the permissible operating range established by the Company. The Company does not assume responsibility for optimizing customer operations or ensuring facility availability.

Actively managed offerings may be configured with different operating “envelopes,” depending on the facility type and interconnection need:

- Dual operational envelope (import and export limits) is particularly relevant for ESS and other resources capable of bidirectional power flow.

- Single operational envelope (export only or import only limits) may apply where only one direction of flow drives the applicable system constraint or is being actively managed.

In all cases, the operating model is intended to keep the DER within defined system constraints while enabling interconnection (a) without (or with reduced) traditional upgrades or (b) while waiting for upgrades to be completed. Where used, operational limits may be paired with program structures that reference energy outcomes (e.g., MWh targets) or other attributes, recognizing the distinction between enabling power capacity (MW) versus enabling energy delivery (MWh) through flexible operation.

### Control & Communications (how the grid and DER interact)

Actively managed connections require an operational control and communications pathway between the Company and the DER facility sufficient to (1) communicate permissible operating limits based on available system information and (2) verify DER response through monitoring or telemetry. Communications performance, data latency, and availability may vary and are not guaranteed.

From an operations perspective, actively managed sites are expected to be observable and controllable through Company operating tools through platforms such as EMS / ADMS/ Grid DERMS or Edge DERMS, including confirmation of telemetry, alarms, and control status.

Curtailment may occur through automated logic and/or operator-initiated actions, with DER response verified through available telemetry and manual actions, when needed, documented. Loss of communications or unexpected site behavior will trigger predefined fail-safe actions. These actions may include automatic curtailment through locally programmed control logic that reduces the facility to a predefined safe operating level (potentially a very low MW output) or, where necessary to maintain system reliability, disconnection of the facility.

For sites where a utility-owned point-of-common-coupling recloser is present, the local utility gateway can trip the site if it does not comply. This capability is crucial to creating a fail-safe system and enables the utility to maintain reliability. Such action is taken only as a last resort, when the site does not respond to direct or local communications from the gateway. The setup also allows the company to employ a cost-effective communication method that tolerates communication loss, enabling local equipment to activate fail-safe settings if communication is disrupted.

Reliable and accurate site response is critical to enable dynamic site management. The Company must be able to rely on customer facilities to fully and consistently comply with all operating signals, as these signals are directly tied to maintaining real-time grid safety and system reliability.

Each EDC will publish its own technical requirements for control and communication applicable to flexible interconnection participation.

### Applicability and Use cases (who this works for and/or targets)

Actively managed connections are intended for projects where time-varying operational control can be used to maintain compliance with distribution system limits while enabling interconnection. These offerings are most effective where system constraints are intermittent or condition-dependent, and where static operating limits would be overly restrictive.

Common use cases include:

- Individual projects facing identified distribution constraints (e.g. thermal or protection) that would otherwise require significant upgrades, where real-time curtailment can keep operation within safe thresholds.

- Broader configurations where dynamic operation provides meaningful capacity enablement at locations across the EPS for multiple projects relative to static alternatives (i.e., leveraging time-varying hosting capacity rather than a single conservative limit).

- Storage and hybrid resources where a dual operational envelope (import and export) can be used to manage constraint risk while enabling interconnection and system utilization.

- In general, the opportunity to mitigate voltage impacts through flexibile operation is limited. Flex IX for dynamic voltage control through reactive power adjustment is technically complex, and industry research has generally found that the level of reactive power (and resulting reduction in real-power output) needed at individual customer sites is typically uneconomic.  Therefore, Flex IX offerings will not explicitly focus to address voltage constraints . However, the EDCs may deploy other voltage management solutions where appropriate to accommodate increased DER penetration via Flex IX.

Actively managed connections may also provide a technical foundation for future offerings, subject to separate regulatory review, where DER dispatch supports broader system objectives (grid services), recognizing that the primary objective in this document is safe interconnection under distribution constraints.

### Contractual Considerations (how this fits in the DG process, commitments, targets, etc.)

Actively managed connections are implemented through a Flexible Operating Agreement under which the facility is mandated to dynamically receive Company inputs for permissible import and/or export limits and to curtail as required to remain within the permissible operating range.

From a contractual perspective, the Flexible Operating Agreement is intended to supplement, not modify, the tariff-defined Interconnection Service Agreement (ISA). The ISA remains the governing interconnection agreement and does not require revision; it simply references that the facility is interconnected under a dynamic operating construct. The separate Flex Operating Agreement governs the additional requirements associated with dynamic operation, including control, communications, and curtailment obligations, and explicitly references the associated ISA so that the two agreements are contractually linked and jointly enforceable.

Queue position and tariff fairness principles are preserved under this approach. Electing a flexible interconnection does not change or advance a project’s queue position. Rather, a customer may be able to interconnect sooner because flexible operation can reduce or defer certain upgrades identified through study. Such outcomes do not create rights to firm capacity. Under the tariff, all projects are evaluated to determine what is required to safely interconnect. In a flexible configuration, dynamic controls serve as the mechanism by which the facility operates safely within system limits, effectively replacing physical system modifications with operational and controls-based requirements. This approach is consistent with both the spirit and intent of the tariff, while enabling timely and safe interconnection.

Per Section X, each EDC will develop and publish a template flexible interconnection operating agreement as part of its implementation plan.

### Benefits & Tradeoffs (why someone would choose this)

Benefits. Actively managed connections can:

- Enable interconnection while adhering to the foundational do-no-harm requirement by keeping DER operation within system thermal, voltage, and protection constraints.

- Leverage dynamic hosting capacity to unlock greater feasible MW injection/absorption than static limits would allow, by managing DER operation in response to system conditions.

- Provide an extensible technical foundation for future grid service capabilities in which the Company monitors real-time conditions and actively signals DER to help mitigate grid issues.

Tradeoffs. Actively managed connections require:

- Greater operational and integration complexity than passive/scheduled approaches due to the need for real-time signaling, telemetry, and operational oversight.

- Customer acceptance of curtailment risk and mandatory compliance with permissible operating limits communicated by the Company.

- Dependable site controls and communications, with the understanding that loss of communications or non-compliance may result in conservative default operation or disconnection.

Customers acknowledge that there may be periods when the system is unavailable. Although not guaranteed, it is typical for restrictions to depend on grid conditions (e.g., sites may be limited in exporting or generating during periods of excess grid generation and restricted in importing or charging when the system is heavily loaded).

## Scheduled (i.e. Timed) Connections

### Offering Overview – what it is and why it exists

Scheduled connections are a Flexible Interconnection offering in which customer facilities operate under predefined, time-based operating limits rather than real-time grid feedback. These limits are established through a Dispatch Limiting Schedule (DLS) that defines permissible import and/or export capacity by time of day, season, or other agreed-upon operating periods.

The purpose of this offering is to enable interconnection where distribution system constraints are predictable and recurring, such that safe operation can be maintained through scheduled limitations without the need for continuous, real-time control. As with all flexible interconnection offerings, scheduled connections are designed to ensure that DER operation does not exceed applicable system limits and maintains the foundational do-no-harm requirement.

### Operating Model  - how functions in practice (active vs passive, etc)

Under a scheduled connection, the facility operates according to a fixed curtailment schedule that is defined in advance and does not vary dynamically based on real-time grid conditions. The Dispatch Limiting Schedule specifies the maximum allowable import and/or export capacity during defined time blocks, such as by season.

The customer is responsible for configuring and operating their facility to comply with the Dispatch Limiting Schedule at all times. Unlike actively managed connections, the Company does not continuously adjust operating limits in response to real-time system conditions and does not provide operational direction outside the predefined schedule. System protection is achieved through predefined operating limits established by the Company based on engineering studies of historical operating conditions on the area electric power system. The safe operating limits are documented in the Dispatch Limiting Schedule and define the permissible operating range for the facility.

Scheduled connections may apply to both single(import-only or export-only) and dual operating envelopes, depending on the facility configuration and the nature of the underlying constraint.

### Control & Communications (how the grid and DER interact)

Scheduled connections rely primarily on local control logic at the customer facility to enforce compliance with the Dispatch Limiting Schedule. Real-time dispatch signals from the Company are not required for normal operation under this offering.

While telemetry and monitoring may be required to verify compliance, the operational control model is intentionally simpler than that of actively managed connections. The Dispatch Limiting Schedule is defined as part of the interconnection documentation.  Customer-owned controls are responsible for implementing the schedule and commanding the facility to curtail or otherwise adjust operation as required.  Company-owned controls or protective devices would additionally be installed as a safeguard to ensure that, if the facility operates outside the defined schedule boundaries, fail-safe actions can be taken—most commonly resulting in disconnection of the site from the electric power system.

### Applicability and Use cases (who this works for and/or targets)

Scheduled connections are best suited for situations where:

- Distribution system constraints are time-dependent but predictable, such as seasonal thermal limitations or recurring peak-period constraints.

- Real-time dynamic control is not necessary to safely manage system impacts.

- A simpler operating construct is preferred, with clearly defined curtailment periods known in advance.

This offering can be particularly effective where curtailment is expected to occur during limited, well-defined periods and where customers can reasonably plan facility operations around scheduled restrictions. Scheduled connections are not intended for locations where constraints are highly variable or materially influenced by real-time operating conditions.

### Contractual Considerations (how this fits in the DG process, commitments, targets, etc.)

Because scheduled operation relies on pre-defined, time-based limits rather than dynamic, real-time control, the operating construct is far less complex than actively managed connections and does not require a separate operating agreement.  The Dispatch Limiting Schedule is incorporated directly into the Special Operating Requirements section of the Interconnection Service Agreement (ISA). The ISA remains the sole governing agreement, with the Dispatch Limiting Schedule establishing the specific operating constraints under which the facility is permitted to interconnect and operate.

Queue position and tariff fairness principles are preserved. Electing a scheduled connection does not change a project’s queue position. A customer may be able to interconnect sooner because scheduled operating limits can reduce or eliminate the need for traditional system upgrades. Under this construct,safe interconnection is achieved through predefined operating limits rather than physical system modifications, consistent with the intent of the tariff.

### Benefits & Tradeoffs (why someone would choose this)

Benefits:

- Enable interconnection without the complexity of real-time control or continuous utility signaling.

- Provide operational certainty through clearly defined curtailment periods established in advance.

- Can reduce or eliminate the need for physical system upgrades where constraints are predictable and recurring.

Tradeoffs:

- Do not respond to real-time grid conditions and therefore require more conservative operating limits.

- May result in curtailment during periods when the system could otherwise accommodate additional DER operation.

- Do not directly enable real-time grid services or dynamic system support capabilities.

## Flexibility as a Bridge

### Offering Overview – what it is and why it exists

Flexibility as a Bridge connections may be used when a standard system upgrade is planned but may take longer to complete than is compatible with a project’s desired in-service timeline. This approach works best if the cost of the required system upgrade—such as adding a substation transformer or reconductoring a lengthy three-phase line—is manageable, but the construction timeline poses challenges. This offering enables facilities, at the Company’s discretion. to interconnect and operate in a limited manner during the upgrade construction period, provided that such operation can be accommodated safely within the constraints of the existing power system. The primary purpose is to allow interim operation within clearly defined limits  while major system improvements are underway. Bridge arrangements are temporary, conditional, and not guaranteed to be available in all cases.  Facilities may begin operating prior to completion of system upgrades only within the safe operating limits of the existing power system. Once all required upgrades are complete, the facility may transition to firm or continued flexible interconnection with a curtailment estimate, as applicable, depending on the project's design and intended operation.

### Operating Model  - how functions in practice (active vs passive, etc)

Under this offering, the facility initially interconnects under flexible operating limits that manage identified system constraints during the upgrade construction period. This is achieved through an actively managed or scheduled flexible connection, as described elsewhere in this document.

In some cases, it may be possible to incrementally increase the facility’s permissible operating limits as upgrades progress; however, this capability is situationally dependent, subject to Company discretion, and may not be available in all circumstances. In many cases, the facility is expected to remain subject to the full flexible operating limits throughout the bridge period and to transition, in full, to firm operation only after all required system upgrades are complete and operational.

Throughout the upgrade period, the facility is required to comply with the applicable flexible operating limits, which remain in effect until the Company confirms that the required system upgrades are complete and that the facility has met all conditions for transition to firm operation or continued flexible operation, as applicable.

Both actively managed and scheduled connections offerings may be used as bridge configurations where appropriate, recognizing that the selected approach must be operationally feasible and administratively manageable.

### Control & Communications (how the grid and DER interact)

Control and communications requirements under this offering are consistent with the type of flexible operation used during the bridge period. Depending on the project, this may include:

- Dynamic operating limits communicated through Company systems;

- Predefined operating schedules; or

- A combination of both, where appropriate.

Refer to the applicable offering sections in this document for additional detail. In general, customer-owned controls are responsible for implementing the applicable operating limits and commanding the facility to adjust output accordingly. Company-owned monitoring, protection, or local control mechanisms may be used as safeguards to ensure that, if the facility operates outside approved limits during the bridge period, fail-safe actions can be taken to protect the electric power system.

As system upgrades are completed and operational limits are adjusted, control settings and operating requirements are updated accordingly to reflect the new permissible operating range.

### Applicability and Use cases (who this works for and/or targets)

The Flex as a Bridge offering is most appropriate where:

- A project requires distribution system upgrades to achieve firm interconnection;

- Those upgrades are expected to take a meaningful amount of time to design and construct; and

- Existing system conditions can support limited or controlled operation prior to upgrade completion.

Common use cases include situations where a project would otherwise remain idle while awaiting construction of network upgrades, despite the ability to safely interconnect and operate at reduced capacity in the interim. This would also be appropriate for situations in which a project faces a deadline for being placed in service (e.g., Investment Tax Credit) that is likely beyond the timeline for the full upgrade to be completed. Bridge arrangements are evaluated on a case-by-case basis and are not intended to accommodate all project timelines or external commercial considerations.

### Contractual Considerations (how this fits in the DG process, commitments, targets, etc)

Under this offering, the facility operates under a flexible interconnection arrangement until the required system upgrades are completed and placed in service. Once those upgrades are complete, the facility may transition from the flexible operating construct to full firm (non-flex) operation, subject to confirmation that all tariff-defined requirements have been met.

In some cases, it may be possible to incrementally increase the facility’s permissible operating limits as upgrades progress; however, this capability is situationally dependent and may not be available in all circumstances. In many cases, the facility is expected to remain subject to the full flexible operating limits throughout the bridge period and then transition only after all system upgrades are complete and operational.

Importantly, this offering does not alter queue position or tariff sequencing. The underlying firm interconnection remains governed by the tariff-defined interconnection process and upgrade requirements. The bridge arrangement simply allows interim operation by substituting temporary operational controls for physical system modifications until those modifications are completed.

### Benefits & Tradeoffs (why someone would choose this)

Benefits:

- Enables earlier, limited interconnection and operation while required system upgrades are underway.

- Reduces customer idle time and improves project economics during the construction period where interim operation is feasible.

- Maintains system safety by using operational controls as a temporary measure during upgrade construction.

Tradeoffs:

- Is explicitly temporary and does not eliminate or reduce the scope of required system upgrades.

- Subjects the facility to flexible operating limits and potentially higher curtailment during the bridge period.

- Involves additional operational and integration complexity and costs due to the need to study and implement both a flexible solution (though temporary) and an eventual firm solution.

- Requires careful coordination to transition from flexible operation to firm service once upgrades are complete.

## Export or Import Limitation Schemes (Permanent Derating)

In some cases, a customer may determine that permanently reducing the size of their facility is preferable to triggering distribution system upgrades. Under this construct, a project may elect, subject to Company review and approval, to permanently derate its export and/or import capability to a level that avoids the need for certain system modifications. Once this election is approved, the reduced capacity becomes the project’s effective interconnection size and is treated as such for all interconnection purposes. The project then proceeds as a standard DG interconnection at the revised MW level, with no flexible operating construct required. From a process perspective, this is accomplished by revising the facility size on the interconnection application, after which the project is evaluated and interconnected consistent with the tariff-defined requirements applicable to that capacity.

While permanent derating represents a reduction in site size, it does not necessarily result in reduced system impacts in all cases. Changes in facility size can affect distribution system modeling assumptions, including DER contributions used to determine upgrade needs, protection coordination, and voltage performance. In some circumstances, a reduction in one customer’s project size may shift upgrade cost responsibility to a subsequent customer that would not otherwise have been obligated to pay, or may cause certain costs to move to rate base, affecting all customers. Additionally, site size reductions may introduce or alter protection or voltage considerations that require further evaluation.

Acknowledging these potential impacts, permanent derating is permitted only subject to the Significant vs. Moderate Change provisions of the DG Interconnection Tariff. If the proposed derating has the potential to materially impact other customers, system upgrade cost allocation, or rate base—or if such impacts are definitively identified—the change will be deemed a Significant Change. In those cases, the customer would be required to withdraw the existing application and submit a new interconnection application at the reduced size, receiving a new queue position consistent with tariff requirements.

# Flex IX Studies & Curtailment Strategy

## Actively Managed Connections

Curtailment is a core component of Actively Managed Connections and is the primary mechanism used to ensure that distributed energy resources (DERs) operate safely within distribution system limits. By limiting import and/or export during the hours of constrained system conditions, curtailment enables certain projects to interconnect more quickly or at lower cost than would be possible under a fully firm construct, while maintaining the foundational needs of safety and reliability that are paramount for the electric power system.

There are three components to a curtailment strategy for actively managed connections:

- Curtailment Target: The level of annual energy curtailment (MWh) that a customer’s DER facility is expected, but not guaranteed, to experience under normal system conditions and that is generally considered economically feasible for participation in a flexible interconnection construct.

- Curtailment Allocation Methodology: The one or more methodologies that governs how curtailment is allocated among Flex IX projects when distribution system limits are reached (i.e., which facilities are curtailed and when at a given location).

- Curtailment Study: The study methodology and the associated inputs, assumptions and outputs used to estimate expected curtailment for a given customer and/or location for planning and screening purposes. Curtailment studies provide indicative estimates only and do not represent operational guarantees.

Below, each component is described in further detail, along with the corresponding determinations applied across actively managed offerings by the EDCs.

### Curtailment Target

Offering Determination & Reasoning: All EDCs will leverage a planning target of 5% of annual MWh curtailment for each facility, which will be applied to the first curtailment group under the pro-rata curtailment tranche. This target is informed by industry experience with other active management flexible interconnection programs in Illinois and New York, as well as validation of the curtailment target by stakeholders.

To support continued flexible operation throughout the system upgrade lifecycle, both the study methodology and real-time operational thresholds are designed to allow ongoing project operation within defined limits. In some circumstances, projects may be allowed to interconnect—where traditional firm capacity analyses would not otherwise permit—by demonstrating the ability to dynamically and promptly respond to system conditions while remaining within established distribution system limits

As part of this framework, new Flex IX applications will be studied and offered a Flex IX agreement if they are generally expected to meet a non-binding target curtailment level based on standard planning criteria and based on what is economically feasible for customers. Where the study determines that this target is unlikely to be met or is deemed infeasible, additional curtailment targets may be considered for projects willing to accept higher levels of curtailment. Future system upgrades are not guaranteed for flexible projects, and flexible project capacity is not assumed or relied upon in long-term system planning criteria for future system buildout. Study agreements for flexible interconnection projects are expected to reflect these principles through appropriate terms and conditions.

The following provides additional context on curtailment targets and offerings:

- Flexible Interconnection may be offered for projects where the expected level of curtailment does not reduce total annual energy production below approximately 95 percent (i.e 5% curtailment target) of the facility’s normal operation. For purposes of this evaluation, “normal operation” assumes rational dispatch of the facility in alignment with system needs and prevailing market signals—such as ISO market prices, Clean Peak incentives, ConnectedSolutions events, and other demand-driven programs-—such that the facility is not contributing to distribution system peak conditions. Under this construct, flexibility enables projects to interconnect efficiently while maintaining high utilization of their expected annual energy output and supporting overall system reliability.

- The contractual language will specify that the planning target will be to curtail or limit 5% of the annual energy (MWh). Over time, changes to the system load profile—including new firm customer load or generation—may affect when the system approaches its operating limits and, therefore, when curtailment is required. Flexible projects are studied using conservative assumptions that account for these future system changes, and curtailment estimates are developed accordingly, as described in Section 5.0.  New flexible interconnections are the most likely source of incremental curtailment, and contractual protections would be provided to prevent additional flexible projects from interconnecting once observed conditions or subsequent flex study results indicate that the 5% curtailment target for an existing flexible project would be exceeded..

- For study purposes, system impacts are evaluated at 75% of the applicable Electric Power System (EPS) rating, while operational curtailment is applied at a higher threshold consistent with EDC planning criteria. This approach provides operational flexibility while maximizing confidence that the non-binding annual energy curtailment target can be met.

### Curtailment Allocation Methodology

Offering Determination & Reasoning: All the EDCs will leverage the pro-rata methodology for the first curtailment group and TBD methodology for the second curtailment group. The merits of both Last-In-First-Out (LIFO) and pro-rata curtailment allocation methodologies were evaluated by the Flex IX IIRG stakeholder group. While LIFO offers simplicity and increased curtailment certainty for early-moving projects, stakeholders determined that leveraging the pro-rata approach for the first tranche better supports the objectives of equity, scalability, and efficient use of existing distribution infrastructure. By distributing curtailment across all similarly situated Flex IX projects contributing to a constraint, pro-rata curtailment avoids structural winners and losers, enables higher overall DER penetration, and provides a more predictable and transparent framework as flexible participation grows. - Maximize safe DER integration without immediate construction: Pro rata enables higher overall DER penetration before curtailment becomes prohibitive. - Maintain queue fairness, while offering optional flexibility: Queue order remains intact for studies and firm upgrades; pro rata only governs how voluntary Flex participants share operational risk. - Avoid structural winners and losers: Flex is intended as a shared, transitional solution—not a mechanism that permanently advantages early projects at the expense of later ones. - Scale operationally: As Flex participation grows, pro rata is simpler to administer and explain than order-based curtailment tied to historic queue positions. [Add logic for second tranche] These curtailment allocation methodologies are generally acknowledged in industry across the country (e.g. pro-rata and last-in-first-out (LIFO) methodologies). The sections below outline how each methodology would work in practice and the differences in allocation methodologies.

#### Pro-rata

The Pro-Rata curtailment allocation approach is one in which all Flex IX projects contributing to a binding system constraint share curtailment proportionally, based on their relative export or operating level at the time the constraint occurs. Rather than concentrating curtailment on a single project, prorata allocation distributes operational impacts across all participating flexible resources, ensuring that similarly situated projects are treated consistently. This approach supports equitable risk sharing, enables greater overall DER integration within existing infrastructure, and aligns with queue fairness principles by preserving study order while allocating curtailment based on -realtime syste-m contribution rather than interconnection sequence.

Benefits:

- Equitable risk sharing: Curtailment impacts are spread across all flexible participants rather than concentrated on the newest project.

- Supports greater hosting capacity: By sharing curtailment, more DER can interconnect before curtailment levels become uneconomic overall.

- Consistent with “treat similarly situated customers the same”: Aligns with stated Flex queue fairness principles and DG tariff philosophy.

- Avoids tracking interconnection order operationally: Curtailment logic does not depend on queue position, simplifying real time control as Flex scales.

- Clearer customer expectations: Curtailment can be modeled and disclosed (e.g., 5% annual target), enabling informed opt in decisions.

Tradeoffs:

- Less protection for early movers: Early projects no longer receive near firm service by default.

- Requires curtailment tolerance assumptions: Financial viability depends on developers accepting defined curtailment targets (e.g., 2.5–10%), which must be clearly communicated and standardized.

- Perceived reduction in “queue value”: Some stakeholders may view pro rata as weakening the benefit of early queue position, even though queue order is still preserved for studies and firm upgrades.

Placeholder Figure from Illinois Workshop Deck – To be updated

#### LIFO

The Last-In--First---Out (LIFO) curtailment allocation approach is one in which curtailment is applied sequentially based on interconnection order, with the most recently interconnected Flex IX project curtailed first when system limits are reached. Under this method, earlier projects experience little or no curtailment until later projects have been fully curtailed. LIFO provides a clear and easily understood prioritization framework and can offer greater curtailment certainty for early-moving- projects. However, because curtailment is concentrated on newer projects, this approach can limit the total amount of flexible capacity that can be accommodated on a constrained asset and may create disproportionate curtailment risk for later participants.

Benefits:

- High certainty for early movers: First projects see minimal curtailment exposure, which can improve project bankability for those early in the queue.

- Simple conceptually: Easy to explain and historically used in some interconnection frameworks.

Tradeoffs:

- Concentrates risk on later projects: Newer projects can face severe or even total curtailment, making Flex uneconomic for them.

- Windfall for early projects: Early projects may receive firm like service without paying for network upgrades, raising equity concerns.

- Limits total DER penetration: Once later projects face excessive curtailment, additional Flex connections become infeasible—even if modest shared curtailment could accommodate more capacity.

- Harder to align with queue fairness principles: Risk allocation is driven by timing rather than system impact or shared benefit, which has been a recurring concern in Flex workshops and queue fairness discussions.

Placeholder Figure from Illinois Workshop Deck – To be updated

#### Implementation of Curtailment Tranches

Curtailment will be structured in discrete tranches to support operational and administrative scalability. Tranches will increase in a doubling sequence (e.g., 5 percent, 10 percent, 20 percent), rather than incremental adjustments, to simplify implementation, maintain transparency for customers, and ensure consistent treatment as additional flexible projects interconnect.

- At enrollment/interconnection, each project is assigned a tranche based on study results and expected curtailment, considering the project and other projects in the queue.

- Operationally, the objective is to manage constraints such that projects can generally remain within their assigned annual curtailment target (noting targets are non-binding and actual outcomes vary with system conditions).

- When a constraint binds, curtailment is applied first to projects in higher-curtailment tranches (e.g., 10% tranche before 5% tranche), then expands to lower-curtailment tranches as system loading/constraint severity increases.

- Doubling tranches are intentionally “nested” (e.g., any time the 5% tranche is curtailed, the 10% tranche is also curtailed), which reduces the number of distinct curtailment groups the EDC must manage.

- The specific “order of operations” is vendor/platform dependent; while finer tranche increments (e.g., 5% steps) may be feasible in theory, they can increase control and coordination complexity and may not be supported by all software implementations.

- Contract language and operational job aids will document tranche selection, tranche definitions, and curtailment application rules to ensure consistent implementation and customer transparency.

### Curtailment Study Analyses

Offering Determination & Reasoning: Several determinations were made regarding curtailment studies as described below. - Inputs: EDCs will use standardized DER profiles for solar, solar + storage and standalone storage developed in collaboration with industry. Standardized profiles will allow EDCs to conduct curtailment studies and estimate the additional DERs that can be interconnected in a streamlined and accelerated manner. Standardized profiles will be included as part of the implementation plans described in Section V. - Outputs: Data transparency was identified as critical to support project financing. Accordingly, EDCs will provide the following information as part of the curtailment study: - Study results, including the estimated curtailment factor, the days the facility is expected to not be able to fully operate, latest peak feeder loading, and system modifications necessary to interconnect the Flex IX project with associated cost estimates - Up to three (3) years of historical feeder data - TBD other data - EDCs remain the sole entity responsible for performing and validating interconnection and curtailment studies, and study results provided by the EDC constitute the authoritative basis for interconnection determinations and operating requirements. - Methodology: Analysis uses an 8,760-hour methodology and evaluates system impacts at 75 percent of the applicable system rating to determine whether flexible operation is viable within the curtailment target - Study Template: EDCs will publish a standardized curtailment study template (see Section V for details)

#### EDC Curtailment Study

Flexible connection studies assess whether a project can operate safely within existing distribution system limits using standardized, transparent methodologies. During the study phase, engineers identify thermal, voltage, and protection constraints and evaluate whether controlled operation below full nameplate output can mitigate those impacts without requiring major system upgrades. Study methodologies and operating thresholds are designed to support continued project operation within defined limits over time, while providing customers with clear, non-binding curtailment expectations and well defined operating envelopes to improve predictability for project economics.  Key study considerations include:

- Consistent engineering treatment: All projects electing a Flexible or Grid Services construct are evaluated using the same underlying power flow, voltage, and protection analyses as firm interconnections, ensuring safety and reliability are not compromised.

- Identification of binding constraints: Studies explicitly identify system elements that drive interconnection limitations and distinguish between impacts that can be mitigated through dynamic control versus those requiring physical upgrades.

- Curtailment quantification: An 8,760-hour analysis is used to estimate the magnitude, frequency, and duration of expected curtailment, expressed on an annual MWh basis to support customer decision-making.

- Defined operating envelopes: Study results inform the permissible import and/or export operating ranges that would apply under normal and constrained conditions.

- Non-binding estimates: Curtailment results are provided as planning estimates to support informed customer choice and are not guarantees of future operational outcomes.

- Separation from long-term planning: Flexible capacity enabled through curtailment is not assumed in long-term system planning or future firm capacity allocations.

For Flex IX evaluations, the study focuses on the most restrictive system constraint and assesses the curtailment impact to the subject facility to address their interconnection through controlled operation rather than physical upgrades. Initial analysis uses an 8,760-hour methodology and evaluates system impacts at 75 percent of the applicable system rating to determine whether flexible operation is viable within the curtailment target.

This approach balances near-term operational flexibility with long-term system planning needs by:

- Ensuring safety and reliability through conservative study assumptions and clearly defined operating limits.

- Using standardized study analysis to maximize confidence that non-binding annual curtailment targets can be met.

- Allowing future system planning to assume full real-time system capability, without requiring flexible projects to be explicitly modeled or reserved as firm capacity

Representative load curves developed by the EDC and a representative generation profile agreed upon by the Flex IX stakeholder group are used in the 8,760-hour curtailment analyses to ensure transparent, consistent, and repeatable study results. These standardized inputs provide a common baseline for evaluating system constraints and estimating expected curtailment across projects, while avoiding project--specific dispatch assumptions that could skew results. By applying the same load and generation profiles across studies, the analysis establishes clear expectations for customers and stakeholders and supports comparability of curtailment outcomes as additional- Flex IX projects are evaluated over time.

As part of the study results, a curtailment summary will be provided that confirms the facility’s appropriate curtailment tranche, and if the site is expected to achieve the curtailment target, which would make it a good candidate for Flex IX.  In addition, three (3) prior years of readily available historical EPS specific data is shared with the customer to support independent financial due diligence.  Available data will be shared to the extent feasible, noting:

- Data may reflect periods of abnormal system conditions, including low loading or saturation of CTs, operational maintenance or switching activities, system outages, communications failures, IT system maintenance, outages, data loss or other activities.

- Data is provided as an average of historized data points captured for each hour.  Where hourly data is not available (“N/A”) it indicates no measurement was historized.  EDCs will not provide interpolated values.

#### ASO Study

TBD

# Equipment and Design

Flexible connections rely on a combination of customer-owned controls and utility owned protection and communication equipment to ensure a facility can operate safely within grid limits. At the center of this setup is the DER gateway, typically integrated with utility owned equipment—such as a point of common coupling (PCC) recloser—which provides a critical fail safe function. This gateway allows the utility to trip a site if it does not comply with required operating limits, ensuring system reliability during abnormal or constrained grid conditions. The Company also deploys site limiting equipment, communication interfaces, and monitoring systems as needed to support dynamic or scheduled operating requirements.

Communication methods vary according to the type of flexible connection, but all require reliable pathways for conveying permissible operating limits and verifying DER response.

## Actively Managed Connections

In actively managed configurations the utility uses platforms to communicate real time operating limits and monitor telemetry. These signals instruct the customer’s control system to curtail import or export as needed. If communications fail, locally programmed logic automatically curtails the facility to a safe output level, with the DER gateway providing an additional layer of protection. For scheduled (timed) connections, customers follow predefined operating schedules, using local control logic while the utility maintains monitoring and the ability to disconnect the site if it exceeds permitted limits.

To participate in flexible interconnection, customers must install and maintain all on site controls and equipment required to receive and respond to operating signals. They are responsible for ensuring their equipment can react promptly to utility signals—sometimes within seconds—and for maintaining equipment in accordance with safety and testing requirements. Experience shows that reliable customer controls, robust communication pathways, and clear operational coordination are essential to successful flexible connections. Lessons learned emphasize the importance of fail safe site behavior, consistent telemetry, and customer readiness to operate under dynamic limits, enabling safe and scalable integration of distributed resources

INSERT FIGURE HERE

Figure 1:  Illustrative Example of Flexible Connection Equipment

The customer experience including curtailment notification and reporting is also important to provide transparency around when and how often facilities are being curtailed.

# Alignment to DG Interconnection Tariff

Offering Determination & Reasoning: Flex IX is intended to operate fully within the existing Distributed Generation interconnection tariff framework and does not replace, bypass, or override any tariff-defined processes or requirements. Under this framework, flexibility serves as a substitute for certain system modifications that would otherwise be required to accommodate interconnection—using controlled operation to manage system constraints in lieu of constructing physical upgrades, while maintaining safety and reliability. TBD: - Should Flex IX be memorialized in a tariff? - If so, should this modify an existing tariff or require a new tariff? - If so, can Flex IX move forward under existing rules while a tariff is reviewed for approval?

The following overview highlights the key stages of the DG interconnection process where Flex IX decisions or related process dependencies must be considered. These stages do not alter or replace the existing DG process, but clarify where Flex IX interfaces with established activities such as screening, study, contracting, construction, and operations. Clearly identifying these touchpoints supports timely and predictable project outcomes while preserving queue fairness, managing customer expectations, and maintaining consistency with tariff and reliability requirements.

## DG Interconnection Process Alignment

The following figure identifies specific points in the interconnection process where the customer would be provided the opportunity to elect to have the project be considered as Flex IX.  These include:

  - Application Submission

  - System Impact Study start

  - Preliminary Assessment

  - ISA delivery (limited to flex-as-a-bridge offering only)

To support timely interconnection and efficient queue management, Flex IX elections are made at defined decision points. Once a customer elects to proceed with a Flexible IX option, that election is non-reversible for the remainder of the process. Similarly, if flexibility is not elected the customer will not be permitted to shift a project to a flex offering outside of these defined decision points. This establishes a structured approach that provides clarity and predictability for all customers, reduces queue churn, and ensures that each project’s election can be reliably incorporated into the base case assumptions used for subsequent applications, as well as for EDC planning and operational processes.

Figure XX:  Flex Offering Decision Points

The Flex IX process is designed to operate within the existing DG Interconnection Tariff without changing fundamental queue principles and to preserve the queue order. While Flex may enable faster interconnection in certain circumstances due to potential study efficiencies and avoidance of some significant infrastructure construction, it does not alter queue position rules, and similarly situated customers will continue to be treated consistently.

Flex projects are not exempt from engineering review requirements and are expected to follow the standardized project progression pathways identified in the DG Interconnection tariff in its entirety. Through the course of engineering review as it appears in the existing tariff processes, the EDCs will be able to provide the information identified in Section 5 as part of the resultant study report.

Curtailment allocation methodologies will be applied as described in Section 4 and communicated to the customer as part of the study results. These curtailment estimates are intended to inform the customer’s assessment and ultimate decision on project feasibility as they consider the impacts on the overall project design and operation. Consideration of curtailment does not alter or affect alignment with the existing DG Interconnection Tariff.

## Group Studies

Group Studies present a unique situation with additional nuance on how Flex IX may be applied.  The following summarizes a potential approach:

- Projects participating in an active Group Study may be offered the option to be Group Exempt and proceed toward interconnection in parallel with the Group, provided they are 1 MW or less and connect flexibly. This is the only scenario in which Flex would be offered to a Group Study participant.

- Group Exempt Flex projects would proceed in parallel, outside of the Group Study timeline, and would be evaluated against existing grid conditions under the assumption that no system modifications are required. These projects would be subject to the same firm injection timelines as a standard individual System Impact Study. If Flex site analysis identifies system impacts, system modifications would only be pursued if they do not conflict with the Group Study solution.  If any part of the flex solution for the project conflicts with the Group Study solution, the Group Study solutions takes precedent.  The Flex IX project is expected to curtail to avoid constraints.  -.

- Projects that are not part of an existing Group Study and are therefore queued behind the Group may voluntarily elect to move forward using Flex in a similar manner. Projects behind the Group may proceed with Flex once the Distribution solution for the Group has been identified, which may occur prior to the start of any Group-related ASO studies. This approach ensures that base cases can be confidently established for parallel study paths. However, if area characteristics indicate that parallel processing would conflict with or disrupt Group Study progress, those projects would not be permitted to move forward in parallel.

- Additional considerations include the requirement that projects must either be studied as Flex or remain within the Group as firm; studying a single project simultaneously as both Flex and firm is not permitted. Projects seeking Flex treatment within Group Study areas must first satisfy the basic Flex eligibility screening criteria, as defined in the process documentation.

# Financing & Risk Mitigation

Flexible interconnection introduces new factors for DER project developers to consider when financing a project including lower DER output and potentially higher curtailment than the expected target. New strategies are needed to support project financing and make flexible interconnection a viable option for DER developers.

## Actively Managed Connections

Offering Determination & Reasoning: - Two non-compensation strategies: - Data sharing (See Section 4.1.3 for details) - Conservative study assumptions (See Section 4.1.3 for details)

Actively managed connections, while studied to target a maximum curtailment percentage, cannot be guaranteed to not exceed this target as the EDCs cannot predict the real-time conditions of the system. This creates challenges for project financing as financiers perceive increased risk due to the lack of guarantees.  A set of strategies are required to provide developers and their financiers with increased certainty regarding flexible interconnection projects. There are generally two categories of financing strategies: (1) non-compensation and (2) compensation strategies.

Non-compensation strategies entail approaches that do not compensate projects if curtailment exceeds the estimated target but provides more certainty to developers and financiers that this scenario will not occur. Two key non-compensation strategies have been identified:

- Data Sharing: The sharing of granular data including both the inputs and results of the curtailment studies will enable developers and financiers to conduct their own independent analysis to assess the risk of curtailment. This approach is aligned with similar implementations in New York and Illinois.

- Conservative Study Assumptions: By adopting more conservative planning assumptions as part of the curtailment study, the EDCs can add a certain “margin” to the analysis further reducing the risk that the facility would be curtailed. Per Section XX, the curtailment study evaluates system impacts at 75 percent of the applicable system rating while the actual flexible interconnection would not curtail until the system reaches 95 percent of the system rating.

Compensation strategies - TBD

# Post-upgrade Processes

For specific use cases, flexible interconnection serves the purpose of connecting additional DERs in a constrained area until the dynamic limits at a given location are reached. If an EDC decides to upgrade this location once dynamic limits are reached, this raises important questions on how this upgrade impacts the flexible interconnection and future customers as well as who pays for the upgrade.

Once an upgrade is complete, Flex IX customers are expected to temporarily benefit from the upgrades as Flex IX customers are expected to be curtailed less as additional capacity becomes available. However, Flex IX customers are unlikely to be incentivized to contribute to the upgrade as these projects have already been financed under Flex IX. Moreover, Flex IX customers would still be curtailed prior to an upgrade and would be the first facilities to be curtailed once firm limits are reached in an upgraded area. The subgroup will continue to evaluate these factors to determine an equitable path forward once upgrades are complete in Flex IX areas.

# Implementation Plan

A separate companion implementation plan(s) will be developed for the EDCs detailing a near and long-term roadmap on how flex IX will be implemented within each of their service territories. As part of this plan, several documents will be included to provide customers guidance on participating in each EDC’s flexible interconnection offerings:

- Curtailment Study Template

- Flex IX Operating Agreement

- Technical & Site Requirements

***************************

See draft outline below for implementation plan (still in-progress)

- DERMS deployment. Locations and estimated MWs enabled

  - Want general agreement on how overall program works and how we would generaly scale

    - Things would vary based on EDC technology deployment and specific constraints

    - Want to address timelines for both EDCs and developers (i.e bridge to wires for ITC)

  - Key steps

    - Identify areas with constraints (substation/downstream feeders, feeders etc.)

    - Prioritize locations based on specific criteria

    - Use this prioritization to inform derms deployments (and other criteria)

    - Conduct curtailment studies and make flex IX offers

      - Is there still a benefit of making offers sooner for the ITC even if DERMS won’t be ready immediately upon completion of construction?

  - National Grid

    - Existing Pilot

      - What are the current capabilities and limits of what the current DERMS can do?

      - How can the pilot evolve to incorporate insights from the workshop?

      - Can we leverage this to target specific constrained areas which the new DERMS can build upon?

    - Future DERMS Deployment

      - When can DERMS realistically be ready to operationalize flex IX? Can this be accelerated?

      - When does it make sense to conduct studies and make offers to align with DERMS deployment?

  - Eversource

    - Pilots/Demonstrations

      - Where can we begin pilots/demonstrations and do we need DERMS to do those?

    - Future DERMS Deployment

      - Where is DERMS currently being prioritized and why? Can the locational deployment be aligned with where flex IX is needed?

      - When can DERMS be activated at specific locations and how can we coordinate that with conducting studies/making offers?

- Program Launch & Communication

  - EDCs will establish dedicated Flex IX website hubs with plans, documentation and areas  where flex IX is available

  - Other places to update

    - HC maps

    - Interconnection app process

  - How to communicate offers/expansions to specific developers/facilities

    - Email IIRG listserv?

    - Make individual offers to those in queue?

- Modified or new tariff

Non inverter based resources such as load or electric vehicles will be addressed in future iterations of this document, or through separate processes

All guidance documents will be standardized across EDCs where possible.