| UST Owner/Operator Requirements: - Impressed current cathodic protection systems shall be inspected at the following frequency: Standard; Testing Frequency. Acceptable system operating voltage and amperage ranges (a) determined by corrosion expert and (b) affixed to each rectifier. Inspected in accordance with: - Manufacturer’s specifications; - NACE Test Method: TM0101-2012 (Tank); or - NACE Test Method: TM0497-2012 (Piping); Every 60 days.. Voltage and amperage reading outside the acceptable range is considered a failed test.; Within 5 days of a failed test, the O/O shall retain a corrosion expert to determine the cause of the failed test and repair or replace the system within 120 days of the date of the failed test.. - Repaired/replaced systems shall be retested within 60 days of repair or excavation at the UST system. - If repair/replacement is not completed within 120 days of the date of the failed test, the UST system shall be taken temporarily out of service, removed or closed in-place, if applicable. - All cathodic testing must be performed by a cathodic protection tester certified by: NACE, The Steel Tank Institute, or the International Code Council. - All records in a hard copy or electronic log shall be maintained for a minimum of four years, including corrosion expert’s determination of cause of system failure. |
| --- |
| Facility Name |  |  |  |  | UST ID# |  |
| Acceptable Voltage Range |  |  | Acceptable Amperage Range |  |  |  |
| Inspection Date: |  |  |  |  |  |  |
| Voltage Reading |  |  |  | Pass |  | Fail |
| Amperage Reading |  |  |  | Pass |  | Fail |
| If voltage and amperage readings are outside their acceptable ranges it is deemed a failed test, and the cathodic protection system must be repaired or replaced within 120 days of the failed test. Date cathodic protection system repaired or replaced: |  |  |  |  |  |  |
| Date repaired or replaced cathodic protection system retested (w/in 60 days of repair/replacement): |  |  |  |  |  |  |
| Inspection Date: |  |  |  |  |  |  |
| Voltage Reading |  |  |  | Pass |  | Fail |
| Amperage Reading |  |  |  | Pass |  | Fail |
| If voltage and amperage readings are outside their acceptable ranges it is deemed a failed test, and the cathodic protection system must be repaired or replaced within 120 days of the failed test. Date cathodic protection system repaired or replaced: |  |  |  |  |  |  |
| Date repaired or replaced cathodic protection system retested (w/in 60 days of repair/replacement): |  |  |  |  |  |  |
| Inspection Date: |  |  |  |  |  |  |
| Voltage Reading |  |  |  | Pass |  | Fail |
| Amperage Reading |  |  |  | Pass |  | Fail |
| If voltage and amperage readings are outside their acceptable ranges it is deemed a failed test, and the cathodic protection system must be repaired or replaced within 120 days of the failed test. Date cathodic protection system repaired or replaced: |  |  |  |  |  |  |
| Date repaired or replaced cathodic protection system retested (w/in 60 days of repair/replacement): |  |  |  |  |  |  |
| Inspection Date: |  |  |  |  |  |  |
| Voltage Reading |  |  |  | Pass |  | Fail |
| Amperage Reading |  |  |  | Pass |  | Fail |
| If voltage and amperage readings are outside their acceptable ranges it is deemed a failed test, and the cathodic protection system must be repaired or replaced within 120 days of the failed test. Date cathodic protection system repaired or replaced: |  |  |  |  |  |  |
| Date repaired or replaced cathodic protection system retested (w/in 60 days of repair/replacement): |  |  |  |  |  |  |
| Inspection Date: |  |  |  |  |  |  |
| Voltage Reading |  |  |  | Pass |  | Fail |
| Amperage Reading |  |  |  | Pass |  | Fail |
| If voltage and amperage readings are outside their acceptable ranges it is deemed a failed test, and the cathodic protection system must be repaired or replaced within 120 days of the failed test. Date cathodic protection system repaired or replaced: |  |  |  |  |  |  |
| Date repaired or replaced cathodic protection system retested (w/in 60 days of repair/replacement): |  |  |  |  |  |  |
| Inspection Date: |  |  |  |  |  |  |
| Voltage Reading |  |  |  | Pass |  | Fail |
| Amperage Reading |  |  |  | Pass |  | Fail |
| If voltage and amperage readings are outside their acceptable ranges it is deemed a failed test, and the cathodic protection system must be repaired or replaced within 120 days of the failed test. Date cathodic protection system repaired or replaced: |  |  |  |  |  |  |
| Date repaired or replaced cathodic protection system retested (w/in 60 days of repair/replacement): |  |  |  |  |  |  |
| Inspection Date: |  |  |  |  |  |  |
| Voltage Reading |  |  |  | Pass |  | Fail |
| Amperage Reading |  |  |  | Pass |  | Fail |
| If voltage and amperage readings are outside their acceptable ranges it is deemed a failed test, and the cathodic protection system must be repaired or replaced within 120 days of the failed test. Date cathodic protection system repaired or replaced: |  |  |  |  |  |  |
| Date repaired or replaced cathodic protection system retested (w/in 60 days of repair/replacement): |  |  |  |  |  |  |