| UST Owner/Operator Requirements: - Retain a qualified SIR vendor to analyze inventory, delivery, and dispensing data collected over a calendar month to determine whether or not the UST system has a release or leakage. - Have in-tank monitoring equipment and procedures in place to accurately collect regulated substance inventory, delivery and dispensing data. - If the SIR analysis is conclusive and identifies a release or leakage, the Owner/Operator shall conduct a tightness test of the suspected tank or piping within 72 hours of obtaining knowledge of the suspected release or leakage. - If the SIR analysis is inconclusive, the Owner/Operator shall immediately, upon obtaining knowledge of the inconclusive result, commence an investigation to determine whether there is a release or leakage. The investigation shall be concluded within 72 hours of obtaining knowledge of the inconclusive result. - If the Owner/Operator is unable to determine that there is not a release or leakage, a tightness test pursuant to 310 CMR 80.32 shall be performed within 72 hours of the conclusion of the investigation. - Any failed tightness test requires compliance with 310 CMR 80.33(1) within 24 hours of obtaining knowledge of a release, or 72 hours of obtaining knowledge of leakage (310 CMR 80.33(2)). - In-tank monitoring system shall be tested annually to determine system is working properly. - All records shall be maintained in a hard copy or electronic log for a minimum of four years. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Facility Name |  |  |  |  |  |  |  |  | UST ID# |  |  |  |  |  |
| Name of Qualified SIR Vendor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date of Monthly SIR Report |  |  |  | Result of SIR Monthly Analysis (attached) |  |  |  |  |  |  | Conclusive: Pass Inconclusive Conclusive: Fail |  |  |  |
| If inconclusive: - Was an investigation to determine whether there is a release or leakage concluded within 72 hours of obtaining knowledge of the inconclusive result? - Did the investigation determine there was not a release or leakage? |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes No Yes No |
| If, as a result of a Conclusive: Fail SIR monthly analysis or an inconclusive investigation that did not determine there was not a release or leakage; was a tightness test conducted within 72 hours of obtaining knowledge of the need to conduct a tightness test? |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes No |
| If Required, Tightness Test Date |  |  | Tank Tightness Test Result |  | Pass Fail Results Attached |  |  | Piping Tightness Test Result |  |  |  | Pass Fail Results Attached |  |  |
| Failed Tightness Test: | If Release: All product removed from UST within 24 hours of failed test? |  |  |  |  | Yes | No | Date Removed (HW Manifest attached) |  |  |  |  |  |  |
|  | If Leakage: All product removed from UST within 72 hours of failed test? |  |  |  |  | Yes | No | Date Removed (HW Manifest attached) |  |  |  |  |  |  |

| Facility Name |  |  |  |  |  |  |  | UST ID# |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Name of Qualified SIR Vendor |  |  |  |  |  |  |  |  |  |  |  |  |
| Date of Monthly SIR Report |  |  |  | Result of SIR Monthly Analysis (attached) |  |  |  |  | Conclusive: Pass Inconclusive Conclusive: Fail |  |  |  |
| If inconclusive: - Was an investigation to determine whether there is a release or leakage concluded within 72 hours of obtaining knowledge of the inconclusive result? - Did the investigation determine there was not a release or leakage? |  |  |  |  |  |  |  |  |  |  |  | Yes No Yes No |
| If, as a result of a Conclusive: Fail SIR monthly analysis or an inconclusive investigation that did not determine there was not a release or leakage; was a tightness test conducted within 72 hours of obtaining knowledge of the need to conduct a tightness test? |  |  |  |  |  |  |  |  |  |  |  | Yes No |
| If Required, Tightness Test Date |  |  | Tank Tightness Test Result |  | Pass Fail Results Attached |  |  | Piping Tightness Test Result |  | Pass Fail Results Attached |  |  |
| Failed Tightness Test: | If Release: All product removed from UST within 24 hours of failed test? |  |  |  |  | Yes | No | Date Removed (HW Manifest attached) |  |  |  |  |
|  | If Leakage: All product removed from UST within 72 hours of failed test? |  |  |  |  | Yes | No | Date Removed (HW Manifest attached) |  |  |  |  |
| Date of Monthly SIR Report |  |  |  | Result of SIR Monthly Analysis (attached) |  |  |  |  | Conclusive: Pass Inconclusive Conclusive: Fail |  |  |  |
| If inconclusive: - Was an investigation to determine whether there is a release or leakage concluded within 72 hours of obtaining knowledge of the inconclusive result? - Did the investigation determine there was not a release or leakage? |  |  |  |  |  |  |  |  |  |  |  | Yes No Yes No |
| If, as a result of a Conclusive: Fail SIR monthly analysis or an inconclusive investigation that did not determine there was not a release or leakage; was a tightness test conducted within 72 hours of obtaining knowledge of the need to conduct a tightness test? |  |  |  |  |  |  |  |  |  |  |  | Yes No |
| If Required, Tightness Test Date |  |  | Tank Tightness Test Result |  | Pass Fail Results Attached |  |  | Piping Tightness Test Result |  | Pass Fail Results Attached |  |  |
| Failed Tightness Test: | If Release: All product removed from UST within 24 hours of failed test? |  |  |  |  | Yes | No | Date Removed (HW Manifest attached) |  |  |  |  |
|  | If Leakage: All product removed from UST within 72 hours of failed test? |  |  |  |  | Yes | No | Date Removed (HW Manifest attached) |  |  |  |  |