| Report Instructions: Highest Levels of Pollutants/Parameters Recorded from Continuous Monitoring Systems for the Year |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GENERAL INFORMATION |  |  |  |  |  |  |  |
| REPORT DESCRIPTION |  | This report must provide the highest level of each of the following pollutants and parameters recorded during the previous calendar year: |  |  |  |  |  |
|  |  | - Opacity |  |  |  |  |  |
|  |  | - SO2 |  |  |  |  |  |
|  |  | - NOx |  |  |  |  |  |
|  |  | - CO |  |  |  |  |  |
|  |  | - Unit Load |  |  |  |  |  |
|  |  | - Particulate Matter Control Device Inlet Temperature (PMCDT) |  |  |  |  |  |
| REGULATORY CITATION |  | This report satisfies the requirements of 310 CMR 7.08(2)(i)1.a. and f. |  |  |  |  |  |
| REPORTING FREQUENCY |  | Annual report |  |  |  |  |  |
| Due Date |  | February 15th following the calendar year that the data covers. |  |  |  |  |  |
| FACILITY information |  |  |  |  |  |  |  |
| FACILITY |  | Enter the name of the facility |  |  |  |  |  |
| SSEIS NUMBER |  | Enter the SSEIS identification number for the facility as provided below. |  |  |  |  |  |
|  |  | Facility |  |  |  | SSEIS identification number |  |
|  |  | SEMASS |  |  |  | 120/1 |  |
|  |  | Wheelabrator-N. Andover |  |  |  | 121/261 |  |
|  |  | Wheelabrator-Millbury |  |  |  | 118/419 |  |
|  |  | Covanta |  |  |  | 121/7 |  |
|  |  | Wheelabrator-Saugus |  |  |  | 119/7654 |  |
| MWC Unit Number |  | The number the facility has assigned each Municipal Waste Combustor Unit(s) included in the report. |  |  |  |  |  |
| Reporting Period |  | Enter the calendar year for the reporting period. For example, enter” 2001” for the report covering calendar year 2001 which is due on February 15, 2002 |  |  |  |  |  |
| Has the required performance evaluation been submitted to the Department? |  | Continuous monitoring systems must be initially certified when they are installed, and periodically recertified to ensure that they meet the performance specifications of Appendix B of 40 CFR part 60. |  |  |  |  |  |
|  |  | IF: |  |  |  |  | ANSWER: |
|  |  | The CMS was certified or recertified during the calendar year AND The required certification WAS submitted to DEP for monitors certified or recertified |  |  |  |  | YES |
|  |  | The CMS was certified or recertified during the calendar year being reported on AND The required certification was NOT submitted to DEP. |  |  |  |  | NO |
|  |  | The CMS did not have to be certified or recertified during the calendar year being reported on |  |  |  |  | NA |
| entering monitoring data |  |  |  |  |  |  |  |
| Date MM/DD/YYYY |  | The date on which the highest level for each listed pollutant/parameter was recorded For example: report January 2, 2003 as 01/02/2003 |  |  |  |  |  |
| Pollutant/ Parameter |  | List on a separate line each pollutant or parameter that must be reported. |  |  |  |  |  |
| Regulatory Standard |  | The following are the numerical values of the pollutant/parameter limit that apply to the municipal waste combustion unit. Insert them into the form. |  |  |  |  |  |
|  |  | Pollutant/ Parameter |  | Regulatory Limit |  |  |  |
|  |  | Opacity |  | 10 |  |  |  |
|  |  | SO2 |  | Limit for unit listed in facility’s approved emission control plan |  |  |  |
|  |  | NOx |  | Limit for unit listed in facility’s approved emission control plan |  |  |  |
|  |  | CO |  | Limit for unit listed in facility’s approved emission control plan. |  |  |  |
|  |  | Unit_Load |  | 110% of the average unit load during the last dioxin/furan compliance test that demonstrated compliance preceding the measurement of highest unit load recorded during the reporting year. Use the directions below to calculate Unit Load: - Determine the date of the highest unit load for the reporting year - Determine the date of the most recent dioxin/furan compliance test that demonstrated compliance preceding the date of the highest unit load. - Determine the average unit load during that dioxin/furan compliance test - Multiply the average unit load by 1.1 - Enter this number in appropriate field |  |  |  |
|  |  | PMCDT |  | Less than 30o F or 17o C plus the average temperature measured during the last dioxin/furan compliance test that demonstrated compliance preceding the measurement of the highest PMCD inlet temperature recorded. - Determine the date of the highest recorded PMCD inlet temperature during the reporting year - Determine the date of the most recent dioxin/furan compliance test that demonstrated compliance preceding the highest recorded PMCD inlet temperature - Determine the average PMCD inlet temperature during that dioxin/furan compliance test - If the temperature is in Fahrenheit, add 30 degrees to the average inlet temperature measured during the dioxin furan compliance test, and enter the resulting temperature. If temperature is measured in Celsius, add 17 degrees to the average inlet temperature measured during the dioxin furan compliance test, and enter the resulting temperature. - Enter this number. |  |  |  |
| UNITS OF APPLICABLE LIMIT |  | The units that the pollutant/parameter standards are expressed in are provided on the form. |  |  |  |  |  |
|  | Pollutant/ Parameter |  |  |  | Units of measure |  |  |
|  | Opacity |  |  |  | Percent (%) |  |  |
|  | SO2 |  |  |  | Parts per million (ppm) |  |  |
|  | NOx |  |  |  | Parts per million (ppm) |  |  |
|  | CO |  |  |  | Parts per million (ppm) |  |  |
|  | Unit Load |  |  |  | Kilo – pounds per hour of steam. |  |  |
|  | PMCD Inlet Temperature |  |  |  | Enter F for degrees Fahrenheit or C for degrees Celsius. |  |  |
| Averaging Time Period |  | Enter the number of hours in the averaging time period for the pollutant/parameter standard. |  |  |  |  |  |
| Highest Recorded Level |  | Enter the highest level recorded during the reporting year for each of the listed pollutants or parameters. The level should be expressed in the same units as the applicable standard. |  |  |  |  |  |