| Report Instructions: Semi-Annual Report for Continuous Emissions Monitoring and Compliance Tests |  |  |  |  |
| --- | --- | --- | --- | --- |
| BASIC INFORMATION |  |  |  |  |
| REPORT DESCRIPTION | This report summarizes any exceedances of the limits for the following pollutants and parameters during the six months of the year covered by the report: |  |  |  |
|  | - Sulfur dioxide - Nitrogen oxides - Carbon monoxide - Particulate Matter Control Device Inlet Temperature - Unit load - Opacity determined by Continuous Opacity Monitoring System (COMS) - Carbon feedrate - Carbon Injection operating parameter(s) |  |  | - Mercury - Lead - Cadmium - Particulate Matter - Dioxin/Furan - Hydrogen Chloride - Opacity determined by Method 9 (certified observer) - Fugitive ash |
| REGULATORY CITATION | This report satisfies the requirements of 310 CMR 7.08(2)(i)2. |  |  |  |
| REPORTING FREQUENCY | Semi-annual |  |  |  |
| Due DATE | Reporting Period |  |  | Due Date |
|  | January 1 through June 30 |  |  | August 1. |
|  | July 1 through December 30 |  |  | February 15 of the following year. |
| FACILITY INFORMATION |  |  |  |  |
| Facility | Enter the name of the facility. |  |  |  |
| SSEIS NUMBER | Enter the SSEIS identification number for the facility: Pick from the following list: |  |  |  |
|  | Facility |  |  | SSEIS identification number |
|  | SEMASS |  |  | 120/1 |
|  | Wheelabrator-N Andover |  |  | 121/261 |
|  | Wheelabrator-Millbury |  |  | 118/419 |
|  | Covanta |  |  | 121/7 |
|  | Wheelabrator-Saugus |  |  | 119/7654 |
| Reporting Period | Enter the appropriate reporting period (January-June with the year (yyyy) or July-December with the year (yyyy)) |  |  |  |
| Pollutant/ Parameter | Enter the applicable pollutant/parameter, using the codes listed below. |  |  |  |
|  | CODE |  | POLLUTANT/PARAMETER |  |
|  | SO2 |  | Sulfur dioxide |  |
|  | NOx |  | Nitrogen oxides |  |
|  | CO |  | Carbon monoxide |  |
|  | PMCDT |  | Particulate Matter Control Device Inlet Temperature (degrees Fahrenheit or degrees Celsius) |  |
|  | UL |  | Unit load |  |
|  | Opacity |  | Opacity determined by Continuous Opacity Monitoring System (COMS) |  |
|  | Carbon Feedrate |  | Carbon feedrate |  |
|  | Carbon parameter |  | Carbon Injection operating parameter(s). If more than one parameter is used, enter a number after the words, e.g., “Carbon parameter 1”, to indicate the parameter. Provide a written description of the carbon feedrate parameter. |  |
|  | Hg |  | Mercury |  |
|  | Pb |  | Lead |  |
|  | Cd |  | Cadmium |  |
|  | PM |  | Particulate Matter |  |
|  | PCDD/PCDF |  | Dioxin/Furan |  |
|  | HCl |  | Hydrogen Chloride |  |
|  | Opacity-M9 |  | Opacity determined by Method 9 |  |
|  | Fugitive Ash |  | Fugitive ash |  |
| Units of applicable limit | Use the following nomenclature to enter the units of the applicable limit. Use the same units as the limit. If the limit cannot be expressed in these units, please contact the Department to establish a different code: |  |  |  |
|  | - mg/dscm @ 7% O2 milli-grams per dry standard cubic meter - ng/dscm @7% O2 nano-grams per dry standard cubic meter - ppmv,d @ 7% O2 parts per million by volume dry basis - % percent - RPM revolutions per minute - lb/hr pounds per hour (carbon injection rate) - kilo-lbs/hr kilo-pounds per hour (unit load as steam load) - F or C Fahrenheit or Celsius |  |  |  |
| Averaging time | Enter the number of hours (or minutes as applicable) in the averaging time of the emission or parametric limit. This can be obtained from the Facility’s emission control plan approval or the regulation. |  |  |  |
| Describe Parameter Being Measured | Fill in For Carbon Feedrate ONLY: Provide a description of the parameter being measured to determine carbon feedrate (e.g., screw feeder speed). |  |  |  |
| Exceedance of Particular Pollutant/ PARAMeter Reported? | Answer YES if a limit for the pollutant or parameter was exceeded during the reporting period. Answer NO if the limit for the pollutant or parameter was NOT exceeded during the reporting period. See 310 CMR 7.08(2). In determining whether or not there was an exceedance, include periods of startup, shutdown or malfunction, even though the limit may not apply during these periods. |  |  |  |
| Use CO2 Diluent Monitor? | Answer Y if the MWC uses a CO2 diluent monitor Answer N if the MWC uses an O2 diluent monitor Note: A diluent monitor is used only for either a NOx, SO2, or CO continuous monitoring system. |  |  |  |
| ENTERING MONITORING DATA |  |  |  |  |
| ENTERING THE DATA in asterisked fields | For Hg, Pb, Cd, PM, PCDD/PCDF, Method 9 opacity, fugitive ash, and HCL enter the fields with an asterisk only. |  |  |  |
| MWC Unit | Municipal Waste Combustor (MWC) unit number the facility has assigned to the unit. |  |  |  |
| Exceedance Date | Enter the date of exceedance of the standard (mm/dd/yyyy). For exceedances determined through stack testing, enter the date of the first valid test run of the tests. For example: express January 03, 2001 as 01/03/2001 |  |  |  |
| Time of Excess Emission | For pollutants/parameters measured with a continuous monitoring system, the pollutant/parameter limits are averaged over a block period, for example CO readings are averaged over a 4 hour block period Enter the beginning time of the block average under FROM and the ending time under TO for any block average period during which there is an exceedance for that particular pollutant/parameter. The duration should correspond with the averaging block period. Use military time HH:MM For example, for a CO excess emission during the four-hour block period from 4 pm until 8 pm, enter 16:00 under FROM and 20:00 under TO. |  |  |  |
| Applicable Limit | Enter the numerical value (with no units) of the applicable limit for the pollutant or parameter being reported. For % reduction, enter as whole number; For example: 75 The values can be found in the Emission Control Plan approval, with the exception of the following parameters which are determined as follows: |  |  |  |
|  | Parameter | Determining the Applicable Standard |  |  |
|  | PMCDT | IF temperature is measured in Fahrenheit, calculate the PMCDT standard as follows: [30 degrees] + [Temperature measured during the last dioxin/furan test that demonstrated compliance] IF temperature is measured in Celsius, calculate PMCDT standard as follows: [17 degrees] + [Temperature measured during the last dioxin/furan test that demonstrated compliance] |  |  |
|  | Unit load | 110% of the unit load (kilo-pounds per hour of steam) measured during the last dioxin/furan test that demonstrated compliance. |  |  |
|  | Carbon Feedrate | Report the higher of the two measurements of the carbon feedrate during the last dioxin/furan test that demonstrated compliance AND the last mercury compliance test that demonstrated compliance. |  |  |
|  | Carbon parameter | Report the higher of the two measurements of the carbon parameter during the last dioxin/furan test that demonstrated compliance AND the last mercury compliance test that demonstrated compliance. |  |  |
|  | NOTE: During any calendar year, the facility will probably be subject to different limits for unit load, PMCDT, carbon feed rate, and carbon injection operating parameters since the measured values for these parameters will probably vary slightly from test to test. The applicable limit for these parameters is determined by the last compliance test that demonstrated compliance. |  |  |  |
| Monitored Level | The average concentration/parameter value measured. For percent reduction enter as a whole number; for example: 65 |  |  |  |
| Specific Reason For Excess Emission | Enter the reason for exceedance. |  |  |  |
| Corrective Actions Taken | Explain what steps were taken to bring the MWC unit into compliance with the limit that was exceeded. |  |  |  |