COMPLIANCE CHECKLIST

IP1_Medical Surgical Patient Care Unit

The following checklist is intended to be used in the plan review applications for health care facilities submitted to the Massachusetts Department of Public Health.  This checklist summarizes and references the applicable requirements from the Licensure Regulations and the 2022 Edition of the FGI Guidelines for Design and Construction of Hospitals.  Applicants must verify compliance of the plans submitted to the Department with all referenced requirements from the Licensure Regulations and FGI Guidelines when completing this Checklist.  A separate Checklist must be completed for each nursing unit, hospital or clinic department, or clinical suite.

Other jurisdictions, regulations and codes may have additional requirements which are not included in this checklist, such as:

- NFPA 101 Life Safety Code (2012) and applicable related standards contained in the appendices of the Code

- State Building Code (780 CMR)

- Accreditation requirements of The Joint Commission

- CDC Guidelines for Preventing the Transmission of Mycobacterium Tuberculosis in Health Care Facilities

- USP 797 & Regulations of the Massachusetts Board of Registration in Pharmacy

- Occupational Safety & Health Standards (OSHA)

- Accessibility Guidelines of the Americans with Disabilities Act (ADA)

- Architectural Access Board Regulations (521 CMR)

- Local Authorities having jurisdiction.

Instructions:

- All requirement lines must be completed according to the following instructions and included in the plan submissions for Self-Certification Process or Abbreviated Review Process.

- This checklist must be completed by the project architect or engineer based on the design actually reflected in the plans at the time of completion of the checklist.

- Each requirement line (___) of this Checklist must be completed exclusively with one of the following marks, unless otherwise directed in the checklist.  If a functional space is not affected by a renovation project, the mark “E” may be indicated on the requirement line (___) before the name of the functional space (associated requirements on indented lines below that name, or associated MEP requirements do not have to be completed in this case).  If more than one functional space serves a given required function (e.g. patient room or exam room), that clarification should be provided in the Project Narrative, and the requirement lines are understood to only address the functional spaces that are involved in the project.

| X = Requirement is met, for new space, for renovated space, or for existing direct support space for an expanded service. | = Check box under section titles or individual requirements lines for optional services or functions that are not included in the project area. |
| --- | --- |
| E = Requirement relative to an existing suite or area that has been licensed for its designated function, is not affected by the construction project and does not pertain to a required direct support space for the specific service affected by the project. “E” must not be used for an existing required support space associated with a new patient care room or area. | W = Waiver requested for specific section of the Regulations or FGI Guidelines, where hardship in meeting requirement can be demonstrated (a Physical Plant Waiver Form must be completed for each waiver request). An explicit floor plan or plan detail must be attached to each waiver request. |

- All room functions marked with "X" must be shown on the plans with the same name labels as in this checklist.

- Mechanical, electrical & plumbing requirements are only partially mentioned in this checklist.  The relevant section of the FGI Guidelines must be used for project compliance with all MEP requirements and for waiver references.

- Oxygen, vacuum, medical air, waste anesthesia gas disposal and instrument air outlets (if required) are identified respectively by the abbreviations "OX", "VAC", "MA", “WAGD” & “IA”.

- Requirements referenced with “FI” result from formal interpretations from the FGI Interpretations Task Group.

- The location requirements including asterisks (*) refer to the definitions of the Glossary in the beginning section of the FGI Guidelines and reproduced in this checklist.

| Facility Name: |  | DoN Project Number: (if applicable) |
| --- | --- | --- |
| Facility Address: |  | Patient Care Unit Bed Complements: Current = Proposed = |
| Satellite Name: (if applicable) |  | Building/Floor Location: |
| Satellite Address: (if applicable) |  | Submission Dates: |
| Project Description: |  | Initial Date: Revision Date: |

|  | Architectural Requirements | Building Systems Requirements |  |
| --- | --- | --- | --- |
| 2.2-2.2 | MEDICAL/SURGICAL PATIENT CARE UNIT |  |  |
| 2.1-1.2.3 | Shared Services: |  |  |
|  | ___ No combined functions unless specifically allowed in this checklist |  |  |
| 2.2-2.2.2 | PATIENT ROOM |  |  |
| 2.2-2.2.2.1 | Capacity: |  |  |
| (1) | ___ maximum number of beds per room is one bed |  |  |
| (2) | or ___ renovation work is undertaken ___ present capacity is more than one patient in each room ___ proposed room capacity is no more than present capacity ___ maximum 2 patients in each room |  |  |
| 2.2-2.2.2.2 | Space Requirements: |  |  |
| (1)(a) | ___ single-patient rooms ☐ check if not included in project | Ventilation: ___ Min. 4 air changes per hour | Table 7-1 |
|  | ___ min. clear floor area 120 sf | Lighting: | 2.1-8.3.4.3(1) |
| 2.2-2.2.2.2 |  | ___ General lighting |  |
| (2)(a) | ___ min. clearance 3’-0” between sides of bed & any wall or any other fixed obstruction | ___ Reading light for each patient bed ___ controls accessible to patients in bed | (a) |
|  | ___ min. clearance 3’-0” between foot of bed & any wall or any other fixed obstruction | ___ Night-light located in each patient room ___ no central control of night-lights outside room | (b) |
| (1)(b) | ___ multiple-patient rooms ☐ check if not included in project ___ min. clear floor area 100 sf per bed | ___ night-light illuminates path from room entrance to bedside |  |
| (2)(a) | ___ min. clearance 3’-0” between sides of bed & any wall or any other fixed obstruction | ___ night-light illuminates path between bed & toilet room |  |
| (2)(b) | ___ min. clearance 4’-0” at foot of each bed to permit passage of equipment & beds | Power: ___ Min. 12 receptacles in total ___ Min. 2 receptacles at each side of the head of the bed | Table 2.1-1 |
| 2.2-2.2.2.3 2.1-7.2.2.5(1) | Windows in Patient Rooms: ___ each patient room provided with natural light by means of window to outside | ___ Min. 2 receptacles on all other walls (not including any TV receptacle) |  |
| 2.1-7.2.2.5(2) | ___ operable windows in patient rooms ☐ check if not included in project | Nurse Call System: ___ Patient station | Table 2.1-2 |
|  | ___ window operation is limited with either stop limit/restrictor hardware or open guard/screen | ___ Staff assistance station ___ Emergency call station |  |
|  | ___ prevents passage of 4-inch diameter sphere through opening | Medical Gases: ___ 1 OX, 1 VAC per bed | Table 2.1-3 |
| 2.1-7.2.2.6 | ___ insect screens |  |  |
| 2.1-7.2.2.5(3) |  |  |  |
| (a) | ___ min. net glazed area be no less than 8% of required min. clear floor area |  |  |
| (b) | ___ max. 36” windowsill height above finished floor |  |  |
| 2.2-2.2.2.4 | Patient Privacy: |  |  |
| 2.1-2.1.2 | ___ provisions are made to address patient visual & speech privacy |  |  |
| 2.1-2.2.5 | Handwashing Station in Patient Room: |  |  |
| 2.1-2.2.5.1 (1) | ___ provided in patient room in addition to that in toilet room ___ adjacent* to entrance to patient room for use by health care personnel & others Multiple-Patient Rooms: ☐check if not included in project |  |  |
| (2) | ___ handwashing station located outside patients cubicle curtains |  |  |
| 2.1-2.2.6 | ___ Patient toilet room |  |  |
| 2.1-2.2.6.2 | ___ in patient care units patient toilet room serve no more than one patient room |  |  |
| 2.1-2.2.6.3 (1) (2) (3) | ___ toilet ___ handwashing station ___ bedpan washer | Ventilation: ___ Min. 10 air changes per hour ___ Exhaust ___ Negative pressure | Table 7-1 |
|  |  | ___ No recirculating room units |  |
|  |  | Nurse Call System: ___ Bath station | Table 2.1-2 |
| 2.2-2.2.2.7 | Patient Bathing Facilities: |  |  |
| 2.1-2.2.7.1(1) | ___ located in toilet room directly accessible from each patient room or |  |  |
| 2.1-2.2.7.1(2) | ___ located in central bathing facility |  |  |
| 2.1-2.2.7.2 | Central Bathing Facilities: ☐ check if not included in project |  |  |
| (1) | ___ each bathtub or shower in individual room or enclosure that provides privacy for bathing drying & dressing | Ventilation: ___ Min. 10 air changes per hour ___ Exhaust ___ Negative pressure | Table 7-1 |
| (2) | ___ at least one shower or bathtub provided for each patient care unit | ___ No recirculating room units Nurse Call System: ___ Bath station | Table 2.1-2 |
| (3)(a) | ___ toilet in or directly accessible to each central bathing facility | Ventilation: ___ Min. 10 air changes per hour ___ Exhaust | Table 7-1 |
|  | ___ in separate enclosure or ___ located in private bathing room | ___ Negative pressure ___ No recirculating room units |  |
| (3)(b) | ___ handwashing sink in or directly accessible to each central bathing facility | Nurse Call System: ___ Bath station | Table 2.1-2 |
| (3)(c) | ___ storage for soap & towels in or directly accessible to each central bathing facility |  |  |
| 2.1-2.2.7.3 | Mobile Lifts, Shower Gurney Devices & Wheelchair Access: |  |  |
| (1) | ___ doorways designed to allow entry of portable/mobile mechanical lifts & shower gurney devices |  |  |
| (2) | ___ thresholds designed to facilitate use & prevent tipping of wheelchairs & other portable wheeled equipment |  |  |
| (3) | ___ patient shower rooms designed to allow entry of portable/mobile mechanical lifts & shower gurney devices |  |  |
| (4) | ___ floor drain grates designed to facilitate use & prevent tipping of wheelchairs & other portable wheeled equipment |  |  |
| 2.2-2.2.2.8 | Patient Storage: |  |  |
|  | ___ separate wardrobe, locker, or closet suitable for garments & for storing personal effects |  |  |
| 2.2-2.2.3 | PATIENT/FAMILY-CENTERED CARE |  |  |
| (1) | ___ Space provided in patient room to support visitation by family members & others |  |  |
| (a) | ___ space for movable seating with min. of one seat for family member or visitor & one seat for patient |  |  |
| (b) | ___ space for at least one chair for long-term sitting |  |  |
| (2) | ___ Family members or visitors are permitted to sleep in patient room overnight ☐ check if not included in project |  |  |
|  | ___ space provided for sleeping accommodation |  |  |
| (3) | ___ Public communication services provided in each patient room |  |  |
| 2.2-2.2.4 | SPECIAL PATIENT CARE ROOMS |  |  |
| 2.2-2.2.4.2 | ___ Airborne infection isolation (AII) room |  |  |
| (2) | ___ at least one AII room in hospital |  |  |
| 2.1-2.4.2.1(3) | Location: |  |  |
|  | ___ AII rooms located in individual patient care units or ___ AII rooms grouped as separate isolation patient care unit |  |  |
| 2.1-2.4.2.2 | ___ complies with requirements applicable to patient rooms | Ventilation: ___ Min. 12 air changes per hour | Table 7-1 |
| (1) | ___ capacity one bed | ___ Exhaust |  |
| (2) | ___ personal protective equipment (PPE) storage at entrance to room | ___ Negative pressure |  |
|  | ___ provisions for PPE disposal at entrance to room |  |  |
| (3) | ___ handwashing station | ___ No recirculating room units |  |
|  |  | ___ Exhaust register located directly above patient bed on ceiling or on wall near head of bed | Part 3/7.2.1 |
| (4) | ___ patient toilet room ___ serves only one AII room | Ventilation: ___ Min. 10 air changes per hour | Table 7-1 |
| (5) | ___ bathtub or shower | ___ Exhaust |  |
| 2.1-2.2.6.3 (1) (2) (3) | ___ toilet ___ handwashing station ___ bedpan washer | ___ Negative pressure ___ No recirculating room units |  |
| 2.1-2.4.2.3 | ___ anteroom ☐ check if not included in project |  |  |
| (1) | ___ provides space for persons to don personal protective equipment (PPE) before entering patient room | Ventilation: ___ Min. 10 air changes per hour ___ Exhaust | Table 7-1 |
|  | ___ provides space for persons to doff PPE after leaving patient room | ___ No recirculating room units |  |
| (2) | ___ all doors to anteroom have self-closing devices or ___ audible alarm activated when AII room is in use as isolation room |  |  |
| (3)(a) | ___ handwashing station |  |  |
| (3)(b) | ___ storage for unused PPE |  |  |
| (3)(c) | ___ disposal/holding container for used PPE |  |  |
| 2.1-2.4.2.4 | Architectural Details & Furnishings: |  |  |
| (1)(a) | ___ perimeter walls ceiling & floor including penetrations constructed to prevent air exfiltration |  |  |
| (1)(b) | ___ self-closing devices on all room exit doors or ___ activation of audible alarm when AII room is in use as isolation room |  |  |
|  | ___ edge seals provided along sides & top of doorframe for any door into AII room |  |  |
| (2) (a) | ___ window treatments do not include fabric drapes & curtains |  |  |
| 2.1-2.4.2.5 | ___ room pressure visual or audible alarm |  |  |
| 2.1-7.2.3.1 (7)(a) | ___ floors are monolithic & integral coved wall bases are at least 6” high & tightly sealed to wall |  |  |
| 2.2-2.2.4.4 | ___ Protective environment (PE) room ☐ check if not included in project |  |  |
| 2.1-2.4.2.2 | ___ complies with requirements applicable to patient rooms | Ventilation: ___ Min. 12 air changes per hour | Table 7-1 |
| (1) | ___ capacity one bed | ___ Positive pressure |  |
| (2) | ___ personal protective equipment (PPE) storage at entrance to room | ___ No recirculating room units |  |
| (3) | ___ handwashing station | ___ Supply air diffusers are located above patient bed | Part 3/7.2.2 |
|  |  | ___ Exhaust grilles or registers located near patient room door |  |
| (4) | ___ patient toilet room ___ serves only one AII room | Ventilation: ___ Min. 10 air changes per hour | Table 7-1 |
| (5) | ___ bathtub or shower | ___ Exhaust |  |
| 2.1-2.2.6.3 (1) (2) (3) | ___ toilet ___ handwashing station ___ bedpan washer | ___ Negative pressure ___ No recirculating room units |  |
| 2.1-2.4.2.3 | ___ anteroom ☐ check if not included in project |  |  |
| (1) | ___ provides space for persons to don personal protective equipment (PPE) before entering patient room | Ventilation: ___ Min. 10 air changes per hour ___ No recirculating room units | Table 7-1 |
| (2) | ___ all doors to anteroom have self-closing devices or ___ audible alarm activated when PE room is in use as isolation room |  |  |
| (3)(a) | ___ handwashing station |  |  |
| (3)(b) | ___ storage for unused PPE |  |  |
| (3)(c) | ___ disposal/holding container for used PPE |  |  |
| 2.1-2.4.2.4 | Architectural Details & Furnishings: |  |  |
| (1)(a) | ___ perimeter walls ceiling & floor including penetrations constructed to prevent air exfiltration |  |  |
| (1)(b) | ___ self-closing devices on all room exit doors or ___ activation of audible alarm when PE room is in use as isolation room |  |  |
|  | ___ edge seals provided along sides & top of doorframe for any door into PE room |  |  |
| (2) (a) | ___ window treatments do not include fabric drapes & curtains |  |  |
| 2.1-2.4.2.5 | ___ room pressure visual or audible alarm |  |  |
| 2.2-2.2.4.4(5) | Special Design Elements: |  |  |
| (a) | ___ monolithic ceiling |  |  |
|  | ___ surfaces are cleanable |  |  |
| (b) | ___ lighting fixtures have lenses & are sealed |  |  |
| 2.1-7.2.3.1 (7)(a) | ___ floors are monolithic & integral coved wall bases are at least 6” high & tightly sealed to wall |  |  |
| 2.2-2.2.4.5 | ___ Combination airborne infection isolation/ protective environment (AII/PE) room ☐ check if not included in project (only if PE room is not provided) |  |  |
| 2.2-2.2.4.5(1) | ___ at least one combination AII/PE room |  |  |
| 2.1-2.4.2.2 | ___ complies with requirements applicable to patient rooms | Ventilation: ___ Min. 12 air changes per hour | Table 7-1 |
| (1) | ___ capacity one bed | ___ Exhaust |  |
| (2) | ___ personal protective equipment (PPE) storage at entrance to room | ___ Positive pressure ___ No recirculating room units |  |
| (3) | ___ handwashing station | ___ Exhaust register located directly above patient bed on ceiling or on wall near head of bed | Part 3/7.2.1 |
| (4) | ___ patient toilet room ___ serves only one AII room | Ventilation: ___ Min. 10 air changes per hour | Table 7-1 |
| (5) | ___ bathtub or shower | ___ Exhaust |  |
| 2.1-2.2.6.3 (1) (2) (3) | ___ toilet ___ handwashing station ___ bedpan washer | ___ Negative pressure ___ No recirculating room units |  |
| 2.1-2.4.2.4 | Architectural Details & Furnishings: |  |  |
| (1)(a) | ___ perimeter walls ceiling & floor including penetrations constructed to prevent air exfiltration |  |  |
| (1)(b) | ___ self-closing devices on all room exit doors or ___ activation of audible alarm when PE room is in use as isolation room |  |  |
|  | ___ edge seals provided along sides & top of doorframe for any door into PE room |  |  |
| (2) (a) | ___ window treatments do not include fabric drapes & curtains |  |  |
| 2.1-2.4.2.5 | ___ room pressure visual or audible alarm |  |  |
| 2.2-2.2.4.4(5) | Special Design Elements: |  |  |
| (a) | ___ monolithic ceiling |  |  |
|  | ___ surfaces are cleanable |  |  |
| (b) | ___ lighting fixtures have lenses & are sealed |  |  |
| 2.2-2.2.4.5(3) | ___ Anteroom |  |  |
| (a) | ___ provides space for persons to don personal protective equipment before entering patient room & doff PPE after leaving patient room | Ventilation: ___ Min. 10 air changes per hour ___ Exhaust ___ No recirculating room units | Table 7-1 |
| (b) | ___ all doors to anteroom have self-closing devices or ___ audible alarm activated when AII/PE room is in use as isolation room |  |  |
| 2.1-2.4.2.3 |  |  |  |
| (3)(a) | ___ handwashing station |  |  |
| (3)(b) | ___ storage for unused PPE |  |  |
| (3)(c) | ___ disposal/holding container for used PPE |  |  |
| 2.2-2.2.4.6 | ___ Medical behavioral & mental health room ☐ check if not included in project |  |  |
| 1.2-4.6.2.2(1) | ___ patient environment designed to protect privacy, dignity & health of patients ___ patient environment addresses potential risks related to patient elopement ___ patient environment addresses harm to self & others |  |  |
| 1.2-4.6.2.2(2) | ___ design of behavioral/mental health patient areas accommodates need for clinical & security resources |  |  |
| 2.2-2.2.4.6(2) | ___ complies with requirements applicable to patient rooms with following exceptions: |  |  |
| (a) | ___ room for single patient occupancy |  |  |
| (b) | ___ room located to permit staff observation of entrance |  |  |
| (c) | ___ patient room & adjoining patient toilet room designed to minimize potential for escape, concealment, injury or suicide |  |  |
|  | ___ no lay-in ceiling |  |  |
|  | ___ security film or glazing provided on windows |  |  |
|  | ___ shatterproof mirror in patient toilet room or no mirror |  |  |
|  | ___ tamper-resistant ceiling & air distribution devices, lighting fixtures sprinkler heads & other appurtenances |  |  |
| (d) | ___ view panels used for observation of patients provide patient privacy & minimize casual observation by visitors & other patients |  |  |
| 2.2-2.14 | BARIATRIC PATIENT ROOMS ☐ check if not included in project |  |  |
| 2.1-2.3.1 | ___ Project Narrative determines the need to provide spaces designed to enable safe care of patients of size |  |  |
| 2.1-2.3.1.1 |  |  |  |
| (2) | ___ Project Narrative includes patient handling & movement assessment including need for expanded-capacity lifts & architectural details supporting movement of patients of size |  |  |
| 2.1-2.3.1.3 | Patient Lift System: |  |  |
| (1) | ___ accommodations for patient handling provided by either overhead lift system or floor-based full-body sling lift & standing-assist lifts |  |  |
| (2) | ___ lifts capable of accommodating projected weight of patients of size |  |  |
| 2.1-2.3.2(1) | ___ Patient rooms designated for patients of size are single-patient rooms |  |  |
| 2.1-2.3.2(2) | ___ Lift system (e.g. ceiling- or wall-mounted system) in rooms designated for care of patients who weigh 600 lbs. or more ☐ check if not included in project |  |  |
|  | ___ can transfer patient from bed to toilet |  |  |
| 2.1-2.3.2.2 | Space Requirements: | Ventilation: ___ Min. 4 air changes per hour | Table 7-1 |
| (2)(a) | ___ min. clearance 5’-0”at foot of bed | Lighting: | 2.1-8.3.4.3(1) |
| (2)(b) | ___ min. clearance 5’-6” on non-transfer side of bed from edge of expanded-capacity patient bed | ___ General lighting ___ Reading light for each patient bed | (a) |
| (2)(c) | Clearance on Transfer Side of Bed: | ___ controls accessible to patients in bed |  |
|  | ___ patient room equipped with ceiling- or wall-mounted lifts ___ rectangular clear floor area min. 10’-6” long by 5’-6” wide measured beginning 2’-0” from headwall | ___ Night-light located in each patient room ___ no central control of night-lights outside room | (b) |
|  | or ___ patient room not equipped with ceiling- or wall-mounted lifts | ___ night-light illuminates path from room entrance to bedside |  |
|  | ___ rectangular clear floor area min. 10’-6” long by 7'-0" wide measured beginning 2’-0” from headwall | ___ night-light illuminates path between bed & toilet room |  |
|  |  | Power: ___ Min. 12 receptacles in total | Table 2.1-1 |
|  |  | ___ Min. 2 receptacles at each side of the head of the bed |  |
|  |  | ___ Min. 2 receptacles on all other walls (not including any TV receptacle) ___ Min. 1 receptacle for each motorized bed |  |
|  |  | Nurse Call System: ___ Patient station ___ Staff assistance station ___ Emergency call station | Table 2.1-2 |
|  |  | Medical Gases: |  |
|  |  | ___ 1 OX, 1 VAC per bed | Table 2.1-3 |
| 2.1-2.3.3 | ___ Airborne infection isolation (AII) room |  |  |
| 2.1-2.3.3.1 | ___ at least one AII room that meets requirements in section 2.1-2.3 (accommodations for care of patients of size) & requirements in section 2.1-2.4.2 (airborne infection isolation room) is provided in facility |  |  |
| 2.1-2.3.4 | ___ handwashing station in each toilet room designated for use by patients of size ___ meets requirements in section 2.1-2.8.7 (handwashing station) |  |  |
| 2.1-2.3.4.1 | ___ downward static force required for handwashing stations designated for patients of size indicated in Project Narrative |  |  |
| 2.1-2.3.5 | ___ Patient toilet room |  |  |
|  | ___ designated for use by patients of size meet requirements in section 2.1-2.2.6 (patient toilet room) | Ventilation: ___ Min. 10 air changes per hour ___ Exhaust ___ Negative pressure ___ No recirculating room units | Table 7-1 |
| 2.1-2.3.5.1 | ___ expanded-capacity toilet ___ min. 36” from finished wall to centerline of toilet on both sides or |  |  |
| 2.1-2.3.5.2 | ___ regular toilet ___ min. 44” from finished wall to centerline of toilet on both sides to allow for positioning of expanded capacity commode over toilet |  |  |
| 2.1-2.3.5.3 | ___ 46” wide clear floor area extends 72” from front of toilet |  |  |
| 2.1-2.3.6 | ___ Shower facilities for patients of size |  |  |
| 2.1-2.3.6.1 | ___ shower stalls min. 4’-0” by 6’-0” |  |  |
| 2.1-2.3.6.2 | ___ equipped with grab bars capable of supporting 800 lbs. | Ventilation: ___ Min. 10 air changes per hour | Table 7-1 |
| 2.1-2.3.6.3 | ___ handheld spray nozzles mounted on side wall | ___ Exhaust ___ Negative pressure ___ No recirculating room units |  |
| 2.1-2.3.8 | ___ Equipment & Supply Storage |  |  |
|  | ___ accommodates size of expanded-capacity equipment (e.g. floor-based lifts lift, slings & accessories etc.) |  |  |
| 2.1-2.3.9 | ___ Waiting areas |  |  |
| 2.1-2.3.9.1 | ___ sized to accommodate expanded-capacity furniture required for patients & visitors of size |  |  |
| 2.1-2.3.9.2 | ___ min. 5% of seating able to accommodate person who weighs 600 lbs. |  |  |
| 2.1-2.3.10 | Special Design Elements for Spaces for Care of Patients of Size: |  |  |
| 2.1-2.3.10.1 | ___ all plumbing fixtures, handrails, grab bars, patient lift equipment, built-in furniture & other furnishings & equipment designed to accommodate maximum planned patient weight |  |  |
| 2.1-2.3.10.2 | Door Openings: |  |  |
| (1) | ___ min. clear width 45.5” for path of travel of expanded-capacity wheelchairs to public areas & patient care areas |  |  |
| (2) | ___ min. clear width 57” to patient rooms |  |  |
| (3) | ___ min. clear width 45.5” to toilet rooms |  |  |
| 2.2-2.2.8 | SUPPORT AREAS FOR MEDICAL/SURGICAL PATIENT CARE UNITS |  |  |
| 2.1-2.8.1 | ___ Support areas provided on each patient care unit floor (permitted to be arranged & located to serve more than one patient care unit) |  |  |
| 2.2-2.2.8.2 | ___ Administrative center or nurse station | Nurse Call System: |  |
| 2.1-2.8.2.1(1) | ___ space for counters | ___ Nurse master station | Table 2.1-2 |
| 2.1-2.8.2.1(2) | ___ handwashing station next to or directly accessible* or ___ hand sanitation dispenser next to or directly accessible* |  |  |
| 2.1-2.8.2.2 | ___ Center for reception & communication |  |  |
|  | ___ self-contained or ___ combined with administrative center or nurse station |  |  |
| 2.2-2.2.8.3 | ___ Documentation area |  |  |
| 2.1-2.8.3.1 | ___ work surface to support documentation process |  |  |
| 2.2-2.2.8.4 | ___ Nurse or supervisor office |  |  |
| 2.2-2.2.8.5 | ___ Multipurpose room |  |  |
| 2.1-2.8.5 | ___ at least one room in facility for patient conferences, reports, education, training sessions & consultation (may serve several patient care units & departments) |  |  |
| 2.2-2.2.8.7 | ___ Handwashing station |  |  |
| 2.1-2.8.7.1 | ___ located in each room where hands-on patient care is provided |  |  |
| 2.2-2.2.8.8 | ___ Medication safety zones |  |  |
| 2.1-2.8.8.1(2) | Design Promoting Safe Medication Use: |  |  |
| (a) | ___ medication safety zones located out of circulation paths |  |  |
| (b) | ___ work space designed so that staff can access information & perform required tasks |  |  |
| (c) | ___ work counters provide space to perform required tasks |  |  |
| (e) | ___ sharps containers placed at height that allows users to see top of container |  |  |
| (f) | ___ max. 45 dBA noise level caused by building systems |  |  |
| 2.1-2.8.8.2(1) | ___ medication preparation room |  |  |
| (a) | ___ under visual control of nursing staff |  |  |
| (b) | ___ work counter | Lighting: |  |
|  | ___ handwashing station | ___ Task lighting | 2.1-2.8.8.1(2)(d) |
|  | ___ lockable refrigerator | Ventilation: |  |
|  | ___ locked storage for controlled drugs | ___ Min. 4 air changes per hour | Table 7-1 |
|  | ___ sharps containers ☐ check if not included in project |  |  |
| (c) | ___ self-contained medication-dispensing unit ☐ check if not included in project |  |  |
|  | ___ room designed with space to prepare medications or |  |  |
| 2.1-2.8.8.2(2) | ___ automated medication-dispensing unit |  |  |
| (a) | ___ located at nurse station, in clean workroom or in alcove |  |  |
| (c) | ___ handwashing station or hand sanitation dispenser located next to stationary medication-dispensing units or stations |  |  |
| 2.2-2.2.8.9 | ___ Nourishment area or room |  |  |
| 2.1-2.8.9.2 |  | Ventilation: |  |
| (1) | ___ handwashing station | ___ Min. 2 air changes per hour | Table 7-1 |
| (2) | ___ work counter |  |  |
| (3) | ___ refrigerator |  |  |
| (4) | ___ microwave |  |  |
| (5) | ___ storage cabinets |  |  |
| (6) | ___ space for temporary storage of food service implements |  |  |
| 2.1-2.8.9.3 | ___ provisions & space for separate temporary storage of unused meal trays |  |  |
| 2.1-2.8.9.4 | ___ provisions & space for soiled meal trays |  |  |
| 2.2-2.2.8.10 | ___ Ice-making equipment ___ located in each patient care unit ___ equipment to provide ice for treatments & for nourishment |  |  |
| 2.2-2.2.8.11 | ___ Clean workroom or clean supply room |  |  |
| 2.1-2.8.11.2 | ___ clean workroom ___ used for preparing patient care items | Ventilation: ___ Min. 4 air changes per hour | Table 7-1 |
| (1) | ___ work counter | ___ Positive pressure |  |
| (2) | ___ handwashing station |  |  |
| (3) | ___ storage facilities for clean & sterile supplies or |  |  |
| 2.1-2.8.11.3 | ___ clean supply room | Ventilation: |  |
|  | ___ used only for storage & holding as part of system for distribution of clean & sterile supplies | ___ Min. 4 air changes per hour ___ Positive pressure | Table 7-1 |
| 2.2-2.2.8.12 | ___ Soiled workroom or soiled holding room |  |  |
| 2.1-2.8.12.2 | ___ soiled workroom | Ventilation: ___ Min. 10 air changes per hour | Table 7-1 |
| (1)(a) | ___ handwashing station | ___ Exhaust |  |
| (1)(b) | ___ flushing-rim clinical service sink with bedpan-rinsing device or equivalent flushing-rim fixture | ___ Negative pressure ___ No recirculating room units |  |
| (1)(c) | ___ work counter |  |  |
| (1)(d) | ___ space for separate covered containers for waste & soiled linen |  |  |
| (2) | ___ fluid management system is used ☐ check if not included in project |  |  |
| (a) | ___ electrical & plumbing connections that meet manufacturer requirements |  |  |
| (b) | ___ space for docking station or |  |  |
| 2.1-2.8.12.3 | ___ soiled holding room | Ventilation: ___ Min. 10 air changes per hour | Table 7-1 |
| (1) | ___ handwashing station or hand sanitation station | ___ Exhaust ___ Negative pressure |  |
| (2) | ___ space for separate covered containers for waste & soiled linen | ___ No recirculating room units |  |
| 2.1-2.8.13.1 | ___ Clean linen storage |  |  |
| (1) | ___ stored in clean workroom or clean supply room or ___ separate closet or ___ covered cart distribution system on each floor |  |  |
| (2) | ___ storage of clean linen carts in designated corridor alcoves, clean workroom or closets |  |  |
| 2.1-2.8.13.2 | ___ Equipment & supply storage room or alcoves ___ sized to provide min. 10 sf per patient bed |  |  |
| 2.1-2.8.13.3 | ___ Storage space for gurneys, stretchers & wheelchairs |  |  |
| 2.1-2.8.13.4 | ___ Emergency equipment storage |  |  |
| (1) | ___ each patient care unit has at least one emergency equipment storage location |  |  |
| (2) | ___ provided under visual observation of staff |  |  |
| (3) | ___ storage locations do not encroach on minimum required corridor width |  |  |
| 2.2-2.2.8.14 | ___ Environmental services room | Ventilation: |  |
| 2.1-2.8.14.1 | ___ readily accessible* to unit or floor it serves (permitted to serve more than one patient care unit on floor) | ___ Min. 10 air changes per hour ___ Exhaust ___ Negative pressure | Table 7-1 |
| 2.1-2.8.14.2 |  | ___ No recirculating room units |  |
| (1) | ___ service sink or floor-mounted mop sink |  |  |
| (2) | ___ provisions for storage of supplies & housekeeping equipment |  |  |
| (3) | ___ handwashing station or ___ hand sanitation station |  |  |
| 2.2-2.2.8.15 (1) | ___ Examination room ☐ check if not included in project (only if all patient rooms in patient care unit are single-patient rooms) |  |  |
|  | ___ designed for single patient |  |  |
| (2) | ___ serves only one patient care unit or ___ serves more than one patient care unit on same floor ___ centrally located |  |  |
| 2.1-2.1.2 | Patient privacy: |  |  |
|  | ___ provisions are made to address patient visual & speech privacy |  |  |
| 2.1-3.2.2.1 | Space Requirements: | Ventilation: |  |
| (1) | ___ min. clear floor area 120 sf ___ min. clear dimension 10’-0” | ___ Min. 6 air changes per hour | Table 7-1 |
| (2)(a) | ___ room size permits room arrangement with min. clearance 3’-0” at each side & at foot of exam table, recliner or chair | Lighting: ___ Portable or fixed exam light | 2.1-8.3.4.3(3) |
|  | ___ room arrangement (layout #1) shown in the plans | Power: ___ Min. 8 receptacles in total | Table 2.1-1 |
| (2)(b) | ___ exam table, recliner or chair is placed at angle closer to one wall | ___ Min. 4 receptacles convenient to head of gurney or bed |  |
|  | than another or against wall to accommodate type of patient being served | Nurse Call System: ___ Emergency call station | Table 2.1-2 |
|  | ☐ check if not included in project ___ room arrangement (layout #2) shown in the plans | Medical Gases: ___ 1 OX & 1 VAC | Table 2.1-3 |
| 2.1-3.2.2.2 |  |  |  |
| (2) | ___ storage for supplies |  |  |
| (3) | ___ accommodations for written or electronic documentation |  |  |
| (4) | ___ space for visitor’s chair |  |  |
| (5) | ___ handwashing station |  |  |
| 2.2-2.2.9 | SUPPORT AREAS FOR STAFF |  |  |
| 2.1-2.9.1 | ___ Staff lounge |  |  |
|  | ___ min.100 sf |  |  |
| 2.1-2.9.2 | ___ Staff toilet room (permitted to be unisex) |  |  |
| 2.1-2.9.2.1 | ___ readily accessible* to each patient care unit | Ventilation: ___ Min. 10 air changes per hour | Table 7-1 |
| 2.1-2.9.2.2 | ___ toilet & handwashing station | ___ Exhaust ___ Negative pressure ___ No recirculating room units |  |
| 2.1-2.9.3 | ___ Staff storage facilities |  |  |
| 2.1-2.9.3.1 | ___ securable closets or cabinet compartments for staff personal articles ___ located in or near nurse station |  |  |
| 2.2-2.2.10 | SUPPORT AREAS FOR PATIENTS FAMILIES & VISITORS |  |  |
| 2.2-2.2.10.1 | ___ Family & visitor lounge | Communications: |  |
|  | ___ each patient care unit provides access to lounge for family & visitors | ___ Public communication services provided in each family & visitor lounge | 2.1-2.10.1.6 |
| 2.1-2.10.1.1 | Size: |  |  |
| (1) | ___ accommodates at minimum 3 chairs & 1 wheelchair space |  |  |
| (2) | ___ accommodates at least 1 person for every 4 beds in unit |  |  |
| 2.1-2.10.1.2 | ___ immediately accessible* to patient care units served (permitted to serve more than one patient care unit) |  |  |
| 2.1-2.10.1.4 | ___ designed to minimize impact of noise & activity on patient rooms & staff functions |  |  |
| 2.2-2.2.10.2 |  |  |  |
| (1) | ___ Toilet room ___ handwashing station ___ readily accessible* to multipurpose room | Ventilation: ___ Min. 10 air changes per hour ___ Exhaust | Table 7-1 |
|  |  | ___ Negative pressure ___ No recirculating room units |  |
| 2.2-2.2.10.4 | ___ Place for meditation & prayer |  |  |
| 2.1-6.2.5 | ___ dedicated space accessible to the public provided to support meditation, bereavement & prayer |  |  |

*LOCATION TERMINOLOGY:

Directly accessible:  Connected to the identified area or room through a doorway, pass-through, or other opening without going through an intervening room or public space

Adjacent:  Located next to but not necessarily connected to the identified area or room

Immediately accessible:  Available either in or adjacent to the identified area or room

Readily accessible:  Available on the same floor or in the same clinic as the identified area or room

Architectural Details & MEP Requirements

| 2.1-7.2.2 | ARCHITECTURAL DETAILS |
| --- | --- |
| 2.1-7.2.2.1 | CORRIDOR WIDTH: |
| NFPA 101, 18.2.3.3 | ___ Aisles, corridors & ramps required for exit access in a hospital not less than 8'-0" in clear & unobstructed width or ___ Detailed code review incorporated in Project Narrative |
|  | ___ Aisles, corridors & ramps in adjunct areas not intended for the housing, treatment, or use of inpatients not less than 44” in clear & unobstructed width |
| 2.1-7.2.2.2 | CEILING HEIGHT: |
| (1) | ___ Min. ceiling height 7’-6” in corridors & in normally unoccupied spaces |
| (2) | ___ Min. ceiling height 9'-0" in seclusion rooms & secure holding rooms |
| (3) | ___ Min height 7’-6” above floor of suspended tracks rails & pipes located in traffic path for patients in beds & on stretchers |
|  | ___ Min ceiling height 7’-10” in other areas |
| (b) | ___ sliding doors ☐ check if not included in project |
|  | ___ manual or automatic sliding doors comply with NFPA 101 ___ detailed code review incorporated in Project Narrative ___ no floor tracks |
| (2) (a) | Door Opening to Patient Rooms: ___ min 45.5” clear door width ___ min 83.5” clear door height |
| (b) | ___ swinging doors for personnel use in addition to sliding doors ☐ check if not included in project ___ min clear width 34.5” |
| (3) | Door Swing: |
| (a) | ___ doors do not swing into corridors except doors in behavioral health units & doors to non-occupiable spaces (e.g. environmental services rooms & electrical closets) & doors with emergency breakaway hardware |
| (4) | ___ Lever hardware or push/pull latch hardware |
| (5) | Doors for Patient Bathing/Toilet Facilities: |
| (a) | ___ two separate doors or |
|  | ___ door that swings outward or |
|  | ___ door equipped with emergency rescue hardware (permits quick access from outside the room to prevent blockage of the door) or |
|  | ___ sliding door other than pocket door |
| (b) | ___ bathing area or toilet room opens onto public area or corridor ☐ check if not included in project |
|  | ___ visual privacy is maintained |
| 2.1-7.2.2.5 | WINDOWS IN PATIENT ROOMS: |
| 2.1-7.2.2.5(1) | ___ Each patient room provided with natural light by means of window to outside |
| 2.1-7.2.2.5(2) | ___ Operable windows in patient rooms or suites ☐ check if not included in project ___ window operation is limited with either stop limit/restrictor hardware or open guard/screen ___ prevents passage of 4-inch diameter sphere through opening |
| 2.1-7.2.2.6 | ___ insect screens |
| 2.1-7.2.2.5(3) | Window Size In Patient Rooms: |
| (a) | ___ minimum net glazed area be no less than 8% of required min. clear floor area of room served |
| (b) | ___ maximum 36 inches windowsill height above finished floor |
| 2.1-7.2.2.7 | GLAZING MATERIALS: ___ Glazing within 1 foot 6 inches of floor ☐ check if not included in project |
|  | ___ must be safety glass wire glass or plastic break-resistant material |
| 2.1-7.2.2.8 | HANDWASHING STATIONS: |
| (1)(c) | ___ Handwashing stations in patient care areas located so they are visible & unobstructed |
| (3) |  |
| (a) | ___ Handwashing station countertops made of porcelain stainless steel solid-surface materials or impervious plastic laminate assembly |
| (b) | ___ Countertops substrate ☐ check if not included in project ___ marine-grade plywood (or equivalent material) with impervious seal |
| (4) | ___ Handwashing station casework ☐ check if not included in project ___ designed to prevent storage beneath sink |
| (5) | ___ Provisions for drying hands |
| (a) | ___ hand-drying device does not require hands to contact dispenser |
| (b) | ___ hand-drying device is enclosed to protect against dust or soil & to ensure single-unit dispensing |
| (6) | ___ liquid or foam soap dispensers |
| 2.1-7.2.2.9 | GRAB BARS: |
| (1) | ___ Grab bars anchored to sustain concentrated load 250 pounds |
| (2) | ___ Grab bars in toilet rooms used by patients of size anchored to sustain concentrated load 800 pounds |
| (3) | ___ Ends of grab bars constructed to prevent snagging clothes of patients staff & visitors |
| 2.1-7.2.2.10 | HANDRAILS: |
| (1)(a) | ___ Installed on both sides of patient use corridors |
| (1)(b) | (may be omitted at nurse stations, doors, alcoves & fire extinguisher cabinets) |
| (2) | ___ Rail ends return to wall or floor |
| (3) | ___ Handrail gripping surfaces & fasteners are smooth (free of sharp or abrasive elements) |
| (4) | ___ Handrails have eased edges & corners |
| (5) | ___ Handrails have surface light reflectance value that contrasts with that of wall surface by min. 30% |
| (6) | ___ Handrail finishes are cleanable & able to withstand disinfection |
| 2.1-7.2.2.12 | NOISE CONTROL: |
| (1) | ___ Recreation rooms exercise rooms equipment rooms & similar spaces where impact noises may be generated are not located directly over patient bed areas or ___ Special provisions are made to minimize impact noise |
| (2) | ___ Noise reduction criteria in Table 1.2-6 applicable to partitions floors & ceiling construction are met in patient areas |
| 2.1-7.2.2.14 | DECORATIVE WATER FEATURES: |
| (1) | ___ No indoor unsealed water features |
| (2) | ___ Covered fish tanks ☐ check if not included in project ___ restricted to public areas |
| 2.1-7.2.3 | SURFACES |
| 2.1-7.2.3.1 | FLOORING & WALL BASES: |
| (1) | ___ Flooring surfaces cleanable & wear-resistant for location |
| (3) | ___ Smooth transitions provided between different flooring materials |
| (4) | ___ Flooring surfaces including those on stairways are stable firm & slip-resistant |
| (5) | ___ Floors & wall bases of soiled workrooms, toilet rooms & other areas subject to frequent wet cleaning are constructed of materials that are not physically affected by cleaning solutions |
| (7)(a) | Floors are monolithic & integral coved wall bases are at least 6” high & tightly sealed to wall in rooms listed below: |
|  | ___ airborne infection isolation (AII) room |
|  | ___ protective environment (PE) room ☐ check if not included in project |
|  | ___ combination AII/PE room ☐ check if not included in project |
|  | ___ anteroom to AII & PE rooms ☐ check if not included in project |
|  | ___ soiled workroom & soiled holding room |
| 2.1-7.2.3.2 | WALLS & WALL PROTECTION: |
| (1)(a) | ___ Wall finishes are washable |
| (1)(b) | ___ Wall finishes near plumbing fixtures are smooth, scrubbable & water-resistant |
| (2) | ___ Wall surfaces in areas routinely subjected to wet spray or splatter (e.g environmental services rooms) are monolithic or have sealed seams that are tight & smooth |
| (5) | ___ Wall protection devices & corner guards durable & scrubbable |
| 2.1-7.2.3.3 | CEILINGS: |
| (1) | ___ Ceilings provided in all areas except mechanical, electrical & communications equipment rooms |
| (a) | ___ Ceilings cleanable with routine housekeeping equipment |
| (b) | ___ Acoustic & lay-in ceilings where used do not create ledges or crevices |
| 2.1-7.2.4.1 | Built-In Furnishings: ☐ check if not included in project |
|  | ___ upholstered with impervious materials in patient treatment areas |
| 2.1-7.2.4.2 | Window Treatments in Patient Rooms & Other Patient Care Areas: |
| (1) | ___ blinds sheers or other patient-controlled window treatments provided to allow for patient privacy & to control light levels & glare |
| (2) | ___ window treatments do not compromise patient safety ___ easy for patients visitors & staff to operate |
| (3) | ___ window treatments selected for ease of cleaning disinfection or sanitization |
| 2.1-7.2.4.3 | ___ Privacy curtains in patient rooms & other patient care areas are washable ☐ check if not included in project |

| 2.1-8.2 | HEATING VENTILATION & AIR-CONDITIONING (HVAC) SYSTEMS |
| --- | --- |
| Part 3/6.1 | UTILITIES: |
| Part 3/6.1.1 | Ventilation Upon Loss of Electrical Power: ___ space ventilation & pressure relationship requirements of Tables 7.1 are maintained for AII Rooms & PE Rooms in event of loss of normal electrical power |
| Part 3/6.1.2 | Heating & Cooling Sources: |
| Part 3/6.1.2.1 | ___ heat sources & essential accessories are provided in number & arrangement sufficient to accommodate facility needs (reserve capacity) even when any one of heat sources is not operating ___ capacity of remaining source or sources is sufficient to provide for domestic hot water & to provide heating for intensive care nursery & inpatient rooms |
| Part 3/6.1.2.2 | Central cooling systems greater than 400 tons (1407 kW) peak cooling load ☐ check if not included in project ___ number & arrangement of cooling sources & essential accessories is sufficient to support owner’s facility operation plan upon breakdown or routine maintenance of any one of cooling sources |
| Part 3/6.2 | AIR-HANDLING UNIT (AHU) DESIGN: |
| Part 3/6.2.1 | ___ AHU casing is designed to prevent water intrusion resist corrosion & permit access |
| . |  |
| Part 3/6.3 | OUTDOOR AIR INTAKES & EXHAUST DISCHARGES: |
| Part 3/6.3.1 | Outdoor Air Intakes: |
| Part 3/6.3.1.1 | ___ located such that shortest distance from intake to any specific potential outdoor contaminant source be equal to or greater than separation distance listed in Table 6-1 |
|  | ___ located min of 25 ft from cooling towers & all exhaust & vent discharges ___ air intakes located away from public access ___ all intakes designed to prevent entrainment of wind-driven rain ___ contain features for draining away precipitation ___ equipped with birdscreen of mesh no smaller than 0.5 inches |
| Part 3/6.3.1.4 | ___ intake in areaway ☐ check if not included in project ___ bottom of areaway air intake opening is at least 6'-0" above grade ___ bottom of air intake opening from areaway into building is at least 3'-0" above bottom of areaway |
| Part 3/6.3.2 | Exhaust Discharges: |
| Part 3/6.3.2.1 | ___ ductwork within building is under negative pressure for exhaust of contaminated air (i.e air from AII rooms) |
|  | ___ exhaust discharge outlets with contaminated air located such that they reduce potential for recirculation of exhausted air back into building |
| Part 3/6.3.2.2 | ___ exhaust discharge outlets with contaminated air is arranged to discharge to atmosphere in vertical direction at least 10'-0" above adjoining roof level |
|  | ___ exhaust discharge outlets from AII rooms is located not less than 25’-0” horizontally from outdoor air intakes, openable windows/doors & areas that are normally accessible to public |
| Part 3/6.4 | FILTRATION: |
| a. | ___ Particulate matter filters, min. MERV-8 provided upstream of first heat exchanger surface of any air-conditioning system that combines return air from multiple rooms or introduces outdoor air |
| b. | ___ Outdoor air filtered in accordance with Table 7-1 |
| c. | ___ Air supplied from equipment serving multiple or different spaces is filtered in accordance with Table 7-1 |
| d. | ___ Air recirculated within room is filtered in accordance with Table 7-1 or Section 7.1(a)(5) |
| h. | ___ For spaces that do not permit air recirculated by means of room units & have minimum filter efficiency of MERV-14, MERV-16 or HEPA in accordance with Table 7-1, the min. filter requirement listed in Table 7-1 is installed downstream of all wet-air cooling coils & supply fan |
| Part 3/6.5 | HEATING & COOLING SYSTEMS: |
| Part 3/6.5.3 | ___ Radiant heating systems ☐ check if not included in project ___ ceiling or wall panels with exposed cleanable surfaces or radiant floor heating are provided in AII room PE room & burn unit |
| Part 3/6.7 | AIR DISTRIBUTION SYSTEMS: |
| Part 3/6.7.1 | ___ pressure relationships required in tables 7.1 maintained in all modes of HVAC system operation ___ Spaces that have required pressure relationships are served by fully ducted return systems or fully ducted exhaust systems ___ Inpatient facilities are served by fully ducted return or exhaust systems |
| Part 3/6.7.2 | Air Distribution Devices: |
|  | ___ supply air outlets comply with Table 6-2 |
| Part 3/6.7.3 | Smoke Barriers: ___ HVAC zones coordinated with compartmentation to minimize ductwork penetrations of fire & smoke barriers. |
| Part 3/6.8 | ENERGY RECOVERY SYSTEMS: ☐ check if not included in project |
| Part 3/6.8.1 | ___ Located upstream of filters required by Part 3/6.8.4 |
| Part 3/6.8.2 | ___ AII room exhaust systems or combination AII/PE rooms are not used for energy recovery |
| Part 3/7 | SPACE VENTILATION - HOSPITAL SPACES: |
| Part 3/7.1.a Part 3/7.1.a.1 | ___ Spaces ventilated according to Table 7-1 ___ Air movement is from clean to less-clean areas |
| Part 3/7.1.a.3 | ___ Min number of total air changes required for positive pressure rooms is provided by total supply airflow ___ Min number of total air changes required for negative pressure rooms is provided by total exhaust airflow |
| Part 3/7.1a.5 | ___ Air recirculation through room unit ☐ check if not included in project ___ complies with Table 7-1 |
|  | ___ room unit receive filtered & conditioned outdoor air ___ serve only single space |
|  | ___ provides min MERV 8 filter located upstream of any cold surface so that all of air passing over cold surface is filtered |
| Part 3/7.2 | ADDITIONAL ROOM-SPECIFIC REQUIREMENTS: |
| Part 3/7.2.1 | Airborne Infection Isolation (AII) Rooms ☐ check if not included in project |
|  | ___ AII rooms have permanently installed device and/or mechanism to constantly monitor differential air pressure between room & corridor ___ Local visual means is provided to indicate whenever negative differential pressure is not maintained |
|  | ___ Air from AII room is exhausted directly to outdoors |
|  | Exhaust air from AII rooms, associated anterooms & toilet rooms: ___ is discharged directly to outdoors without mixing with exhaust air from any other non-AII room or exhaust system |
|  | or |
|  | ___ is discharged into the general exhaust stream, provided the All exhaust air first passes through a HEPA filter (all exhaust ductwork kept under negative pressure) |
| Part 3/7.2.1 | ___ Exhaust air grille or register in patient room is located directly above patient bed on ceiling or on wall near head of bed |
|  | ___ Anteroom ☐ check if not included in project ___ AII room is at negative pressure with respect to anteroom ___ Anteroom is at negative pressure with respect to corridor |
| Part 3/7.2.2 | Protective Environment (PE) Rooms ☐ check if not included in project |
| Part 3/7.2.2 | ___ Supply air diffusers are located above patient bed |
|  | ___ Exhaust grilles or registers are located near patient room door |
|  | ___ PE rooms have permanently installed device to constantly monitor differential air pressure between room & corridor ___ Visual means is provided to indicate whenever positive differential pressure is not maintained |
| Part 3/7.2.3 | Combination Airborne Infectious Isolation/ Protective Environment Room (AII/PE) ☐ check if not included in project |
|  | ___ Supply air diffusers are located above patient bed |
|  | ___ Exhaust grilles or registers are located near patient room door. |
|  | ___ Anteroom ☐ check if not included in project |
|  | ___ anteroom is at positive pressure with respect to both AII/PE room & corridor or common space or |
|  | ___ anteroom is at negative pressure with respect to both AII/PE room & corridor or common space |
|  | ___ First device monitors pressure differential between AII/PE room & anteroom ___ Second device monitors pressure differential between anteroom & corridor or common space ___ Local visual means are provided to indicate whenever differential pressures are not maintained |

| 2.1-8.3 | ELECTRICAL SYSTEMS |
| --- | --- |
| 2.1-8.3.2.2 | Panelboards: |
| (1) | ___ panelboards serving life safety branch circuits serve floors on which they are located & floors immediately above & below |
| (2) | ___ panelboard critical branch circuits serve floors on which they are located |
| (3) | ___ panelboards not located in exit enclosures or exit passageways |
| 2.1-8.3.3 | POWER-GENERATING & -STORING EQUIPMENT |
| 2.1-8.3.3.1 | ___ Essential electrical system or emergency electrical power |
| (1) | ___ essential electrical system complies with NFPA 99 |
| (2) | ___ emergency electrical power complies with NFPA 99 |
| 2.1-8.3.4 | LIGHTING: |
| 2.1-8.3.4.1 |  |
| (1) | ___ Luminaires in patient areas shall have smooth, cleanable, impact-resistant lenses concealing light source |
| (2) | ___ Luminaires dissipate heat such that touchable surfaces will not burn occupants or ignite materials. |
| 2.1-8.3.4.2 |  |
| (1) | Patient rooms: |
| (a) | ___ provide general level of illumination ___ provide exam level of illumination |
| (b) | (may be dimmable & limited to patient care station) |
| (c) | ___ illumination for reading provided for each patient bed ___ patients must be able to adjust illumination without having to get out of bed |
| (d) | ___ no incandescent & halogen light sources |
| (e) | ___ light sources are either encapsulated or covered by diffuser or lens or use fixtures designed to contain fragments |
| (f) | Night-lighting: ___ at least one night-light fixture located in each patient room ___ night-lights used by staff that illuminate path from entry to bedside are switched at room entrance ___ night-light fixture located no more than 18 inches from finished floor illuminates pathway from bed to toilet room ___ night-light color temperature 2,700K or warmer |
| (2)(a) | ___ Corridors in patient care units have general illumination with provisions for reducing light levels at night |
| (3) | Exam/treatment rooms: ___ portable or fixed exam light |
| (6) | Food & nutrition areas: ___ light sources in kitchen & serving areas are either encapsulated or covered by diffuser or lens or use fixtures designed to contain fragments |
| (7) | ___ Uplight fixtures installed in patient care areas are covered |
| 2.1-8.3.5 | ELECTRICAL EQUIPMENT: |
| 2.1-8.3.5.1 | ___ Handwashing sinks that depend on building electrical service for operation are connected to essential electrical system |
| 2.1-8.3.6 | ELECTRICAL RECEPTACLES: |
| 2.1-8.3.6.1 | Receptacles In Corridors: |
| (1) | ___ duplex-grounded receptacles for general use installed 50’-0” apart or less in all corridors ___ duplex-grounded receptacles for general use installed within 25’-0” of corridor ends |
| (2) | ___ receptacles in pediatric & psychiatric unit corridors are of tamper-resistant type |
| 2.1-8.3.6.3 | Essential Electrical System Receptacles: |
| (1) | ___ cover plates for electrical receptacles supplied from essential electrical system are distinctively colored or marked for identification |
| (2) | ___ same color is used throughout facility |
| 2.1-8.4 | PLUMBING SYSTEMS |
| 2.1-8.4.2 | Plumbing & Other Piping Systems: |
| 2.1-8.4.2.1(3) | ___ no plumbing piping exposed overhead or on walls where possible accumulation of dust or soil may create cleaning problem |
| 2.1-8.4.2.2 | Hemodialysis/Hemoperfusion Water Distribution: ☐ check if not included in project |
| (1)(a) (2)(b) (1)(b) | ___ separate treated water distribution system ___ outlet at each individual hemodialysis treatment bay ___ outlet at hemodialysis equipment repair area ___ outlet at dialysate preparation area or ___ dialysis equipment includes sufficient water treatment provisions for use of domestic cold water |
| (1)(a) | ___ drainage system independent from tap water drainage |
| (4) | ___ liquid waste & disposal system for hemodialysis treatment area are designed to minimize odor & prevent backflow |
| (5) | ___ hemodialysis distribution piping is readily accessible* for inspection & maintenance |
| 2.1-8.4.2.5 | Heated potable water distribution systems: |
| (2) | ___ heated potable water distribution systems serving patient care areas are under constant recirculation to provide continuous hot water at each hot water outlet ___ non-recirculated fixture branch piping does not exceed 10 feet in length |
| (3)(a) (3)(c) | ___ no installation of dead-end piping (installation of empty risers mains & branches for future use is permitted) |
| (3)(b) | Renovations: ☐ check if not included in project |
|  | ___ dead-end piping is removed |
| 2.1-8.4.2.6 | Drainage Systems: |
| (1)(a) | ___ drainage piping above ceiling of or exposed in rooms listed below piping have special provisions to protect space below from leakage & condensation |
|  | - operating rooms - delivery rooms - procedure rooms - trauma rooms - nurseries - central kitchens - one-room sterile processing facilities - clean workroom of two-room sterile processing facilities - pharmacies - Class 2 & 3 imaging rooms - electronic mainframe rooms (EFs & TERs) - main switchgear - electrical rooms - electronic data processing areas - electric closets |
| (1)(b) | ___ drip pan for drainage piping above ceiling of sensitive area ☐ check if not included in project ___ accessible ___ overflow drain with outlet located in normally occupied area that is not open to restricted area |
| 2.1-8.4.3 | PLUMBING FIXTURES: |
| 2.1-8.4.3.1(1) | ___ Materials used for plumbing fixtures are non-absorptive & acid-resistant |
| 2.1-8.4.3.2 | Handwashing Station Sinks: |
| (1) | ___ designed with basins & faucets that reduce risk of splashing to areas where direct patient care is provided, sterile procedures are performed, medications are prepared or food is prepared |
| (2) | ___ sink basins have nominal size of no less than 144 square inches ___ sink basins have min dimension 9 inches in width or length |
| (3) | ___ sink basins are made of porcelain stainless steel or solid-surface materials |
| (5) | ___ water discharge point of faucets is at least 10 inches above bottom of basin |
| (7) | ___ anchored so that allowable stresses are not exceeded where vertical or horizontal force of 250 lbs. is applied |
| (8) | ___ sinks used by medical/nursing staff, patients & public have fittings that can be operated without using hands (may be single-lever or wrist blade devices) |
| (a) | ___ blade handles ☐ check if not included in project ___ at least 4 inches in length |
|  | ___ provide clearance required for operation |
| (b) | ___ sensor-regulated water fixtures ☐ check if not included in project |
|  | ___ meet user need for temperature & length of time water flows |
|  | ___ designed to function at all times & during loss of normal power |
| 2.1-8.4.3.3 | Showers & Tubs: |
| (1) | ___ nonslip surfaces |
| (2) | Surfaces for personal effects (e.g., shampoo, soap): ☐ check if not included in project |
|  | ___ surfaces for personal effects are recessed |
| 2.1-8.4.3.4 | Ice-Making Equipment: ___ copper tubing provided for supply connections to ice-making equipment |
| 2.1-8.4.3.5 | Clinical Sinks: ☐ check if not included in project |
| (1) (a) | ___ trimmed with valves that can are operated without hands (may be single-lever or wrist blade devices) |
| (b) | ___ handles are at least 6 in long |
| (2) | ___ integral trap wherein upper portion of water trap provides visible seal |
| 2.1-8.4.3.7 | Human waste disposal systems: |
| (1) | ___ bedpan-rinsing device |
| (a) | ___ provided in each inpatient toilet room (except in behavioral & alcohol-abuse units) |
| (b) | ___ use cold water only |
|  | or |
| (2) | ___ bedpan washer-disinfector system |
| (a) | ___ located in patient toilet room or soiled workroom |
| (b) | ___ electrical & plumbing connections that meet manufacturer requirements are provided |
|  | or |
| (3) | ___ disposable bedpan macerator system |
| (a) | ___ installed in soiled workroom |
| (b) | ___ electrical & plumbing connections per manufacturer requirements are provided |
| 2.1-8.4.4 | MEDICAL GAS & VACUUM SYSTEMS |
|  | ___ Station outlets provided as indicated in Table 2.1-3 |
| 2.1-8.5.1 | CALL SYSTEMS |
| 2.1-8.5.1.1(1) | ___ Nurse call stations provided as required in Table 2.1-2 |
| 2.1-8.5.1.1(2) | ___ Nurse call systems report to attended location with electronically supervised visual & audible annunciation as indicated in Table 2.1-2 |
| 2.1-8.5.1.1(4) | ___ Call system complies with UL 1069 “Standard for Hospital Signaling & Nurse Call Equipment” |
| 2.1-8.5.1.1(5) | ___ Wireless nurse call system ☐ check if not included in project |
|  | ___ complies with UL 1069 |
| 2.1-8.5.1.2 | Patient Call Stations: |
| (1) | ___ each patient sleeping bed except nursery beds provided with patient call station equipped for two-way voice communication |
| (2)(a) | ___ indicator light that remains lighted as long as voice circuit is operating |
| (2)(b) | ___ reset switch for canceling call |
| (3)(a) | ___ visible signal in corridor at patient’s door Multi-Corridor Patient Areas: ☐ check if not included in project |
|  | ___ additional visible signals at corridor intersections |
| (3)(b) | ___ visible & audible signal at the nurse master station of patient care units or patient care areas |
| 2.1-8.5.1.2(4) | ___ Nurse call system provided in each patient care area as required in Table 2.1-2 |
| 2.1-8.5.1.3 | Bath Stations: ___ bath station that can be activated by patient lying on floor provided at each patient toilet bathtub sitz bath or shower stall |
| (1) | ___ alarm in these areas can only be turned off at bath station where it was initiated |
| (2) | ___ shower/tub bath stations located 3'-0" to 4’-0” above floor within view of user & within reach of staff without need to step into shower or tub |
| (3) | ___ toilet bath stations located on the side of toilets within 12” of front of toilet bowl & 3'-0" to 4’-0” above floor |
| 2.1-8.5.1.5 | ___ Emergency call stations are equipped with continuous audible or visual confirmation to person who initiated the code call |
| 2.1-8.6.2 | ELECTRONIC SURVEILLANCE SYSTEMS ☐ check if not included in project |
| 2.1-8.6.2.1 | ___ Display screens in patient areas are mounted in tamper-resistant enclosure that is unobtrusive |
| 2.1-8.6.2.2 | ___ Display screens are located so they are not readily observable by general public or patients |
| 2.1-8.6.2.3 | ___ Electronic surveillance systems receive power from essential electrical system |