**COMPLIANCE CHECKLIST**

**IP30\_Public & Administrative Areas**

The following checklist is intended to be used in plan review applications for health care facilities submitted to Massachusetts Department of Public Health This checklist summarizes & references applicable requirements from Licensure Regulations & 2022 Edition of FGI Guidelines for Design & Construction of Hospitals Applicants must verify compliance of plans submitted to Department with all referenced requirements from Licensure Regulations & FGI Guidelines when completing this Checklist separate Checklist must be completed for each nursing unit hospital or clinic department or clinical suite

Other jurisdictions regulations & codes may have additional requirements which are not included in this checklist such as:

1. NFPA 101 Life Safety Code (2012) & applicable related standards contained in appendices of Code
2. State Building Code (780 CMR)
3. Accreditation requirements of Joint Commission
4. CDC Guidelines for Preventing Transmission of Mycobacterium Tuberculosis in Health Care Facilities
5. USP 797 & Regulations of Massachusetts Board of Registration in Pharmacy
6. Occupational Safety & Health Standards (OSHA)
7. Accessibility Guidelines of Americans with Disabilities Act (ADA)
8. Architectural Access Board Regulations (521 CMR)
9. Local Authorities having jurisdiction

Instructions:

1. All requirement lines must be completed according to following instructions & included in plan submissions for Self-Certification Process or Abbreviated Review Process
2. This checklist must be completed by project architect or engineer based on design actually reflected in plans at time of completion of checklist
3. Each requirement line (\_\_\_) of this Checklist must be completed exclusively with one of following marks unless otherwise directed in checklist If functional space is not affected by renovation project mark “E” may be indicated on requirement line (\_\_\_) before name of functional space (associated requirements on indented lines below that name or associated MEP requirements do not have to be completed in this case) If more than one functional space serves given required function (e.g patient room or exam room) that clarification should be provided in Project Narrative & requirement lines are understood to only address functional spaces that are involved in project

|  |  |
| --- | --- |
| **X** = Requirement is met for new space for renovated space or for existing direct support space for expanded service | ⌧ = Check box under section titles or individual requirements lines for optional services or functions that are not included in project area |
| **E** = Requirement relative to existing suite or area that has been *licensed* for its designated function is *not affected* by construction project & *does not pertain to required direct support space* for specific service affected by project “E” must not be used for existing required support space associated with new patient care room or area | **W** = Waiver requested for specific section of Regulations or FGI Guidelines where hardship in meeting requirement can be demonstrated (a Physical Plant Waiver Form must be completed for each waiver request) explicit floor plan or plan detail must be attached to each waiver request |

1. All room functions marked with "X" must be shown on plans with same name labels as in this checklist
2. Mechanical electrical & plumbing requirements are only partially mentioned in this checklist relevant section of FGI Guidelines must be used for project compliance with all MEP requirements & for waiver references
3. Oxygen vacuum medical air waste anesthesia gas disposal & instrument air outlets (if required) are identified respectively by abbreviations "OX" "VAC" "MA" “WAGD” & “IA”
4. Requirements referenced with “FI” result from formal interpretations from FGI Interpretations Task Group
5. The location requirements including asterisks (\*) refer to definitions of Glossary in beginning section of FGI Guidelines & reproduced in this checklist

|  |  |  |
| --- | --- | --- |
| Facility Name: |  | DoN Project Number: (if applicable) |
| Facility Address: |  |  |
| Satellite Name: (if applicable) |  | Building/Floor Location: |
| Satellite Address: (if applicable) |  | Submission Dates: |
| Project Description: |  | Initial Date:  Revision Date: |

|  | **Architectural Requirements** | **Building Systems Requirements** |  |
| --- | --- | --- | --- |
| 2.1‑6 | **PUBLIC AREAS**  check if not included in project |  |  |
|  |  |  |  |
| 2.1‑6.1.2 | Location: |  |  |
|  | \_\_\_ public areas clearly identified  \_\_\_ located to accommodate persons with disabilities |  |  |
|  |  |  |  |
| 2.1‑6.2.1 | \_\_\_ Vehicular drop‑off & pedestrian entrance |  |  |
|  | \_\_\_ minimum of one entrance are reachable from grade level |  |  |
|  |  |  |  |
| 2.1‑6.2.2 | \_\_\_ Reception area or lobby |  |  |
| 2.1‑6.2.2.1(1) | \_\_\_ access to information |  |  |
| 2.1‑6.2.2.1(2) | \_\_\_ public waiting area |  |  |
| 2.1‑6.2.2.1(3) | \_\_\_ public toilet room | Ventilation:  \_\_\_ Min 10 air changes per hour  \_\_\_ Exhaust  \_\_\_ Negative pressure  \_\_\_ No recirculating room units | Table 7-1 |
| (4) | \_\_\_ access to drinking water |  |  |
| (5) | \_\_\_ access to public communications services |  |  |
|  |  |  |  |
| 2.1‑6.2.3 | \_\_\_ Public waiting rooms or areas |  |  |
|  | \_\_\_ toilet room readily accessible to all public waiting rooms without passing through patient care or staff work areas |  |  |
|  |  |  |  |
| 2.1-6.2.5 | \_\_\_ Place for meditation bereavement & prayer  \_\_\_ dedicated space accessible to public |  |  |
|  |  |  |  |
| 2.1‑6.2.7 | \_\_\_ Wheelchair storage & parking space  check if not included in project  (only if no wheelchair owned by health care organization is made available for patient use) |  |  |
| 2.1‑6.2.7.1 | \_\_\_ designated area located out of required corridor width & directly accessible\* to entrance provided for storage of at least one wheelchair |  |  |
| 2.1‑6.2.7.2 | \_\_\_ wheelchair parking space |  |  |
|  | \_\_\_ facility provides services that require patients to transfer to facility chair wheelchair recliner examination table or gurney  \_\_\_ designated area is provided for parking at least one patient‑owned wheelchair in non‑public area  \_\_\_ located out of any required egress width or other required clearance  **or**  \_\_\_ facility does not provide services that require patients to transfer to facility chair wheelchair recliner examination table or gurney |  |  |
|  |  |  |  |
| 2.1‑6.3 | **ADMINISTRATIVE AREAS**  check if not included in project |  |  |
|  |  |  |  |
| 2.1‑6.3.1 | \_\_\_ Admissions area |  |  |
| 2.1‑6.3.1.1 | \_\_\_ separate waiting area for patients & accompanying persons |  |  |
| 2.1‑6.3.1.2 | \_\_\_ work counter or desk for staff |  |  |
| 2.1‑6.3.1.3 | \_\_\_ storage area for wheelchairs located out of path of egress |  |  |
|  |  |  |  |
| 2.1‑6.3.2 | \_\_\_ Interview space |  |  |
| 2.1‑6.3.2.1 | \_\_\_ space(s) for private interviews separate from public & patient areas |  |  |
| 2.1‑6.3.2.2 | (shared use of office or consultation room for this purpose is permitted) |  |  |
|  |  |  |  |
| 2.1‑6.3.4 | \_\_\_ Multipurpose room |  |  |
| 2.1‑6.3.4.1 | (several services or departments are permitted to share one multipurpose room) |  |  |
|  |  |  |  |
| 2.1‑6.3.5 | \_\_\_ Medical records area |  |  |
|  | \_\_\_ provisions made for securing medical records of all media types |  |  |
| 2.1‑6.3.5.1 | \_\_\_ location restricted to staff access to maintain confidentiality of records |  |  |
|  |  |  |  |
| 2.1‑6.4 | Support Areas for Staff & Volunteers: |  |  |
| 2.1‑6.4.2 | \_\_\_ Separate from those provided for public |  |  |
| 2.1‑6.4.1 | \_\_\_ Lounge  \_\_\_ Locker facilities |  |  |
|  | \_\_\_ Staff & volunteers toilet room | Ventilation:  \_\_\_ Min 10 air changes per hour  \_\_\_ Exhaust  \_\_\_ Negative pressure  \_\_\_ No recirculating room units | Table 7-1 |
| 2.1-6.4.3  2.1-6.4.3.1 | Lactation rooms  (may be shared by several services and/or departments) |  |  |
|  | \_\_\_ lactation rooms provided for use by staff & volunteers |  |  |
| 2.1-6.4.3.2 | \_\_\_ staff lactation rooms are separate from any public lactation rooms |  |  |
|  |  |  |  |

\*LOCATION TERMINOLOGY:

Directly accessible: Connected to identified area or room through doorway pass-through or other opening without going through intervening room or public space

Adjacent: Located next to but not necessarily connected to identified area or room

Immediately accessible: Available either in or adjacent to identified area or room

Readily accessible: Available on same floor or in same clinic as identified area or room

Architectural Details & MEP Requirements

|  |  |
| --- | --- |
| 2.1‑7.2.2 | **ARCHITECTURAL DETAILS** |
| 2.1‑7.2.2.1 | CORRIDOR WIDTH: |
|  | \_\_\_ Aisles, corridors & ramps in adjunct areas not intended for the housing, treatment, or use of inpatients not less than 44” in clear & unobstructed width |
|  |  |
| 2.1‑7.2.2.2 | CEILING HEIGHT: |
| (1) | \_\_\_ Min. ceiling height 7’-6” in corridors & in normally unoccupied spaces |
|  | \_\_\_ Min. ceiling height 7’‑10” in other areas |
|  |  |
| 2.1‑7.2.2.3  (1)  (a)  (b) | DOORS & DOOR HARDWARE:  Door Type:  \_\_\_ doors between corridors, rooms, or spaces subject to occupancy swing type or sliding doors  \_\_\_ sliding doors  check if not included in project |
|  | \_\_\_ manual or automatic sliding doors comply with NFPA 101  \_\_\_ detailed code review incorporated in Project Narrative  \_\_\_ no floor tracks |
|  |  |
| (3) | Door Swing: |
| (a) | \_\_\_ doors do not swing into corridors except doors to non‑occupiable spaces (e.g. environmental services rooms & electrical closets) & doors with emergency breakaway hardware |
|  |  |
| (4) | \_\_\_ Lever hardware or push/pull latch hardware |
|  |  |
| 2.1‑7.2.2.7 | GLAZING MATERIALS:  \_\_\_ Glazing within 1 foot 6 inches of floor must be safety glass, wire glass or plastic break‑resistant material |
|  |  |
| 2.1‑7.2.2.8 | HANDWASHING STATIONS: |
| (3)(a) | \_\_\_ Handwashing station countertops made of porcelain, stainless steel, solid‑surface materials or impervious plastic laminate assembly |
| (3)(b) | \_\_\_ Countertops substrate  check if not included in project  \_\_\_ marine‑grade plywood (or equivalent material) with impervious seal |
| (4) | \_\_\_ Handwashing station casework  check if not included in project  \_\_\_ designed to prevent storage beneath sink |
| (5) | \_\_\_ Provisions for drying hands  check if not included in project  (only at hand scrub facilities) |
| (a) | \_\_\_ hand‑drying device does not require hands to contact dispenser |
| (b) | \_\_\_ hand‑drying device is enclosed to protect against dust or soil & to ensure single‑unit dispensing |
| (6) | \_\_\_ liquid or foam soap dispensers |
| 2.1‑7.2.2.12 | NOISE CONTROL: |
| (2) | \_\_\_ Noise reduction criteria in Table 1.2‑6 applicable to partitions, floors & ceiling construction are met in patient areas |
| 2.1‑7.2.2.14 | DECORATIVE WATER FEATURES: |
| (1) | \_\_\_ No indoor unsealed water features |
| (2) | \_\_\_ Covered fish tanks  check if not included in project  \_\_\_ restricted to public areas |
|  |  |
| 2.1‑7.2.3 | **SURFACES** |
| 2.1‑7.2.3.1 | FLOORING & WALL BASES: |
| (1) | \_\_\_ Flooring surfaces cleanable & wear‑resistant for location |
| (3) | \_\_\_ Smooth transitions provided between different flooring materials |
| (4) | \_\_\_ Flooring surfaces including those on stairways are stable, firm & slip‑resistant |
| (5) | \_\_\_ Floors & wall bases of kitchens, soiled workrooms, toilet rooms & other areas subject to frequent wet cleaning are constructed of materials that are not physically affected by germicidal or other types of cleaning solutions |
|  |  |
| 2.1‑7.2.3.2 | WALLS & WALL PROTECTION: |
| (1)(a) | \_\_\_ Wall finishes are washable |
| (1)(b) | \_\_\_ Wall finishes near plumbing fixtures are smooth, scrubbable & water‑resistant |
| (2) | \_\_\_ Wall surfaces in areas routinely subjected to wet spray or splatter (e.g. kitchens, environmental services rooms) are monolithic or have sealed seams that are tight & smooth |
| (5) | \_\_\_ Wall protection devices & corner guards durable & scrubbable |
| 2.1‑7.2.3.3 | CEILINGS: |
| (1) | \_\_\_ Ceilings provided in all areas except mechanical, electrical & communications equipment rooms |
| (a) | \_\_\_ Ceilings cleanable with routine housekeeping equipment |
| (b) | \_\_\_ Acoustic & lay‑in ceilings where used not create ledges or crevices |

|  |  |
| --- | --- |
| 2.1‑8.2 | **HEATING VENTILATION & AIR‑CONDITIONING (HVAC) SYSTEMS** |
| Part 3/6.1.2 | Heating & Cooling Sources: |
| Part 3/6.1.2.1 | \_\_\_ provide heat sources & essential accessories in number & arrangement sufficient to accommodate facility needs (reserve capacity) even when any one of heat sources or essential accessories is not operating due to breakdown or routine maintenance |
|  | \_\_\_ capacity of remaining source or sources is sufficient to provide for domestic hot water sterilization & dietary purposes; fuel sufficient to support owner’s facility operation plan upon loss of fuel service is provided on site |
| Part 3/6.1.2.2 | Central cooling systems greater than 400 tons (1407 kW) peak cooling load  check if not included in project  \_\_\_ number & arrangement of cooling sources & essential accessories is sufficient to support owner’s facility operation plan upon breakdown or routine maintenance of any one of cooling sources. |
|  |  |
| Part 3/6.2 | AIR-HANDLING UNIT (AHU) DESIGN: |
| Part 3/6.2.1 | \_\_\_ AHU casing is designed to prevent water intrusion, resist corrosion & permit access for inspection & maintenance |
| Part 3/6.3 | OUTDOOR AIR INTAKES |
| Part 3/6.3.1.1 | \_\_\_ located such that shortest distance from intake to any specific potential outdoor contaminant source be equal to or greater than separation distance listed in Table 6-1 |
|  | \_\_\_ located min. of 25 ft from cooling towers & all exhaust & vent discharges  \_\_\_ facilities with moderate-to-high risk of natural or man-made extraordinary incidents locate new air intakes away from public access  \_\_\_ all intakes are designed to prevent entrainment of wind-driven rain  \_\_\_ contain features for draining away precipitation  \_\_\_ equipped with birdscreen of mesh no smaller than 0.5 in |
| Part 3/6.3.1.4 | \_\_\_ intake in areaway  check if not included in project  \_\_\_ bottom of areaway air intake opening is at least 6 ft above grade  \_\_\_ bottom of air intake opening from areaway into building is at least 3 ft above bottom of areaway |
|  |  |
| Part 3/6.4 | FILTRATION: |
| a. | \_\_\_ Particulate matter filters, minimum MERV-8 provided upstream of first heat exchanger surface of any air-conditioning system that combines return air from multiple rooms or introduces outdoor air. |
| b. | \_\_\_ Outdoor air filtered in accordance with Table 7-1 |
| c. | \_\_\_ Air supplied from equipment serving multiple or different spaces is filtered in accordance with Table 7-1 |
| d. | \_\_\_ Air recirculated within room be filtered in accordance with Table 7-1 or Section 7.1(a)(5) |
| e. | \_\_\_ Design includes all necessary provisions to prevent moisture accumulating on filters located downstream of cooling coils & humidifiers |
| h. | \_\_\_ For spaces that do not permit air recirculated by means of room units & have minimum filter efficiency of MERV-14, MERV-16 or HEPA in accordance with Table 7-1, the min. filter requirement listed in Table 7-1 is installed downstream of all wet-air cooling coils & supply fan |
|  |  |
| Part 3/6.7 | AIR DISTRIBUTION SYSTEMS: |
| Part 3/6.7.1 | \_\_\_ Maintain pressure relationships required in tables 7.1 in all modes of HVAC system operation  \_\_\_ Spaces that have required pressure relationships are served by fully ducted return systems or fully ducted exhaust systems |
|  |  |
| Part 3/6.7.2 | Air Distribution Devices: |
|  | \_\_\_ supply air outlets comply with Table 6-2 |
|  |  |
| Part 3/6.7.3 | Smoke Barriers:  \_\_\_ HVAC zones coordinated with compartmentation to minimize ductwork penetrations of fire & smoke barriers. |
|  |  |
| Part 3/6.8 | ENERGY RECOVERY SYSTEMS:  check if not included in project |
| Part 3/6.8.1 | \_\_\_ Located upstream of filters required by Part 3/6.8.4 |
|  |  |
| Part 3/7 | SPACE VENTILATION-HOSPITAL SPACES: |
| Part 3/7.1.a  Part 3/7.1.a.1 | \_\_\_ Spaces ventilated according to Table 7-1  \_\_\_ Air movement is from clean to less-clean areas |
|  |  |
| Part 3/7.1.a.3 | \_\_\_ Min. number of total air changes required for positive pressure rooms is provided by total supply airflow  \_\_\_ Min. number of total air changes required for negative pressure rooms is provided by total exhaust airflow |
| Part 3/7.1.a.4 | \_\_\_ Entire minimum outdoor air changes per hour required by Table 7-1 for each space meet filtration requirements of Section 6.4 |
|  |  |
| Part 3/7.1a.5 | \_\_\_ Air recirculation through room unit  check if not included in project  \_\_\_ complies with Table 7-1 |
|  | \_\_\_ room unit receive filtered & conditioned outdoor air  \_\_\_ serve only a single space |
|  | \_\_\_ provides min MERV 8 filter located upstream of any cold surface so that all of air passing over cold surface is filtered |

|  |  |
| --- | --- |
| 2.1‑8.3 | **ELECTRICAL SYSTEMS** |
|  |  |
| 2.1‑8.3.2 | **ELECTRICAL DISTRIBUTION & TRANSMISSION** |
| 2.1‑8.3.2.2 | Panelboards: |
| (1) | \_\_\_ panelboards serving life safety branch circuits serve floors on which they are located & floors immediately above & below |
| (2) | \_\_\_ panelboard critical branch circuits serve floors on which they are located |
| (3) | \_\_\_ panelboards not located in exit enclosures or exit passageways |
|  |  |
| 2.1-8.3.3 | **POWER-GENERATING & -STORING EQUIPMENT** |
| 2.1-8.3.3.1 | \_\_\_ Essential electrical system or emergency electrical power |
| (1) | \_\_\_ essential electrical system complies with NFPA 99 |
| (2) | \_\_\_ emergency electrical power complies with NFPA 99 |
|  |  |
| 2.1‑8.3.5 | **ELECTRICAL EQUIPMENT** |
| 2.1‑8.3.5.1 | \_\_\_ Handwashing sinks & scrub sinks that depends on building electrical service for operation are connected to essential electrical system |
| 2.1‑8.3.5.2 | \_\_\_ Electronic health record system servers & centralized storage provided with uninterruptible power supply |
|  |  |
| 2.1‑8.3.6 | **ELECTRICAL RECEPTACLES** |
| 2.1‑8.3.6.1 | Receptacles In Corridors: |
| (1) | \_\_\_ duplex‑grounded receptacles for general use installed 50’‑0” apart or less in all corridors  \_\_\_ duplex‑grounded receptacles for general use installed within 25’‑0” of corridor ends |
|  |  |
| 2.1‑8.3.6.3 | Essential Electrical System Receptacles: |
| (1) | \_\_\_ cover plates for electrical receptacles supplied from essential electrical system are distinctively colored or marked for identification |
| (2) | \_\_\_ same color is used throughout facility |
|  |  |
| 2.1‑8.4 | **PLUMBING SYSTEMS** |
| 2.1‑8.4.2 | Plumbing & Other Piping Systems: |
| 2.1‑8.4.2.1(3) | \_\_\_ no plumbing piping exposed overhead or on walls where possible accumulation of dust or soil may create cleaning problem  \_\_\_ no plumbing piping exposed overhead or on walls where leaks would create potential for food contamination |
| 2.1‑8.4.2.5 | Heated Potable Water Distribution Systems: |
| (2) | \_\_\_ heated potable water distribution systems serving patient care areas are under constant recirculation  \_\_\_ non‑recirculated fixture branch piping does not exceed 25’‑0” in length |
| (3)(a)  (3)(c) | \_\_\_ no installation of dead‑end piping (except for empty risers mains & branches for future use) |
| (3)(b) | \_\_\_ any existing dead‑end piping is removed  check if not included in project |
| (4)(a) | \_\_\_ water‑heating system supplies water at temperatures & amounts indicated in Table 2.1‑4 |
|  |  |
| 2.1‑8.4.2.6 | Drainage Systems: |
| (1)(a) | \_\_\_ drainage piping installed above ceiling of or exposed in rooms listed below piping have special provisions (e.g. double wall containment piping or oversized drip pans) to protect space below from leakage & condensation |
|  | * operating rooms * delivery rooms * procedure rooms * trauma rooms * nurseries * central kitchens * one-room sterile processing facilities * clean workroom of two-room sterile processing facilities * pharmacies * Class 2 & 3 imaging rooms * electronic mainframe rooms (EFs & TERs) * main switchgear * electrical rooms * electronic data processing areas * electric closets |
| (1)(b) | \_\_\_ drip pan for drainage piping above ceiling of sensitive area  check if not included in project  \_\_\_ accessible  \_\_\_ overflow drain with outlet located in normally occupied area that is not open to restricted area |
|  |  |
| 2.1‑8.4.3 | **PLUMBING FIXTURES** |
| 2.1‑8.4.3.1(1) | \_\_\_ Materials used for plumbing fixtures are non‑absorptive & acid‑resistant |
|  |  |
| 2.1‑8.4.3.2 | Handwashing Station Sinks: |
| (2) | \_\_\_ sink basins have nominal size of no less than 144 square inches  \_\_\_ sink basins have min. dimension 9 inches in width or length |
| (3) | \_\_\_ sink basins are made of porcelain, stainless steel or solid‑surface materials |
| (5) | \_\_\_ water discharge point of faucets is at least 10 inches above bottom of basin |
| (7) | \_\_\_ anchored so that allowable stresses are not exceeded where vertical or horizontal force of 250 lbs. is applied |
| (8) | \_\_\_ sinks used by medical & nursing staff, patients, public & food handlers have fittings that can be operated without using hands (may be single‑lever or wrist blade devices) |
| (a) | \_\_\_ blade handles  check if not included in project  \_\_\_ at least 4 inches in length |
|  | \_\_\_ provide clearance required for operation |
| (b) | \_\_\_ sensor‑regulated water fixtures  check if not included in project |
|  | \_\_\_ meet user need for temperature & length of time water flows |
|  | \_\_\_ designed to function at all times and during loss of normal power |
|  |  |
| 2.1‑8.6.2 | **ELECTRONIC SURVEILLANCE SYSTEMS**  check if not included in project |
| 2.1-8.6.2.1 | \_\_\_ Display screens in patient areas are mounted in tamper-resistant enclosure that is unobtrusive |
| 2.1-8.6.2.2 | \_\_\_ Display screens are located so they are not readily observable by general public or patients |
| 2.1‑8.6.2.3 | \_\_\_ Electronic surveillance systems receive power from essential electrical system |
|  |  |