COMPLIANCE CHECKLIST

IP9_Nursery Unit

The following checklist is intended to be used in the plan review applications for health care facilities submitted to the Massachusetts Department of Public Health.  This checklist summarizes and references the applicable requirements from the Licensure Regulations and the 2022 Edition of the FGI Guidelines for Design and Construction of Hospitals.  Applicants must verify compliance of the plans submitted to the Department with all referenced requirements from the Licensure Regulations and FGI Guidelines when completing this Checklist.  A separate Checklist must be completed for each nursing unit, hospital or clinic department, or clinical suite.

Other jurisdictions, regulations and codes may have additional requirements which are not included in this checklist, such as:

- NFPA 101 Life Safety Code (2012) and applicable related standards contained in the appendices of the Code

- State Building Code (780 CMR)

- Accreditation requirements of The Joint Commission

- CDC Guidelines for Preventing the Transmission of Mycobacterium Tuberculosis in Health Care Facilities

- USP 797 & Regulations of the Massachusetts Board of Registration in Pharmacy

- Occupational Safety & Health Standards (OSHA)

- Accessibility Guidelines of the Americans with Disabilities Act (ADA)

- Architectural Access Board Regulations (521 CMR)

- Local Authorities having jurisdiction.

Instructions:

- All requirement lines must be completed according to the following instructions and included in the plan submissions for Self-Certification Process or Abbreviated Review Process.

- This checklist must be completed by the project architect or engineer based on the design actually reflected in the plans at the time of completion of the checklist.

- Each requirement line (___) of this Checklist must be completed exclusively with one of the following marks, unless otherwise directed in the checklist.  If a functional space is not affected by a renovation project, the mark “E” may be indicated on the requirement line (___) before the name of the functional space (associated requirements on indented lines below that name, or associated MEP requirements do not have to be completed in this case).  If more than one functional space serves a given required function (e.g. patient room or exam room), that clarification should be provided in the Project Narrative, and the requirement lines are understood to only address the functional spaces that are involved in the project.

| X = Requirement is met, for new space, for renovated space, or for existing direct support space for an expanded service. | = Check box under section titles or individual requirements lines for optional services or functions that are not included in the project area. |
| --- | --- |
| E = Requirement relative to an existing suite or area that has been licensed for its designated function, is not affected by the construction project and does not pertain to a required direct support space for the specific service affected by the project. “E” must not be used for an existing required support space associated with a new patient care room or area. | W = Waiver requested for specific section of the Regulations or FGI Guidelines, where hardship in meeting requirement can be demonstrated (a Physical Plant Waiver Form must be completed for each waiver request). An explicit floor plan or plan detail must be attached to each waiver request. |

- All room functions marked with "X" must be shown on the plans with the same name labels as in this checklist.

- Mechanical, electrical & plumbing requirements are only partially mentioned in this checklist.  The relevant section of the FGI Guidelines must be used for project compliance with all MEP requirements and for waiver references.

- Oxygen, vacuum, medical air, waste anesthesia gas disposal and instrument air outlets (if required) are identified respectively by the abbreviations "OX", "VAC", "MA", “WAGD” & “IA”.

- Requirements referenced with “FI” result from formal interpretations from the FGI Interpretations Task Group.

- The location requirements including asterisks (*) refer to the definitions of the Glossary in the beginning section of the FGI Guidelines and reproduced in this checklist.

| Facility Name: |  | DoN Project Number: (if applicable) |
| --- | --- | --- |
| Facility Address: |  | Patient Care Unit Bed Complements: Current = Proposed = |
| Satellite Name: (if applicable) |  | Building/Floor Location: |
| Satellite Address: (if applicable) |  | Submission Dates: |
| Project Description: |  | Initial Date: Revision Date: |

|  | Architectural Requirements | Building Systems Requirements |  |
| --- | --- | --- | --- |
| 2.2-2.11 | NURSERY UNIT |  |  |
| 2.1-1.2.3 | Shared Services: |  |  |
|  | ___ No combined functions unless specifically allowed in this checklist |  |  |
| 2.2-2.11.1.1 | Location: ___ all nurseries are located in Obstetrical Unit or immediately accessible* to NICU |  |  |
| 2.2-2.11.1.2 | Layout: |  |  |
| (1) | ___ nurseries located & arranged to preclude need for unrelated pedestrian traffic |  |  |
| (2) | ___ no nursery opens directly onto another nursery |  |  |
| 2.2-2.11.1.3 | Safety & Security: |  |  |
| (1) | ___ all nurseries designed to protect physical security of infants, parents & staff & to minimize risk of infant abduction |  |  |
| (2) | ___ all entries to nursery are controlled |  |  |
| 2.2-2.11.2 | REQUIREMENTS FOR ALL NURSERY TYPES |  |  |
| 2.2-2.11.2.2 | Space Requirements: ___ enough space provided for parents to stay 24 hours |  |  |
| 2.2-2.11.2.3 | ___ Viewing windows ☐ check if not included in project ___ means to provide visual privacy |  |  |
| 2.2-2.11.2.4 | ___ Handwashing stations ___ at least one handwashing station for each eight or fewer infant stations |  |  |
| 2.2-2.11.2.5 | ___ Storage for linens & infant supplies provided at each nursery room |  |  |
| 130.624(C) | ___ All newborns in the nursery are in direct view of personnel accountable for them |  |  |
| 2.2-2.11.3 | REQUIREMENTS FOR SPECIFIC NURSERY TYPES |  |  |
| 2.2-2.11.3.1 | ___ Newborn nursery (Level I) |  |  |
| (1) (a) | Capacity: ___ each newborn nursery room contains no more than 16 infant stations | Ventilation: ___ Min. 6 air changes per hour ___ No recirculating room units | Table 7-1 |
| (b) | ___ total number of infant care stations determined according to rooming-in program | Power: ___ Min. 4 receptacles ___ convenient to each bassinet | Table 2.1-1 |
| (2) | ___ min. 3'-0" clearance between bassinets ___ min. 3'-0" clearance between each bassinet and any adjacent wall | Nurse Call System: ___ Staff assistance station ___ Emergency call station | Table 2.1-2 |
|  |  | Medical Gases: ___ 1 OX, 1 VAC , 1 MA per bassinet | Table 2.1-3 |
| 2.2-2.11.8.5(2) | ___ workroom or work area ___ each nursery room served by connecting workroom or work area |  |  |
| 2.2-2.11.8.5(1) |  |  |  |
| (a) | ___ handwashing station & gowning facilities at entrance for staff & families |  |  |
| (b) | ___ work counter |  |  |
| (c) | ___ refrigerator |  |  |
| (d) | ___ storage for supplies |  |  |
| (3) | ___ space required for work area located in nursery is in addition to area required for infant care |  |  |
| (4) | ___ provision be made for storage of emergency cart & equipment out of traffic |  |  |
| (5) | ___ provision be made for sanitary storage & disposal of soiled waste |  |  |
| (6) | ___ visual control be provided via view panels between staff work area & each nursery |  |  |
| 2.2-2.11.3.2 | ___ Continuing care nursery (Level IB) ☐ check if not included in project |  |  |
| (1)(b) | Location: |  |  |
|  | ___ location separate from NICU or ___ continuing care infant care stations located in defined area of NICU |  |  |
| (2) (a) | Space Requirements: ___ min. clear floor area 120 sf per infant care station | Ventilation: ___ Min. 6 air changes per hour ___ No recirculating room units | Table 7-1 |
| (b) | ___ min. clearance 8’-0” between adjacent* bassinets/infant beds ___ min. clearance 4’-0” between bassinets/infant beds & walls or other fixed obstructions ___ min. clearance 1’-0” at the head of each bassinet/infant bed | Power: ___ Min. 5 receptacles ___ convenient to head of each bed, crib, or bassinet ___ At least 50% receptacles on emergency power | Table 2.1-1 |
|  | ___ min. clearance 4’-0” between foot of bassinets/infant beds and cubicle curtains | Nurse Call System: ___ Staff assistance station ___ Emergency call station | Table 2.1-2 |
|  |  | Medical Gases: ___ 1 OX, 1 VAC , 1 MA per bassinet | Table 2.1-3 |
| 2.2-2.11.8.5(2) | ___ workroom or work area ___ each nursery room served by connecting workroom or work area |  |  |
| 2.2-2.11.8.5(1) |  |  |  |
| (a) | ___ handwashing station & gowning facilities at entrance for staff & families |  |  |
| (b) | ___ work counter |  |  |
| (c) | ___ refrigerator |  |  |
| (d) | ___ storage for supplies |  |  |
| (3) | ___ space required for work area located in nursery is in addition to area required for infant care |  |  |
| (4) | ___ provision be made for storage of emergency cart & equipment out of traffic |  |  |
| (5) | ___ provision be made for sanitary storage & disposal of soiled waste |  |  |
| (6) | ___ visual control be provided via view panels between staff work area & each nursery |  |  |
| 2.2-2.11.3.2 | ___ Special care nursery (Level II) ☐ check if not included in project |  |  |
| (1)(b) | Location: |  |  |
|  | ___ location separate from NICU or ___ special care infant care stations located in defined area of NICU |  |  |
| (2) (a) | Space Requirements: ___ min. clear floor area 120 sf per infant care station | Ventilation: ___ Min. 6 air changes per hour ___ No recirculating room units | Table 7-1 |
| (b) | ___ min. clearance 8’-0” between adjacent* bassinets/infant beds ___ min. clearance 4’-0” between bassinets/infant beds & walls or other fixed objects ___ min. clearance 4’-0” between foot of bassinets/infant beds and cubicle curtains | Power: ___ Min. 5 receptacles ___ convenient to head of each bed, crib, or bassinet ___ At least 50% receptacles on emergency power | Table 2.1-1 |
|  |  | Nurse Call System: ___ Staff assistance station ___ Emergency call station | Table 2.1-2 |
|  |  | Medical Gases: ___ 1 OX, 1 VAC , 1 MA per bassinet | Table 2.1-3 |
| 2.2-2.11.8.5(2) | ___ workroom |  |  |
| 130.624(D) | ___ special care nurseries are arranged so that entrance is gained solely through anteroom/workroom ___ well-lighted |  |  |
| 2.2-2.11.8.5(1) |  |  |  |
| (a) | ___ handwashing station & gowning facilities at entrance for staff & families |  |  |
| (b) | ___ work counter |  |  |
| (c) | ___ refrigerator |  |  |
| (d) | ___ storage for supplies |  |  |
| (3) | ___ provision be made for storage of emergency cart & equipment out of traffic |  |  |
| (4) | ___ provision be made for sanitary storage & disposal of soiled waste |  |  |
| (5) | ___ visual control provided via view panels between workroom and each nursery |  |  |
| 2.2-2.11.4 | SPECIAL PATIENT CARE ROOMS |  |  |
| 2.2-2.11.4.2 | ___ Airborne infection isolation (AII) room immediately accessible to at least one level of nursery care |  |  |
| (1) | ___ room enclosed & separated from nursery unit ___ provisions for observation of infant from adjacent* nurseries or control area |  |  |
| (2) |  |  |  |
| 2.1-2.4.2.2 | ___ complies with requirements applicable to patient rooms |  |  |
| (1) | ___ capacity one bed |  |  |
| (2) | ___ personal protective equipment (PPE) storage at entrance to room |  |  |
| (3) | ___ handwashing station |  |  |
| 2.1-2.4.2.3 | ___ Anteroom ☐ check if not included in project |  |  |
| (1) | ___ provides space for persons to don personal protective equipment (PPE) before entering patient room | Ventilation: ___ Min. 10 air changes per hour ___ Exhaust ___ No recirculating room units | Table 7-1 |
| (2) | ___ all doors to anteroom have self-closing devices or ___ audible alarm activated when AII room is in use as isolation room |  |  |
| (3)(a) | ___ handwashing station |  |  |
| (3)(b) | ___ storage for unused PPE |  |  |
| (3)(c) | ___ disposal/holding container for used PPE |  |  |
| 2.1-2.4.2.4 | Architectural Details & Furnishings: |  |  |
| (1)(a) | ___ perimeter walls ceiling & floor including penetrations constructed to prevent air exfiltration |  |  |
| (1)(b) | ___ self-closing devices on all room exit doors or ___ activation of audible alarm when AII room is in use as isolation room |  |  |
|  | ___ edge seals provided along sides & top of doorframe for any door into AII room |  |  |
| (2) (a) | ___ window treatments do not include fabric drapes & curtains |  |  |
| 2.1-7.2.3.1(7)(a) | ___ floors are monolithic & integral coved wall bases are at least 6” high & tightly sealed to wall |  |  |
| 2.1-2.4.2.5 | ___ room pressure visual or audible alarm |  |  |
| 2.2-2.11.8 | SUPPORT AREAS FOR NURSERIES |  |  |
| 2.2-2.11.8.3 | ___ Documentation area |  |  |
| 2.1-2.8.3.1 | ___ work surface to support documentation process |  |  |
| 2.2-2.11.8.8 | ___ Medication safety zone |  |  |
| 2.1-2.8.8.1(2) | Design Promoting Safe Medication Use: |  |  |
| (a) | ___ medication safety zones located out of circulation paths |  |  |
| (b) | ___ work space designed for staff to access information & perform required tasks | Lighting: ___ Task-specific lighting level min. 100 foot-candles | 2.1-2.8.8.1(2)(d) |
| (c) | ___ work counters provide space to perform required tasks |  |  |
| (e) | ___ sharps containers placed at height that allows users to see top of container |  |  |
| (f) | ___ max. 45 dBA noise level caused by building systems |  |  |
| 2.1-2.8.8.2(1) | ___ medication preparation room |  |  |
| (a) | ___ under visual control of nursing staff | Ventilation: |  |
| (b) | ___ work counter | ___ Min. 4 air changes per hour | Table 7-1 |
|  | ___ handwashing station | Lighting: |  |
|  | ___ lockable refrigerator | ___ Task lighting | 2.1-2.8.8.1(2)(d) |
|  | ___ locked storage for controlled drugs |  |  |
|  | ___ sharps containers ☐ check if not included in project |  |  |
| (c) | ___ self-contained medication-dispensing unit ☐ check if not included in project |  |  |
|  | ___ room designed with space to prepare medications or |  |  |
| 2.1-2.8.8.2(2) | ___ automated medication-dispensing unit |  |  |
| (a) | ___ located at nurse station, in clean workroom or in alcove | Lighting: ___ Task lighting | 2.1-2.8.8.1(2)(d) |
| (c) | ___ handwashing station or hand sanitation dispenser located next to stationary medication-dispensing units or stations |  |  |
| 2.2-2.11.8.12(1) | Soiled workroom or soiled holding room |  |  |
| 2.1-2.8.12.2 | ___ soiled workroom | Ventilation: |  |
| (1)(a) | ___ handwashing station | ___ Min. 10 air changes per hour | Table 7-1 |
| (1)(b) | ___ flushing-rim clinical service sink ☐ check if not included in project (if only disposable diapers are used) | ___ Exhaust ___ Negative pressure ___ No recirculating room units |  |
| (1)(c) | ___ work counter |  |  |
| (1)(d) | ___ space for separate covered containers for waste & soiled linen |  |  |
| (2) | ___ fluid management system is used ☐ check if not included in project |  |  |
| (a) | ___ electrical & plumbing connections that meet manufacturer requirements |  |  |
| (b) | ___ space for docking station or |  |  |
| 2.1-2.8.12.3 | ___ soiled holding room | Ventilation: ___ Min. 10 air changes per hour | Table 7-1 |
| (1) | ___ handwashing station or hand sanitation station | ___ Exhaust ___ Negative pressure |  |
| (2) | ___ space for separate covered containers for waste & soiled linen | ___ No recirculating room units |  |
| 2.2-2.11.8.14 | ___ Environmental services room | Ventilation: ___ Min. 10 air changes per hour | Table 7-1 |
| (1) (2) | ___ provided in nursery or ___ ES room is shared with obstetrical unit | ___ Exhaust ___ Negative pressure ___ No recirculating room units |  |
| 2.1-2.8.14.2 |  |  |  |
| (1) | ___ service sink or floor-mounted mop sink |  |  |
| (2) | ___ provisions for storage of supplies & housekeeping equipment |  |  |
| (3) | ___ handwashing station or ___ hand sanitation station |  |  |
| 2.2-2.11.8.15 | ___ Infant examination area |  |  |
| (1) | ___ work counter |  |  |
| (2) | ___ storage facilities |  |  |
| (3) | ___ handwashing station |  |  |
| 130.624(E)(3) | ___ appropriate facilities and necessary equipment for circumcision ___ readily available to the nursery |  |  |
| 2.2-2.11.8.16 | ___ Lactation support space |  |  |
|  | ___ immediately accessible* to nursery or ___ immediately accessible* to obstetrical unit served by nursery |  |  |
| 2.2-2.8.8.16 |  |  |  |
| (1) | ___ handwashing station ___ counter |  |  |

*LOCATION TERMINOLOGY:

Directly accessible:  Connected to the identified area or room through a doorway, pass-through, or other opening without going through an intervening room or public space

Adjacent:  Located next to but not necessarily connected to the identified area or room

Immediately accessible:  Available either in or adjacent to the identified area or room

Readily accessible:  Available on the same floor or in the same clinic as the identified area or room

Architectural Details & MEP Requirements

| 2.1-7.2.2 | ARCHITECTURAL DETAILS |
| --- | --- |
| 2.1-7.2.2.1 | CORRIDOR WIDTH: |
| NFPA 101, 18.2.3.3 | ___ Aisles, corridors & ramps required for exit access in a hospital not less than 8'-0" in clear & unobstructed width or ___ Detailed code review incorporated in Project Narrative |
|  | ___ Aisles, corridors & ramps in adjunct areas not intended for the housing, treatment, or use of inpatients not less than 44” in clear & unobstructed width |
| 2.1-7.2.2.2 | CEILING HEIGHT: |
| (1) | ___ Min. ceiling height 7’-6” in corridors & in normally unoccupied spaces |
| (2) | ___ Min. ceiling height 9'-0" in seclusion rooms & secure holding rooms |
| (3) | ___ Min height 7’-6” above floor of suspended tracks rails & pipes located in traffic path for patients in beds & on stretchers |
|  | ___ Min ceiling height 7’-10” in other areas |
| 2.1-7.2.2.3 (1) (a) | DOORS & DOOR HARDWARE: Door Type: ___ doors between corridors rooms or spaces subject to occupancy swing type or sliding doors |
| (b) | ___ sliding doors ☐ check if not included in project |
|  | ___ manual or automatic sliding doors comply with NFPA 101 ___ detailed code review incorporated in Project Narrative ___ no floor tracks |
| (2) (a) | Door Opening to Patient Rooms: ___ min 45.5” clear door width ___ min 83.5” clear door height |
| (b) | ___ swinging doors for personnel use in addition to sliding doors ☐ check if not included in project ___ min clear width 34.5” |
| (3) | Door Swing: |
| (a) | ___ doors do not swing into corridors except doors in behavioral health units & doors to non-occupiable spaces (e.g. environmental services rooms & electrical closets) |
| (4) | ___ Lever hardware or push/pull latch hardware |
| 2.1-7.2.2.7 | GLAZING MATERIALS: ___ Glazing within 1 foot 6 inches of floor ☐ check if not included in project |
|  | ___ must be safety glass wire glass or plastic break-resistant material |
| 2.1-7.2.2.8 | HANDWASHING STATIONS: |
| (1)(c) | ___ Handwashing stations in patient care areas located so they are visible & unobstructed |
| (3)(a) | ___ Handwashing station countertops made of porcelain stainless steel solid-surface materials or impervious plastic laminate assembly |
| (3)(b) | ___ Countertops substrate ☐ check if not included in project ___ marine-grade plywood (or equivalent material) with impervious seal |
| (4) | ___ Handwashing station casework ☐ check if not included in project ___ designed to prevent storage beneath sink |
| (5) | ___ Provisions for drying hands |
| (a) | ___ hand-drying device does not require hands to contact dispenser |
| (b) | ___ hand-drying device is enclosed to protect against dust or soil & to ensure single-unit dispensing |
| (6) | ___ liquid or foam soap dispensers |
| (7) | ___ no mirror at handwashing stations in nurseries |
| 2.1-7.2.2.12 | NOISE CONTROL: |
| (1) | ___ Recreation rooms exercise rooms equipment rooms & similar spaces where impact noises may be generated are not located directly over patient bed areas or ___ Special provisions are made to minimize impact noise |
| (2) | ___ Noise reduction criteria in Table 1.2-6 applicable to partitions floors & ceiling construction are met in patient areas |
| 2.1-7.2.2.14 | DECORATIVE WATER FEATURES: |
| (1) | ___ No indoor unsealed water features |
| (2) | ___ Covered fish tanks ☐ check if not included in project ___ restricted to public areas |
| 2.1-7.2.3 | SURFACES |
| 2.1-7.2.3.1 | FLOORING & WALL BASES: |
| (1) | ___ Flooring surfaces cleanable & wear-resistant for location |
| (3) | ___ Smooth transitions provided between different flooring materials |
| (4) | ___ Flooring surfaces including those on stairways are stable firm & slip-resistant |
| (5) | ___ Floors & wall bases of soiled workrooms, toilet rooms & other areas subject to frequent wet cleaning are constructed of materials that are not physically affected by cleaning solutions |
| (7)(a) | Floors are monolithic & integral coved wall bases are at least 6” high & tightly sealed to wall in rooms listed below: |
|  | ___ airborne infection isolation (AII) room |
|  | ___ protective environment (PE) room ☐ check if not included in project |
|  | ___ combination AII/PE room ☐ check if not included in project |
|  | ___ anteroom to AII & PE rooms ☐ check if not included in project |
|  | ___ soiled workroom & soiled holding room |
| 2.1-7.2.3.2 | WALLS & WALL PROTECTION: |
| (1)(a) | ___ Wall finishes are washable |
| (1)(b) | ___ Wall finishes near plumbing fixtures are smooth, scrubbable & water-resistant |
| (2) | ___ Wall surfaces in areas routinely subjected to wet spray or splatter (e.g environmental services rooms) are monolithic or have sealed seams that are tight & smooth |
| (5) | ___ Wall protection devices & corner guards durable & scrubbable |
| 2.1-7.2.3.3 | CEILINGS: |
| (1) | ___ Ceilings provided in all areas except mechanical, electrical & communications equipment rooms |
| (a) | ___ Ceilings cleanable with routine housekeeping equipment |
| (b) | ___ Acoustic & lay-in ceilings where used do not create ledges or crevices |
| 2.1-7.2.4.1 | Built-In Furnishings: ☐ check if not included in project |
|  | ___ upholstered with impervious materials in patient treatment areas |
| 2.1-7.2.4.3 | ___ Privacy curtains in patient rooms & other patient care areas are washable ☐ check if not included in project |

| 2.1-8.2 | HEATING VENTILATION & AIR-CONDITIONING (HVAC) SYSTEMS |
| --- | --- |
| Part 3/6.1 | UTILITIES: |
| Part 3/6.1.1 | Ventilation Upon Loss of Electrical Power: ___ space ventilation & pressure relationship requirements of Tables 7.1 are maintained for AII Rooms & PE Rooms in event of loss of normal electrical power |
| Part 3/6.1.2 | Heating & Cooling Sources: |
| Part 3/6.1.2.1 | ___ heat sources & essential accessories are provided in number & arrangement sufficient to accommodate facility needs (reserve capacity) even when any one of heat sources is not operating ___ capacity of remaining source or sources is sufficient to provide for domestic hot water & to provide heating for intensive care nursery & inpatient rooms |
| Part 3/6.1.2.2 | Central cooling systems greater than 400 tons (1407 kW) peak cooling load ☐ check if not included in project ___ number & arrangement of cooling sources & essential accessories is sufficient to support owner’s facility operation plan upon breakdown or routine maintenance of any one of cooling sources |
| Part 3/6.2 | AIR-HANDLING UNIT (AHU) DESIGN: |
| Part 3/6.2.1 | ___ AHU casing is designed to prevent water intrusion resist corrosion & permit access |
| . |  |
| Part 3/6.3 | OUTDOOR AIR INTAKES & EXHAUST DISCHARGES: |
| Part 3/6.3.1 | Outdoor Air Intakes: |
| Part 3/6.3.1.1 | ___ located such that shortest distance from intake to any specific potential outdoor contaminant source be equal to or greater than separation distance listed in Table 6-1 |
|  | ___ located min of 25 ft from cooling towers & all exhaust & vent discharges ___ air intakes located away from public access ___ all intakes designed to prevent entrainment of wind-driven rain ___ contain features for draining away precipitation ___ equipped with birdscreen of mesh no smaller than 0.5 inches |
| Part 3/6.3.1.4 | ___ intake in areaway ☐ check if not included in project ___ bottom of areaway air intake opening is at least 6'-0" above grade ___ bottom of air intake opening from areaway into building is at least 3'-0" above bottom of areaway |
| Part 3/6.3.2 | Exhaust Discharges: |
| Part 3/6.3.2.1 | ___ ductwork within building is under negative pressure for exhaust of contaminated air (i.e air from AII rooms) |
|  | ___ exhaust discharge outlets with contaminated air located such that they reduce potential for recirculation of exhausted air back into building |
| Part 3/6.3.2.2 | ___ exhaust discharge outlets with contaminated air is arranged to discharge to atmosphere in vertical direction at least 10'-0" above adjoining roof level |
|  | ___ exhaust discharge outlets from AII rooms is located not less than 25’-0” horizontally from outdoor air intakes, openable windows/doors & areas that are normally accessible to public |
| Part 3/6.4 | FILTRATION: |
| a. | ___ Particulate matter filters, min. MERV-8 provided upstream of first heat exchanger surface of any air-conditioning system that combines return air from multiple rooms or introduces outdoor air |
| b. | ___ Outdoor air filtered in accordance with Table 7-1 |
| c. | ___ Air supplied from equipment serving multiple or different spaces is filtered in accordance with Table 7-1 |
| d. | ___ Air recirculated within room is filtered in accordance with Table 7-1 or Section 7.1(a)(5) |
| h. | ___ For spaces that do not permit air recirculated by means of room units & have minimum filter efficiency of MERV-14, MERV-16 or HEPA in accordance with Table 7-1, the min. filter requirement listed in Table 7-1 is installed downstream of all wet-air cooling coils & supply fan |
| Part 3/6.5 | HEATING & COOLING SYSTEMS: |
| Part 3/6.5.3 | ___ Radiant heating systems ☐ check if not included in project ___ ceiling or wall panels with exposed cleanable surfaces or radiant floor heating are provided in AII room PE room & burn unit |
| Part 3/6.7 | AIR DISTRIBUTION SYSTEMS: |
| Part 3/6.7.1 | ___ pressure relationships required in tables 7.1 maintained in all modes of HVAC system operation ___ Spaces that have required pressure relationships are served by fully ducted return systems or fully ducted exhaust systems ___ Inpatient facilities are served by fully ducted return or exhaust systems |
| Part 3/6.7.2 | Air Distribution Devices: |
|  | ___ supply air outlets comply with Table 6-2 |
| Part 3/6.7.3 | Smoke Barriers: ___ HVAC zones coordinated with compartmentation to minimize ductwork penetrations of fire & smoke barriers. |
| Part 3/6.8 | ENERGY RECOVERY SYSTEMS: ☐ check if not included in project |
| Part 3/6.8.1 | ___ Located upstream of filters required by Part 3/6.8.4 |
| Part 3/6.8.2 | ___ AII room exhaust systems or combination AII/PE rooms are not used for energy recovery |
| Part 3/7 | SPACE VENTILATION - HOSPITAL SPACES: |
| Part 3/7.1.a Part 3/7.1.a.1 | ___ Spaces ventilated according to Table 7-1 ___ Air movement is from clean to less-clean areas |
| Part 3/7.1.a.3 | ___ Min number of total air changes required for positive pressure rooms is provided by total supply airflow ___ Min number of total air changes required for negative pressure rooms is provided by total exhaust airflow |
| Part 3/7.1a.5 | ___ Air recirculation through room unit ☐ check if not included in project ___ complies with Table 7-1 |
|  | ___ room unit receive filtered & conditioned outdoor air ___ serve only single space |
|  | ___ provides min MERV 8 filter located upstream of any cold surface so that all of air passing over cold surface is filtered |
| Part 3/7.2 | ADDITIONAL ROOM-SPECIFIC REQUIREMENTS: |
| Part 3/7.2.1 | Airborne Infection Isolation (AII) Rooms ☐ check if not included in project |
|  | ___ AII rooms have permanently installed device and/or mechanism to constantly monitor differential air pressure between room & corridor ___ Local visual means is provided to indicate whenever negative differential pressure is not maintained |
|  | ___ Air from AII room is exhausted directly to outdoors |
|  | Exhaust air from AII rooms, associated anterooms & toilet rooms: ___ is discharged directly to outdoors without mixing with exhaust air from any other non-AII room or exhaust system |
|  | or |
|  | ___ is discharged into the general exhaust stream, provided the All exhaust air first passes through a HEPA filter (all exhaust ductwork kept under negative pressure) |
| Part 3/7.2.1 | ___ Exhaust air grille or register in patient room is located directly above patient bed on ceiling or on wall near head of bed |
|  | ___ Anteroom ☐ check if not included in project ___ AII room is at negative pressure with respect to anteroom ___ Anteroom is at negative pressure with respect to corridor |
| Part 3/7.2.2 | Protective Environment (PE) Rooms ☐ check if not included in project |
| Part 3/7.2.2 | ___ Supply air diffusers are located above patient bed |
|  | ___ Exhaust grilles or registers are located near patient room door |
|  | ___ PE rooms have permanently installed device to constantly monitor differential air pressure between room & corridor ___ Visual means is provided to indicate whenever positive differential pressure is not maintained |
| Part 3/7.2.3 | Combination Airborne Infectious Isolation/ Protective Environment Room (AII/PE) ☐ check if not included in project |
|  | ___ Supply air diffusers are located above patient bed |
|  | ___ Exhaust grilles or registers are located near patient room door. |
|  | ___ Anteroom ☐ check if not included in project |
|  | ___ anteroom is at positive pressure with respect to both AII/PE room & corridor or common space or |
|  | ___ anteroom is at negative pressure with respect to both AII/PE room & corridor or common space |
|  | ___ First device monitors pressure differential between AII/PE room & anteroom ___ Second device monitors pressure differential between anteroom & corridor or common space ___ Local visual means are provided to indicate whenever differential pressures are not maintained |

| 2.1-8.3 | ELECTRICAL SYSTEMS |
| --- | --- |
| 2.1-8.3.2.2 | Panelboards: |
| (1) | ___ panelboards serving life safety branch circuits serve floors on which they are located & floors immediately above & below |
| (2) | ___ panelboard critical branch circuits serve floors on which they are located |
| (3) | ___ panelboards not located in exit enclosures or exit passageways |
| 2.1-8.3.3 | POWER-GENERATING & -STORING EQUIPMENT |
| 2.1-8.3.3.1 | ___ Essential electrical system or emergency electrical power |
| (1) | ___ essential electrical system complies with NFPA 99 |
| (2) | ___ emergency electrical power complies with NFPA 99 |
| 2.1-8.3.4 | LIGHTING: |
| 2.1-8.3.4.1(1) | ___ Luminaires in patient areas shall have smooth, cleanable, impact-resistant lenses concealing light source |
| 2.1-8.3.4.1(2) | ___ Luminaires dissipate heat such that touchable surfaces will not burn occupants or ignite materials. |
| 2.1-8.3.4.2 |  |
| (1) | Patient rooms: |
| (a) | ___ provide general level of illumination ___ provide exam level of illumination |
| (b) | (may be dimmable & limited to patient care station) |
| (d) | ___ no incandescent & halogen light sources |
| (e) | ___ light sources are either encapsulated or covered by diffuser or lens or use fixtures designed to contain fragments |
| (f) | Night-lighting: ___ at least one night-light fixture located in each patient room ___ night-lights used by staff that illuminate path from entry to bedside are switched at room entrance ___ night-light color temperature 2,700K or warmer |
| (2)(a) | ___ Corridors in patient care units have general illumination with provisions for reducing light levels at night |
| (3) | Exam/treatment rooms: ___ portable or fixed exam light |
| (6) | Food & nutrition areas: ___ light sources in kitchen & serving areas are either encapsulated or covered by diffuser or lens or use fixtures designed to contain fragments |
| (7) | ___ Uplight fixtures installed in patient care areas are covered |
| 2.1-8.3.5 | ELECTRICAL EQUIPMENT: |
| 2.1-8.3.5.1 | ___ Handwashing sinks that depend on building electrical service for operation are connected to essential electrical system |
| 2.1-8.3.6 | ELECTRICAL RECEPTACLES: |
| 2.1-8.3.6.1 | Receptacles In Corridors: |
| (1) | ___ duplex-grounded receptacles for general use installed 50’-0” apart or less in all corridors ___ duplex-grounded receptacles for general use installed within 25’-0” of corridor ends |
| 2.1-8.3.6.3 | Essential Electrical System Receptacles: |
| (1) | ___ cover plates for electrical receptacles supplied from essential electrical system are distinctively colored or marked for identification |
| (2) | ___ same color is used throughout facility |
| 2.1-8.4 | PLUMBING SYSTEMS |
| 2.1-8.4.2 | Plumbing & Other Piping Systems: |
| 2.1-8.4.2.1(3) | ___ no plumbing piping exposed overhead or on walls where possible accumulation of dust or soil may create cleaning problem |
| 2.1-8.4.2.5 | Heated potable water distribution systems: |
| (2) | ___ heated potable water distribution systems serving patient care areas are under constant recirculation to provide continuous hot water at each hot water outlet ___ non-recirculated fixture branch piping does not exceed 10 feet in length |
| (3)(a) (3)(c) | ___ no installation of dead-end piping (installation of empty risers mains & branches for future use is permitted) |
| (3)(b) | Renovations: ☐ check if not included in project |
|  | ___ dead-end piping is removed |
| 2.1-8.4.2.6 | Drainage Systems: |
| (1)(a) | ___ drainage piping above ceiling of or exposed in rooms listed below piping have special provisions to protect space below from leakage & condensation |
|  | - operating rooms - delivery rooms - procedure rooms - trauma rooms - nurseries - central kitchens - one-room sterile processing facilities - clean workroom of two-room sterile processing facilities - pharmacies - Class 2 & 3 imaging rooms - electronic mainframe rooms (EFs & TERs) - main switchgear - electrical rooms - electronic data processing areas - electric closets |
| (1)(b) | ___ drip pan for drainage piping above ceiling of sensitive area ☐ check if not included in project ___ accessible ___ overflow drain with outlet located in normally occupied area that is not open to restricted area |
| 2.1-8.4.3 | PLUMBING FIXTURES: |
| 2.1-8.4.3.1(1) | ___ Materials used for plumbing fixtures are non-absorptive & acid-resistant |
| 2.1-8.4.3.2 | Handwashing Station Sinks: |
| (1) | ___ designed with basins & faucets that reduce risk of splashing to areas where direct patient care is provided, sterile procedures are performed, medications are prepared or food is prepared |
| (2) | ___ sink basins have nominal size of no less than 144 square inches ___ sink basins have min dimension 9 inches in width or length |
| (3) | ___ sink basins are made of porcelain stainless steel or solid-surface materials |
| (5) | ___ water discharge point of faucets is at least 10 inches above bottom of basin |
| (7) | ___ anchored so that allowable stresses are not exceeded where vertical or horizontal force of 250 lbs. is applied |
| (8) | ___ sinks used by medical/nursing staff, patients & public have fittings that can be operated without using hands (may be single-lever or wrist blade devices) |
| (a) | ___ blade handles ☐ check if not included in project ___ at least 4 inches in length |
|  | ___ provide clearance required for operation |
| (b) | ___ sensor-regulated water fixtures ☐ check if not included in project |
|  | ___ meet user need for temperature & length of time water flows |
|  | ___ designed to function at all times & during loss of normal power |
| 2.1-8.4.3.4 | Ice-Making Equipment: ___ copper tubing provided for supply connections to ice-making equipment |
| 2.1-8.4.3.5 | Clinical Sinks: ☐ check if not included in project |
| (1) (a) | ___ trimmed with valves that can are operated without hands (may be single-lever or wrist blade devices) |
| (b) | ___ handles are at least 6 in long |
| (2) | ___ integral trap wherein upper portion of water trap provides visible seal |
| 2.1-8.4.3.7 | Human waste disposal systems: |
| (2) | ___ bedpan washer-disinfector system |
| (a) | ___ located in soiled workroom |
| (b) | ___ electrical & plumbing connections that meet manufacturer requirements are provided |
|  | or |
| (3) | ___ disposable bedpan macerator system |
| (a) | ___ installed in soiled workroom |
| (b) | ___ electrical & plumbing connections per manufacturer requirements are provided |
| 2.1-8.4.4 | MEDICAL GAS & VACUUM SYSTEMS |
|  | ___ Station outlets provided as indicated in Table 2.1-3 |
| 2.1-8.5.1 | CALL SYSTEMS |
| 2.1-8.5.1.1(1) | ___ Nurse call stations provided as required in Table 2.1-2 |
| 2.1-8.5.1.1(2) | ___ Nurse call systems report to attended location with electronically supervised visual & audible annunciation as indicated in Table 2.1-2 |
| 2.1-8.5.1.1(4) | ___ Call system complies with UL 1069 “Standard for Hospital Signaling & Nurse Call Equipment” |
| 2.1-8.5.1.1(5) | ___ Wireless nurse call system ☐ check if not included in project |
|  | ___ complies with UL 1069 |
| 2.1-8.5.1.2(4) | ___ Nurse call system provided in each patient care area as required in Table 2.1-2 |
| 2.1-8.5.1.5 | ___ Emergency call stations are equipped with continuous audible or visual confirmation to person who initiated the code call |
| 2.1-8.6.2 | ELECTRONIC SURVEILLANCE SYSTEMS ☐ check if not included in project |
| 2.1-8.6.2.1 | ___ Display screens in patient areas are mounted in tamper-resistant enclosure that is unobtrusive |
| 2.1-8.6.2.2 | ___ Display screens are located so they are not readily observable by general public or patients |
| 2.1-8.6.2.3 | ___ Electronic surveillance systems receive power from essential electrical system |