INDOOR AIR QUALITY ASSESSMENT

JFK Middle School

201 Manning Street

Hudson, Massachusetts

Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health

Indoor Air Quality Program

August 2010

# Background/Introduction

In response to a request from Mr. Sam Wong, Agent, Hudson Board of Health (HBOH), the Massachusetts Department of Public Health (MDPH), Bureau of Environmental Health (BEH) provided assistance and consultation regarding indoor air quality concerns at JFK Middle School (JFKMS), 201 Manning Street, Hudson, Massachusetts.  On March 26, 2010, Cory Holmes, an Environmental Analyst/Regional Inspector within BEH’s Indoor Air Quality (IAQ) Program visited the JFKMS to conduct an assessment.  Mr. Holmes was accompanied by Mike Feeney, Director, BEH/IAQ Program and Mr. Wong for portions of the assessment.

The JFKMS building complex is built into the side of a hill.  The main section of this school is a two-story, combination tan brick/cement/metal panel building, built in the early 1960s.  A one-story library and classroom wing exists at the rear of the building attached on the uphill side of the main building.  A one-story classroom wing is attached to the downhill side of the building and a modular classroom wing was added to the northeast side of the building.  It is important to note that at the time of the assessment the JFKMS was in Phase I of a building-wide feasibility study to address current and future needs of the building to present to the Massachusetts School Building Authority (MSBA) in order to obtain funding to build a new school.  If funding for the new building project is approved, town officials have estimated that construction would be conducted over the next several years.

# Methods

Air tests for carbon monoxide, carbon dioxide, temperature and relative humidity were conducted with the TSI, Q-Trak, IAQ Monitor, Model 7565.  Air tests for airborne particle matter with a diameter less than 2.5 micrometers were taken with the TSI, DUSTTRAK™ Aerosol Monitor Model 8520.  MDPH staff also performed visual inspection of building materials for water damage and/or microbial growth.  Moisture content of porous building materials was measured with a Delmhorst, BD-2000 Model, Moisture Detector equipped with a Delmhorst Standard Probe.

# Results

The school houses approximately 800 students in grades 6 to 8 with approximately 80 staff members.  Tests were taken during normal operations and results appear in Table 1.

# Discussion

## Ventilation

It can be seen from Table 1 that carbon dioxide levels were above 800 parts per million (ppm) in 23 of 42 areas at the time of the assessment, indicating poor air exchange in more than half of the areas surveyed.  These higher carbon dioxide levels are primarily attributed to deactivated/non-functional mechanical ventilation equipment.  It is also important to note that several classrooms had open windows and/or were empty/sparsely populated, which typically reduces carbon dioxide levels.  Carbon dioxide levels would be expected to be higher with full occupancy and/or windows closed.

Fresh air is supplied to most classrooms by unit ventilator (univent) systems.  A univent draws air from the outdoors through a fresh air intake located on the exterior wall of the building (Picture 1).  Return air from the classroom is drawn through an air intake located at the base of the unit (Figure 1).  Fresh and return air are mixed, filtered, heated and provided to classrooms through an air diffuser located in the top of the unit.  Univents were found deactivated and/or obstructed in many areas (Table 1/Pictures 2 and 3); therefore, there was limited means at best to provide mechanical ventilation to these classrooms at the time of the assessment.  The univent in classroom in classroom 27-C was reportedly deactivated due to excessive noise.  In order for univents to provide fresh air as designed, intakes/diffusers must remain free of obstructions.  Importantly, these units must remain ‘on’ and be allowed to operate while rooms are occupied.  In one case a univent was missing a panel exposing heated pipes (Picture 4), which could be a safety hazard.

The univents were installed when the building was originally constructed in the early 1960s.  According to the American Society of Heating, Refrigeration and Air-Conditioning Engineering (ASHRAE), the service life for a unit heater, hot water or steam is 20 years, assuming routine maintenance of the equipment (ASHRAE, 1991).  Despite attempts to maintain the univents (i.e., cleaning univents and changing filters regularly), the operational lifespan of this equipment has been exceeded.  Maintaining the balance of fresh air to exhaust air will be difficult with univents and exhaust vent motors/equipment of this vintage.

Exhaust ventilation in classrooms is provided by wall or ceiling vents ducted to rooftop motors.  Many exhaust vents were not drawing air and/or were obstructed (Table 1/Picture 5) at the time of the assessment.  As with univents, in order to function properly, exhaust vents must be activated and allowed to operate while rooms are occupied.  Without adequate supply and exhaust ventilation, excess heat and environmental pollutants can build up and lead to indoor air quality/comfort complaints.  In basement classrooms 13 and 37, the exhaust vents are located in closets and are sealed off from the classrooms (Pictures 6 and 7).  In order to provide a means of exhaust, passive wall vents should be installed to allow airflow to the exhaust vents.

Ventilation for the modular classroom is provided by an air-handling unit (AHU) located on the exterior of the building.  Fresh air is distributed to classrooms via ductwork connected to ceiling-mounted air diffusers.  Return vents draw air back to the AHU through wall or ceiling-mounted grilles.  A digital wall-mounted thermostat controls the heating, ventilating and air conditioning (HVAC) system.  The thermostat has fan settings of “on” and “automatic”.  The thermostat was set to the “automatic” setting at the time of the assessment.  The automatic setting on the thermostat activates the HVAC system at a preset temperature.  Once a preset temperature is measured by the thermostat, the HVAC system is deactivated.  Therefore, no mechanical ventilation is provided until the thermostat re-activates the system.  Due to tight building envelope construction, outdoor air infiltration through window frames and other unintentional sources is minimized; therefore little air exchange occurs when AHUs are deactivated by the thermostats.

To maximize air exchange, the MDPH recommends that both supply and exhaust ventilation operate continuously during periods of occupancy.  In order to have proper ventilation with a mechanical supply and exhaust system, the systems must be balanced to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room.  It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).  The date of the last balancing of these systems was not available at the time of the assessment.

The Massachusetts Building Code requires a minimum ventilation rate of 15 cubic feet per minute (cfm) per occupant of fresh outside air or have openable windows in each room (SBBRS, 1997; BOCA, 1993).  The ventilation must be on at all times that the room is occupied.  Providing adequate fresh air ventilation with open windows and maintaining the temperature in the comfort range during the cold weather season is impractical.  Mechanical ventilation is usually required to provide adequate fresh air ventilation.

Carbon dioxide is not a problem in and of itself.  It is used as an indicator of the adequacy of the fresh air ventilation.  As carbon dioxide levels rise, it indicates that the ventilating system is malfunctioning or the design occupancy of the room is being exceeded.  When this happens, a buildup of common indoor air pollutants can occur, leading to discomfort or health complaints.  The Occupational Safety and Health Administration (OSHA) standard for carbon dioxide is 5,000 parts per million parts of air (ppm).  Workers may be exposed to this level for 40 hours/week, based on a time-weighted average (OSHA, 1997).

The MDPH uses a guideline of 800 ppm for publicly occupied buildings.  A guideline of 600 ppm or less is preferred in schools due to the fact that the majority of occupants are young and considered to be a more sensitive population in the evaluation of environmental health status.  Inadequate ventilation and/or elevated temperatures are major causes of complaints such as respiratory, eye, nose and throat irritation, lethargy and headaches.  For more information concerning carbon dioxide, consult Appendix A.

Temperature measurements ranged from 66o F to 78o F, which were within the MDPH recommended comfort range in all but two of the areas surveyed during the assessment (Table 1).  The MDPH recommends that indoor air temperatures be maintained in a range of 70o F to 78o F in order to provide for the comfort of building occupants.  Temperature control complaints (primarily heat complaints) were reported in classrooms 1 and 1-C, mainly due to solar gain.  Also of note was the condition of windows (loose panes, missing/damaged caulking), which can allow for drafts making temperature control difficult.  In many cases concerning indoor air quality, fluctuations of temperature in occupied spaces are typically experienced, even in a building with an adequate fresh air supply.  In addition, it is difficult to control temperature and maintain comfort without operating the ventilation equipment as designed (e.g., univents/exhaust vents deactivated/obstructed).

The relative humidity measured in the building ranged from 15 to 37 percent, which was below the MDPH recommended comfort range in all areas surveyed during the assessment (Table 1).  The MDPH recommends a comfort range of 40 to 60 percent for indoor air relative humidity.  Relative humidity levels in the building would be expected to drop during the winter months due to heating.  The sensation of dryness and irritation is common in a low relative humidity environment.  Low relative humidity is a very common problem during the heating season in the northeast part of the United States.

## Microbial/Moisture Concerns

In order for building materials to support mold growth, a source of water exposure is necessary (e.g., roof/plumbing leaks).  Identification and elimination of water moistening building materials is necessary to control mold growth.  The building has a history of chronic roof/building envelope leaks.  School officials reported that efforts have been made to patch the roof in many areas.  However, numerous areas had water-damaged/missing ceiling tiles remaining (Table 1/Picture 8).  Water-damaged ceiling tiles can provide a source of mold and should be replaced after a water leak is discovered and repaired.  However, according to school officials many of the ceiling tiles reportedly contain asbestos, thus they are left in place to avoid disturbing asbestos containing materials.

Intact asbestos-containing materials do not pose a health hazard.  If damaged, asbestos-containing materials can become “friable” and aerosolized.  Friable asbestos is a chronic (long-term) health hazard that can lead to serious lung disease (i.e., mesothelioma).  These types of health impacts are very different from those more typically associated with indoor air quality comfort problems (e.g., headache, fatigue).  Where asbestos-containing materials are found damaged, these materials should be removed or remediated in a manner consistent with Massachusetts asbestos remediation laws (MDLI, 1993).

It is also important to note that schools should be in compliance with the Asbestos Hazard Emergency Response Act (AHERA), which requires inspection of asbestos-containing materials every three years.  In addition, a semi-annual walkthrough is required to determine current conditions of asbestos-containing materials.  AHERA requires public and private non-profit primary and secondary schools to inspect their buildings for asbestos-containing building materials and to develop, maintain and update an asbestos management plan to be kept at the school (US EPA, 1986).

Severely damaged/loose/missing interior and exterior caulking around windows was noted throughout the building (Pictures 9 through 13).  Depending on its age, this sealant (in addition to sealant on the exterior of the building) may contain regulated materials [e.g., asbestos, polychlorinated biphenyls (or PCBs)].  If so, materials should be addressed in accordance with EPA regulations.  For further information on addressing PCB-containing materials in schools, consult MDPH guidance (Appendix B).

BEH staff also examined the building exterior to identify breaches or other issues in the building envelope that could provide a source of water penetration.  Several potential sources were identified:

- Missing/damaged sealant between expansion joints and masonry (Picture 14);

- Damaged/delaminating exterior wooden doors (Pictures 15 and 16);

- Damaged/crumbling masonry (Picture 17 and 18);

- Moss growth on exterior ledge, indicating chronic water exposure (Picture 19);

- Damaged downspouts and downspouts empting in close proximity to the base of the modular building (Picture 20); and

- Damaged missing panels to exterior siding for the modular building (Picture 21).

The conditions listed above can undermine the integrity of the building envelope and create/provide a means of water entry by capillary action into the building through exterior walls, foundation concrete and masonry (Lstiburek & Brennan, 2001).  The freezing and thawing action of water during the winter months can create cracks and fissures in the foundation.  In addition, they can serve as pathways for insects, rodents and other pests into the building.

Repeated water damage to porous building materials can result in microbial growth.  The US Environmental Protection Agency (US EPA) and the American Conference of Governmental Industrial Hygienists (ACGIH) recommend that porous materials be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2001; ACGIH, 1989).  If not dried within this time frame, mold growth may occur.  Once mold has colonized porous materials, they are difficult to clean and should be removed.

Plants were noted in several classrooms.  Plants can be a source of pollen and mold, which can be respiratory irritants for some individuals.  Plants should be properly maintained and equipped with drip pans to prevent water damage to porous building materials, which can lead to mold growth.  Plants should also be located away from ventilation sources (e.g., air intakes, univent diffusers) to prevent the entrainment and/or aerosolization of dirt, pollen or mold.  Also of note was the presence of lawn/plant debris accumulated in the bottom of the univent fresh air intakes (Picture 1).  With repeated water exposure, these accumulated materials can become moistened, resulting in potential mold growth, particularly within several days after rainstorms.

## Other IAQ Evaluations

Indoor air quality can be negatively influenced by the presence of respiratory irritants, such as products of combustion.  The process of combustion produces a number of pollutants.  Common combustion emissions include carbon monoxide, carbon dioxide, water vapor and smoke (fine airborne particle material).  Of these materials, exposure to carbon monoxide and particulate matter with a diameter of 2.5 micrometers (μm) or less (PM2.5) can produce immediate, acute health effects upon exposure.  To determine whether combustion products were present in the indoor environment, BEH staff obtained measurements for carbon monoxide and PM2.5.

### Carbon Monoxide

Carbon monoxide is a by-product of incomplete combustion of organic matter (e.g., gasoline, wood and tobacco).  Exposure to carbon monoxide can produce immediate and acute health affects.  Several air quality standards have been established to address carbon monoxide and prevent symptoms from exposure to these substances.  The MDPH established a corrective action level concerning carbon monoxide in ice skating rinks that use fossil-fueled ice resurfacing equipment.  If an operator of an indoor ice rink measures a carbon monoxide level over 30 ppm, taken 20 minutes after resurfacing within a rink, that operator must take actions to reduce carbon monoxide levels (MDPH, 1997).

The American Society of Heating Refrigeration and Air-Conditioning Engineers (ASHRAE) has adopted the National Ambient Air Quality Standards (NAAQS) as one set of criteria for assessing indoor air quality and monitoring of fresh air introduced by HVAC systems (ASHRAE, 1989).  The NAAQS are standards established by the US EPA to protect the public health from six criteria pollutants, including carbon monoxide and particulate matter (US EPA, 2006).  As recommended by ASHRAE, pollutant levels of fresh air introduced to a building should not exceed the NAAQS levels (ASHRAE, 1989).  The NAAQS were adopted by reference in the Building Officials & Code Administrators (BOCA) National Mechanical Code of 1993 (BOCA, 1993), which is now an HVAC standard included in the Massachusetts State Building Code (SBBRS, 1997).  According to the NAAQS, carbon monoxide levels in outdoor air should not exceed 9 ppm in an eight-hour average (US EPA, 2006).

Carbon monoxide should not be present in a typical, indoor environment.  If it is present, indoor carbon monoxide levels should be less than or equal to outdoor levels.  On the day of the assessment, outdoor carbon monoxide concentrations were non-detect (ND) (Table 1).  No measurable levels of carbon monoxide were detected inside the building (Table 1).

### Particulate Matter

The US EPA has established NAAQS limits for exposure to particulate matter.  Particulate matter is airborne solids that can be irritating to the eyes, nose and throat.  The NAAQS originally established exposure limits to particulate matter with a diameter of 10 μm or less (PM10).  According to the NAAQS, PM10 levels should not exceed 150 micrograms per cubic meter (μg/m3) in a 24-hour average (US EPA, 2006).  These standards were adopted by both ASHRAE and BOCA.  Since the issuance of the ASHRAE standard and BOCA Code, US EPA established a more protective standard for fine airborne particles.  This more stringent PM2.5 standard requires outdoor air particle levels be maintained below 35 μg/m3 over a 24-hour average (US EPA, 2006).  Although both the ASHRAE standard and BOCA Code adopted the PM10 standard for evaluating air quality, MDPH uses the more protective PM2.5 standard for evaluating airborne particulate matter concentrations in the indoor environment.

Outdoor PM2.5 concentrations were measured at 4 μg/m3 (Table 1).  PM2.5 levels measured indoors ranged from 5 to 18 μg/m3 (Table 1), which were below the NAAQS PM2.5 level of 35 μg/m3.  Frequently, indoor air levels of particulates (including PM2.5) can be at higher levels than those measured outdoors.  A number of mechanical devices and/or activities that occur indoors can generate particulate during normal operations.  Sources of indoor airborne particulates may include but are not limited to particles generated during the operation of fan belts in the HVAC system, use of stoves and/or microwave ovens in kitchen areas; use of photocopiers, fax machines and computer printing devices; operation of an ordinary vacuum cleaner and heavy foot traffic indoors.

### Volatile Organic Compounds

Indoor air quality can also be negatively influenced by the presence of materials containing volatile organic compounds (VOCs).  VOCs are carbon-containing substances that have the ability to evaporate at room temperature.  Frequently, exposure to low levels of total VOCs (TVOCs) may produce eye, nose, throat and/or respiratory irritation in some sensitive individuals.  For example, chemicals evaporating from a paint can stored at room temperature would most likely contain VOCs.  In an effort to identify materials that can potentially increase indoor VOC concentrations, BEH staff examined classrooms and common areas for products containing these respiratory irritants.

The majority of classrooms contained dry erase boards and related materials.  Materials such as dry erase markers and dry erase board cleaners may contain VOCs, such as methyl isobutyl ketone, n-butyl acetate and butyl-cellusolve (Sanford, 1999), which can be irritating to the eyes, nose and throat.

Air deodorizers and other scented materials were observed in some areas (Table 1).  Air deodorizers can contain chemicals that can be irritating to the eyes, nose and throat of sensitive individuals.  Furthermore, deodorizing agents do not remove materials causing odors, but rather mask odors that may be present in the area.

In an effort to reduce noise from sliding desks/chairs, tennis balls were observed sliced open and placed on the base of the legs (Table 1).  Tennis balls are made of a number of materials that are a source of respiratory irritants.  Constant wearing of tennis balls can produce fibers and cause VOCs to off-gas.  Tennis balls are made with a natural rubber latex bladder, which becomes abraded when used as a chair leg pad.  Use of tennis balls in this manner may introduce latex dust into the school environment.  Some individuals are highly allergic to latex (e.g., spina bifida patients) (SBAA, 2001).  It is recommended that the use of materials containing latex be limited in buildings to reduce the likelihood of symptoms in sensitive individuals (NIOSH, 1997).

## Other Conditions

Other conditions that can affect indoor air quality were observed during the assessment.  In several classrooms, items were observed on the floor, windowsills, tabletops, counters, bookcases and desks (Pictures 2 and 3).  The large number of items stored in classrooms provides a source for dusts to accumulate.  These items (e.g., papers, folders, boxes) make it difficult for custodial staff to clean.  Items should be relocated and/or be cleaned periodically to avoid excessive dust build up.  In addition, these materials can accumulate on flat surfaces (e.g., desktops, shelving and carpets) in occupied areas and subsequently be re-aerosolized causing further irritation.

A number of air diffusers, exhaust/return vents and personal fans were observed to have accumulated dust.  If exhaust vents are not functioning, backdrafting can occur, which can re-aerosolize accumulated dust particles.  Re-activated univents and fans can also aerosolize dust accumulated on vents/fan blades.

Large pillows and cushions were seen on the floor in several classrooms (Table 1).  Upholstered furniture, pillows and cushions are covered with fabric that comes in contact with human skin.  This type of contact can leave oils, perspiration, hair and skin cells.  Dust mites feed upon human skin cells and excrete waste products that contain allergens.  In addition, if relative humidity levels increase above 60 percent, dust mites tend to proliferate (US EPA, 1992).  In order to remove dust mites and other pollutants, frequent vacuuming of upholstered furniture is recommended (Berry, M.A., 1994).  It is also recommended that upholstered furniture (if present in schools), be professionally cleaned on an annual basis.  If outdoor conditions or indoor activities (e.g., renovations) create an excessively dusty environment, cleaning frequency should be increased (every six months) (IICRC, 2000).

Restrooms are equipped with mechanical exhaust vents.  Several of the vents were not drawing air at the time of the assessment (Table 1).  Exhaust ventilation is necessary in restrooms to remove excess moisture and to prevent odors from penetrating into adjacent areas.

# Recommendations

The conditions related to indoor air quality problems at the JFKMS raise a number of issues.  The general building conditions, presence of asbestos-containing materials, maintenance, work hygiene practices and the condition of HVAC equipment, if considered individually, present conditions that could degrade indoor air quality.  When combined, these conditions can serve to further degrade indoor air quality.  Some of these conditions can be remedied by actions of building occupants.  Other remediation efforts will require alteration to the building structure and equipment.

For these reasons, a two-phase approach is required for remediation.  The first consists of short-term measures to improve air quality and the second consists of long-term measures that will require planning and resources to adequately address the overall indoor air quality concerns, a number of which will likely be addressed in the feasibility study.

The following short-term measures should be considered for implementation:

- Examine each univent and AHU for function.  Consider consulting an HVAC engineer concerning the calibration of fresh air control dampers throughout the school.

- Operate all ventilation systems throughout the building (e.g., gymnasium, locker rooms, cafeteria, classrooms) continuously during periods of school occupancy.  To increase airflow in classrooms, set univent controls to “high”.

- Set the thermostats for modular classrooms to the fan “on” position rather than “automatic” to operate the ventilation system continuously during the school day.

- Examine univent noise complaint in classroom 27-C, make repairs/adjustments as needed.

- Replace access panel or fabricate cover for univent in classroom 32 to prevent injury/access to steam pipes.

- Inspect exhaust motors and belts for proper function.  Repair and replace as necessary.

- Install passive vents in closet walls in classroom 13 and 37 to allow airflow to exhaust vents.

- Remove all blockages from univents and exhaust vents to ensure adequate airflow.

- Close classroom doors to maximize air exchange.

- Use openable windows in conjunction with classroom univents and exhaust vents to increase air exchange.  Care should be taken to ensure windows are properly closed at night and weekends to avoid the freezing of pipes and potential flooding.

- Consider adopting a balancing schedule of every 5 years for all mechanical ventilation systems, as recommended by ventilation industrial standards (SMACNA, 1994).

- For buildings in New England, periods of low relative humidity during the winter are often unavoidable.  Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low.  To control for dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended.  Avoid the use of feather dusters.  Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

- Consider applying solar (tinted) film to classroom windows as needed to reduce solar gain/excess heat (e.g., in classrooms 1 & 1-C).

- Ensure roof/plumbing leaks are repaired and remove/replace any remaining water-damaged non asbestos-containing ceiling tiles.

- Ensure compliance with the Asbestos Hazard Emergency Response Act (AHERA), which requires inspection of asbestos containing materials every three years as well as a semi-annual walkthrough to determine current conditions of asbestos-containing materials.

- Remediate damaged asbestos-containing materials (e.g., ceiling/floor tiles, window caulking) throughout the building in conformance with Massachusetts asbestos remediation and hazardous waste disposal laws (MDLI, 1993).

- Seal window panes and frames to prevent water penetration drafts and pest entry.  Address deteriorated window sealant in accordance with EPA regulations and MDPH guidance.

- Repair gutter and downspout system in order to direct rainwater as far as practicable from the base of the building.

- Repair cracked, broken masonry and missing/damaged mortar.

- Repair/replace exterior panels/siding on modular units.

- Remove moss growth from window sills/ledges, clean and disinfect.

- Make repairs to exterior doors or replace.

- Provide plants with drip pans and avoid over-watering.  Examine drip pans periodically for mold growth.  Disinfect with an appropriate antimicrobial where necessary.  Locate plants away from ventilation sources (e.g., univent air diffusers).

- Eliminate use of tennis balls on chair legs or replace with latex-free tennis balls or alternative glides.

- Routinely clean particulate residue from dry erase boards and trays.

- Remove grass and debris from univent fresh air intakes.  In the future, consider mowing grass in such a way as to avoid depositing grass clippings in the direction of air intakes.

- Relocate or consider reducing the amount of materials stored in classrooms to allow for more thorough cleaning of classrooms.  Clean items regularly with a wet cloth or sponge to prevent excessive dust build-up.

- Clean personal fans, univent air diffusers, return vents and exhaust vents periodically of accumulated dust.

- Clean floor cushions and pillows on a regular basis.  If not possible/practical, consider removing from classrooms.

- Refrain from using air fresheners and deodorizers to prevent exposure to VOCs.

- Ensure that restroom exhaust ventilation is operating and ducted to the outside of the building.

- Consider adopting the US EPA (2000) document, “Tools for Schools”, as an instrument for maintaining a good indoor air quality environment in the building.  This document is available at: http://www.epa.gov/iaq/schools/index.html.

- Refer to resource manual and other related indoor air quality documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings.  These documents are available at: http://mass.gov/dph/iaq.

At the time of the assessment, replacement of the JFKMS was being proposed by the town of Hudson.  In the event that these plans do not progress, the following long-term recommendations are made.

- Contact an HVAC engineering firm for an assessment of the ventilation system’s control system (e.g., controls, air intake louvers, thermostats).  Based on the age, physical deterioration and availability of parts for ventilation components, such an evaluation is necessary to determine the operability and feasibility of repairing/replacing the equipment.

- Consider replacing window systems to prevent air infiltration and water penetration.

- Consider plans for roof replacement including the removal of historical “patches” originally intended for temporary repair.  Until the roof can be replaced, continue to make roof repairs as needed to prevent water penetration.

- Consider having exterior walls re-pointed and waterproofed to prevent water intrusion.  This measure should include a full building envelope evaluation.

- Consider replacing univent fresh air intakes with an alternate design not prone to accumulating debris.

# References

ACGIH.  1989.  Guidelines for the Assessment of Bioaerosols in the Indoor Environment.  American Conference of Governmental Industrial Hygienists, Cincinnati, OH.

ASHRAE.  1989.  Ventilation for Acceptable Indoor Air Quality.  American Society of Heating, Refrigeration and Air Conditioning Engineers. ANSI/ASHRAE 62-1989

ASHRAE.  1991.  ASHRAE Applications Handbook, Chapter 33 “Owning and Operating Costs”.  American Society of Heating, Refrigeration and Air Conditioning Engineers, Atlanta, GA.

Berry, M.A.  1994.  Protecting the Built Environment: Cleaning for Health, Michael A. Berry, Chapel Hill, NC.

BOCA.  1993.  The BOCA National Mechanical Code/1993.  8th ed.  Building Officials and Code Administrators International, Inc., Country Club Hill, IL.

IICRC.  2000.  IICRC S001 Reference Guideline for Professional On-Location Cleaning of Textile Floor Covering Materials Institute of Inspection, Cleaning and Restoration Certification.  Institute of Inspection Cleaning and Restoration, Vancouver, WA.

Lstiburek, J. & Brennan, T.  2001.  Read This Before You Design, Build or Renovate.  Building Science Corporation, Westford, MA.  U.S. Department of Housing and Urban Development, Region I, Boston, MA.

MDLI.  1993.  Regulation of the Removal, Containment or Encapsulation of Asbestos, Appendix 2.  453 CMR 6,92(I)(i).

MDPH.  1997.  Requirements to Maintain Air Quality in Indoor Skating Rinks (State Sanitary Code, Chapter XI).  105 CMR 675.000.  Massachusetts Department of Public Health, Boston, MA.

NIOSH.  1997.  NIOSH Alert Preventing Allergic Reactions to Natural Rubber latex in the Workplace.  National Institute for Occupational Safety and Health, Atlanta, GA.

OSHA.  1997.  Limits for Air Contaminants.  Occupational Safety and Health Administration.  Code of Federal Regulations.  29 C.F.R 1910.1000 Table Z-1-A.

Sanford.  1999.  Material Safety Data Sheet (MSDS No: 198-17).  Expo Dry Erase Markers Bullet, Chisel, and Ultra Fine Tip.  Sanford Corporation.  Bellwood, IL.

SBAA.  2001.  Latex In the Home And Community Updated Spring 2001.  Spina Bifida Association of America, Washington, DC.

SBBRS.  1997.  Mechanical Ventilation.  State Board of Building Regulations and Standards.  Code of Massachusetts Regulations.  780 CMR 1209.0

SMACNA.  1994.  HVAC Systems Commissioning Manual.  1st ed.  Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

US EPA.  1986.  Asbestos Hazard Emergency Response Act of 1986 (AHERA) Public Law 99-519, Oct 22, 1986.  15 USC Section 2651.

US EPA.  1992.  Indoor Biological Pollutants.  US Environmental Protection Agency, Environmental Criteria and Assessment Office, Office of Health and Environmental Assessment, research Triangle Park, NC.  EPA 600/8-91/202 January 1992.

US EPA.  2000.  Tools for Schools.  Office of Air and Radiation, Office of Radiation and Indoor Air, Indoor Environments Division (6609J). EPA 402-K-95-001, Second Edition.  http://www.epa.gov/iaq/schools/tools4s2.html.

US EPA.  2001.  Mold Remediation in Schools and Commercial Buildings. US Environmental Protection Agency, Office of Air and Radiation, Indoor Environments Division, Washington, D.C.  EPA 402-K-01-001.  March 2001.

US EPA.  2006.  National Ambient Air Quality Standards (NAAQS).  US Environmental Protection Agency, Office of Air Quality Planning and Standards, Washington, DC.  http://www.epa.gov/air/criteria.html.

Picture 1

Univent Fresh Air Intake, Note Design Allowing Debris to Accumulate in Vent

Picture 2

Univent Return Vent (along bottom front) Obstructed by Classroom Items

Picture 3

Univent Airflow (top/front) Obstructed by Various Items

Picture 4

Univent Missing Access Panel Exposing Steam Pipes

Picture 5

Obstructed Wall-Mounted Exhaust Vent

Picture 6

Exhaust Vent in Closet Sealed off from Classroom 13

Picture 7

Wall/Closet Sealing in Classroom Exhaust Vent in Preceding Picture

Picture 8

Water-Damaged Ceiling Tiles in School Psychologist’s Office

Reportedly Containing Asbestos

Picture 9

Missing/Damaged Window Caulking

Picture 10

Missing/Damaged Window Caulking

Picture 11

Missing/Damaged Window Caulking

Picture 12

Missing/Damaged Window Caulking

Picture 13

Missing/Damaged Window Caulking

Picture 14

Missing/Damaged Sealant in Expansion Joint

Picture 15

Damaged/Delaminating Exterior Wooden Door

Picture 16

Damaged/Delaminating Exterior Wooden Door

Picture 17

Damaged/Crumbling Masonry

Picture 18

Damaged/Crumbling Masonry, Note Plant Growing in Space between

Concrete and Window Frame

Picture 19

Moss Growth on Exterior Ledge Indicating Chronic Moisture Exposure

Picture 20

Damaged Downspout, Note Close Proximity to Base of Building

Picture 21

Missing/Damaged Panels on Exterior of Modular Classroom Building

| Location/ Room | Occupants in Room | Temp (°F) | Relative Humidity (%) | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | PM2.5 (µg/m3) | Windows Openable | Ventilation |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| background |  | 29 | 39 | 307 | ND | 4 |  |  |  | Cloudy, cold, winds NNE 9-18 mph, gusts up to 25 mph |
| 1 | 19 | 78 | 20 | 950 | ND | 9 | Y | Y | Y | Exhaust blocked, heat issues (thermostat) |
| 1-C | 8 | 75 | 23 | 990 | ND | 9 | Y | N | N | Solar heat issues |
| 2 | 18 | 74 | 17 | 632 | ND | 8 | Y | Y | Y |  |
| 3 | 5 | 73 | 16 | 541 | ND | 7 | Y | Y | Y | Exhaust blocked by cardboard, occupants at lunch, missing/damaged window caulking (interior/exterior) |
| 4 | 21 | 73 | 27 | 1094 | ND | 18 | Y | Y | Y | UV off, DO, items on/front of UV, missing/damaged window caulking (interior/exterior) |
| 5 | 18 | 73 | 25 | 1206 | ND | 9 | Y | Y | Y | UV off, PF-dusty, missing/damaged window caulking (interior/exterior) |
| 6 | 0 | 74 | 21 | 766 | ND | 9 | Y | Y | Y | UV off |
| 12 | 18 | 72 | 30 | 1826 | ND | 10 | Y | Y | Y | UV and exhaust off, ceiling UV |
| 13 | 19 | 76 | 22 | 1094 | ND | 10 | Y | Y | Y | Ceiling UV, new carpet odor, former locker room, exhaust vent sealed off in closet, recommend passive vent in wood |
| 15-B | 20 | 71 | 17 | 712 | ND | 9 | Y | Y | Y | Window open, UV off, missing/damaged window caulking (interior) |
| 15-C | 19 | 74 | 21 | 892 | ND | 9 | Y | Y | Y | Window open, UV off |
| 20 | 22 | 74 | 17 | 875 | ND | 10 | Y | Y | Y | DO, , TB, PF-dusty, missing/damaged (loose) window caulking (interior/exterior) |
| 21 | 18 | 69 | 17 | 613 | ND | 8 | Y | Y | Y | Window open, UV off, DO, pillows/cushions, missing/damaged window |
| 22 | 16 | 74 | 24 | 940 | ND | 9 | Y | Y | Y | UV off, exhaust blocked, missing/damaged window caulking |
| 23 | 19 | 74 | 27 | 1272 | ND | 10 | Y | Y | Y | UV off, missing/damaged caulking around UV |
| 24 | 19 | 73 | 17 | 737 | ND | 8 | Y | Y | Y | Window open, items on/front of UV, missing/damaged window caulking (interior/exterior) |
| 25-C | 14 | 72 | 24 | 835 | ND | 8 | Y | Y | Y | Exhaust blocked by furniture, plants, missing/damaged window caulking (interior/exterior) |
| 25-S | 21 | 73 | 23 | 1036 | ND | 9 | Y | Y | Y | Window open, UV-off, exhaust-no draw, missing/damaged window caulking (interior/exterior) |
| 26 | 19 | 74 | 30 | 1102 | ND | 13 | Y | Y | Y | UV off/blocked, exhaust blocked, missing/damaged window caulking (interior) |
| 27 | 19 | 73 | 31 | 958 | ND | 8 | Y | Y | Y | UV off, plants near UV, DO, AD |
| 27-C | 6 | 73 | 25 | 876 | ND | 7 | Y | Y | Y | UV off-noise, missing/damaged window caulking (interior/exterior) |
| 28 | 4 | 72 | 22 | 616 | ND | 6 | Y | Y | Y | Pillows/cushions on floor, TB, missing/damaged interior caulking |
| 30 | 19 | 74 | 31 | 1558 | ND | 10 | Y | Y | Y | UV off, WD-wall/historic leaks |
| 31 | 16 | 74 | 26 | 1202 | ND | 7 | Y | Y | Y | UV-off, plants, missing/damaged window caulking (interior/exterior) |
| 32 | 11 | 75 | 25 | 1140 | ND | 5 | Y | Y | Y | UV off, TB, missing/damaged window caulking (interior/exterior), missing UV panel-exposing hot pipes |
| 33 | 13 | 74 | 15 | 594 | ND | 7 | Y | Y | Y | Window open, UV off, exhaust blocked by furniture |
| 34 | 18 | 74 | 22 | 774 | ND | 9 | Y | Y | Y | Window open, plants, unit exhaust vent, missing/damaged window caulking |
| 35-C | 3 | 74 | 26 | 710 | ND | 8 | Y | Y | Y | MT, 6 WD CT, historic leaks |
| 37 | 12 | 73 | 16 | 674 | ND | 7 | Y | Y | Y | Exhaust off, former locker room exhaust in closet |
| Art | 0 | 70 | 24 | 576 | ND | 6 | Y | Y | Y | Caulking replaced in some areas others is missing/damaged |
| Auditorium | 20 | 72 | 25 | 781 | ND | 10 | N | Y | Y |  |
| Cafeteria | ~100 | 74 | 27 | 1037 | ND | 11 | Y | Y | Y | missing/damaged window caulking (interior/exterior), WD CT along exterior door exit |
| Gym | 20 | 71 | 27 | 650 | ND | 14 | Y | Y | Y | Musty odors |
| Hallway 2nd Floor |  |  |  |  |  |  |  |  |  | Numerous WD CTs |
| Library | 1 | 72 | 24 | 599 | ND | 8 | Y | Y | Y | Drafty windows, passive vents for interior rooms |
| Main Office | 4 | 70 | 31 | 679 | ND | 9 | Y | N | N | Plants, AC |
| Modular Classroom | 10 | 70 | 35 | 1174 | ND | 7 | Y | Y | Y | Thermostat “Auto” |
| Nurse’s Office | 1 | 75 | 22 | 723 | ND | 9 | Y | N | Y | 5 WD CTs, missing/damaged window caulking (interior/exterior), restroom exhaust no draw |
| Principal’s Office | 5 | 66 | 37 | 855 | ND | 8 | Y | N | N | Plants, AC |
| S-5 Band Room | 1 | 74 | 22 | 823 | ND | 10 | N | N | N | Spaces under door |
| School Psychologist | 0 | 74 | 26 | 998 | ND | 13 | N | N | Y | 10 WD CTs, bulging CT |
| Teachers Room | 0 | 73 | 21 | 718 | ND | 8 | N | N | N |  |
| Technology | 19 | 73 | 18 | 635 | ND | 12 | Y | Y | Y | 6 WD CTs, thermostat fan “Auto” |

An Information Booklet Addressing PCB-Containing Materials in the Indoor Environment of Schools

and Other Public Buildings

Prepared by

Bureau of Environmental Health

Massachusetts Department of Public Health

December 2009

INTRODUCTION

The purpose of this information booklet is to provide assistance to school and public building officials and the general public in assessing potential health concerns associated with polychlorinated biphenyl (PCB) compounds in building materials used in Massachusetts and elsewhere.  Recently, the U.S. Environmental Protection Agency (EPA) provided broad guidance relative to the presence of PCBs in building materials, notably PCBs in caulking materials.  The most common building materials that may contain PCBs in facilities constructed or significantly renovated during the 1950s through the 1970s are fluorescent light ballasts, caulking, and mastic used in tile/carpet as well as other adhesives and paints.

This information booklet, developed by the Massachusetts Department of Public Health’s Bureau of Environmental Health (MDPH/BEH), is designed to supplement guidance offered by EPA relative to potential health impacts and environmental testing.  It also addresses managing building materials, such as light ballasts and caulking, containing PCBs that are likely to be present in many schools and public buildings across the Commonwealth.  This is because the Northeastern part of the country, and notably Massachusetts, has a higher proportion of schools and public buildings built during the 1950s through 1970s than many other parts of the U.S. according to a 2002 U.S. General Accounting Office report.  The Massachusetts School Building Authority noted in a 2006 report that 53 percent of over 1,800 Massachusetts school buildings surveyed were built during the 1950s through 1970s.  This information booklet contains important questions and answers relative to PCBs in the indoor environment and is based on the available scientific literature and MDPH/BEH’s experience evaluating the indoor environment of schools and public buildings for a range of variables, including for PCBs as well as environmental data reviewed from a variety of sources.

1. What are PCBs?

Polychlorinated biphenyl (PCB) compounds are stable organic chemicals used in products from the 1930s through the late 1970s.  Their popularity and wide-spread use were related to several factors, including desirable features such as non-flammability and electrical insulating properties.  Although the original use of PCBs was exclusive to closed system electrical applications for transformers and capacitors (e.g., fluorescent light ballasts), their use in other applications, such as using PCB oils to control road dust or caulking in buildings, began in the 1950s.

2. When were PCBs banned from production?

Pursuant to the Toxic Substance Control Act (TSCA) of 1976 (effective in 1979), manufacturing, processing, and distribution of PCBs was banned.  While the ban prevented production of PCB-containing products, it did not prohibit the use of products already manufactured that contained PCBs, such as building materials or electrical transformers.

3. Are PCBs still found in building materials today?

Yes.  Products made with PCBs prior to the ban may still be present today in older buildings.  In buildings constructed during the 1950s through 1970s, PCBs may be present in caulking, floor mastic, and in fluorescent light ballasts.  Available data reviewed by MDPH suggests that caulking manufactured in the 1950s through 1970s will likely contain some levels of PCBs.  Without testing it is unclear whether caulking in a given building may exceed EPA’s definition of PCB bulk product waste of 50 parts per million (ppm) or greater.  If it does, removal and disposal of the caulk is required in accordance with EPA’s TSCA regulations (40 CFR § 761).

4. Are health concerns associated with PCB exposure opportunities?

Although the epidemiological evidence is sometimes conflicting, most health agencies have concluded that PCBs may reasonably be anticipated to be a carcinogen, i.e., to cause cancer.

PCBs can have a number of non-cancer effects, including those on the immune, reproductive, neurological and endocrine systems.  Exposure to high levels of PCB can have effects on the liver, which may result in damage to the liver.  Acne and rashes are symptoms typical in those that are exposed to high PCB levels for a short period of time (e.g., in industry / occupational settings).

5. If PCBs are present in caulking material, does that mean exposure and health impacts are likely?

No.  MDPH/BEH’s review of available data suggests that if caulking is intact, no appreciable exposures to PCBs are likely and hence health effects would not be expected.  MDPH has conducted indoor tests and reviewed available data generated through the efforts of many others in forming this opinion.

6. How can I tell if caulking or light ballasts in my building may contain PCBs?

If the building was built sometime during the 1950s through 1970s, then it is likely that the caulking in the building and/or light ballasts may contain some level of PCBs.  Light ballasts manufactured after 1980 have the words “No PCBs” printed on them.  If the light ballast does not have this wording or was manufactured before 1980, it should be assumed that it contains PCBs.

7. What are light ballasts?

A light ballast is a piece of equipment that controls the starting and operating voltages of fluorescent lights.  A small capacitor within older ballasts contains about one ounce of PCB oil.  If light bulbs are not changed soon after they go out, the ballast will continue to heat up and eventually result in the release of low levels of PCBs into the indoor air.

8. Does the presence of properly functioning fluorescent light ballasts in a building present an environmental exposure concern?

No appreciable exposure to PCBs is expected if fluorescent light ballasts that contain PCBs are intact and not leaking or damaged (i.e., no visible staining of the light lenses), and do not have burned-out bulbs in them.

9.  Should I be concerned about health effects associated with exposure to PCBs as a result of PCB-containing light ballasts?

While MDPH has found higher PCB levels in indoor air where light bulbs have burned-out, the levels are still relatively low and don’t present imminent health threats.  A risk assessment conducted recently at one school did not suggest unusual cancer risks when considering a worst case exposure period of 35 years for teachers in that school.  Having said this, MDPH believes that facility operators and building occupants should take prompt action to replace bulbs and/or ballasts as indicated to reduce/eliminate any opportunities for exposure to PCBs associated with PCB-containing light ballasts.

10. When should PCB-containing light ballasts be replaced?

If ballasts appear to be in disrepair, they should be replaced immediately and disposed of in accordance with environmental regulatory guidelines and requirements.  However, if light bulbs burn out, the best remedy is to change them as soon as possible.  If light bulbs are not changed soon after they go out, the ballast will continue to heat up and eventually result in the release of low levels of PCBs into the indoor air.  Thus, burned-out bulbs should be replaced promptly to reduce overheating and stress on the ballast.  As mentioned, ballasts that are leaking or in any state of disrepair should be replaced as soon as possible.

It should be noted that although older light ballasts may still be in use today, the manufacturers’ intended lifespan of these ballasts was 12 years.  Thus, to the extent feasible or in connection with repair/renovation projects, the older light ballasts should be replaced consistent with the intended lifespan specified by the manufacturers.

11. Does MDPH recommend testing of caulking in buildings built during the 1950s -1980?

Caulking that is intact should not be disturbed.  If caulking is deteriorating or damaged, conducting air and surface wipe testing in close proximity to the deteriorating caulking will help to determine if indoor air levels of PCBs are a concern as well as determining the need for more aggressive cleaning.  Results should be compared with similar testing done in an area without deteriorating caulking.  In this way, a determination can be made regarding the relative contribution of caulking materials to PCBs in the general indoor environment.

12. What if we determine that caulking in our building is intact and not deteriorating?

Based on a review of available data collected by MDPH and others, the MDPH does not believe that intact caulking presents appreciable exposure opportunities and hence should not be disturbed for testing.  As with any building, regular operations and maintenance should include a routine evaluation of the integrity of caulking material.  If its condition deteriorates then the steps noted above should be followed.  Consistent with EPA advice, if buildings may have materials that contain PCBs, facility operators should ensure thorough cleaning is routinely conducted.

13. Should building facilities managers include information about PCB-containing building materials in their Operations and Maintenance (O&M) plans?

Yes.  All buildings should have an O&M plan that includes regular inspection and maintenance of PCB building materials, as well as thorough cleaning of surfaces not routinely used.  Other measures to prevent potential exposure to PCBs include increasing ventilation, use of HEPA filter vacuums, and wet wiping.  These O&M plans should be available to interested parties.

14. Are there other sources of PCBs in the environment?

Yes.  The most common exposure source of PCBs is through consumption of foods, particularly contaminated fish.  Because PCBs are persistent in the environment, most residents of the U.S. have some level of PCBs in their bodies.

15.  Where can I obtain more information?

For guidance on replacing and disposing of PCB building materials, visit the US EPA website: http://www.epa.gov/pcbsincaulk/.  For information on health concerns related to PCBs in building materials, please contact MDPH/BEH at 617-624-5757.

The service life is the median time during which a particular system or component of …[an HVAC]… system remains in its original service application and then is replaced.  Replacement may occur for any reason, including, but not limited to, failure, general obsolescence, reduced reliability, excessive maintenance cost, and changed system requirements due to such influences as building characteristics or energy prices (ASHRAE, 1991).