INDOOR AIR QUALITY ASSESSMENT

Lowell High School

1922 Building

14 French Street

Lowell, MA

Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health

Indoor Air Quality Program

December 2017

# Background

| Building: | Lowell High School |
| --- | --- |
| Address: | 14 French Street, Lowell, MA |
| Assessment Coordinated Through: | Lowell Public Schools |
| Reason for Request: | General Indoor Air Quality (IAQ) concerns. Note that a preliminary walkthrough of the building was conducted over the summer while this visit was conducted during the school year while the building was under normal occupancy. |
| Date of Assessment: | December 12, 2017 |
| Massachusetts Department of Public Health/Bureau of Environmental Health (MDPH/BEH) Staff Conducting Assessment: | Cory Holmes, Environmental Analyst, Jason Dustin, Environmental Analyst, Sharon Lee, Environmental Analyst Ruth Alfasso, Environmental Engineer, and Mike Feeney Director, IAQ |
| Building Description: | The Building at 14 French Street was built in 1922 with brick and concrete construction and a complex shape. This building is connected to the building at 50 Father Morissette Boulevard by several enclosed walkways. |
| Windows: | Openable |

# Methods

Please refer to the IAQ Manual for methods, sampling procedures, and interpretation of results (MDPH, 2015).

# IAQ Testing Results

Table 1 shows the information collected during the preliminary walkthrough in July of 2017. Table 2 includes indoor air testing results, which are summarized below.

- Carbon dioxide levels were above 800 parts per million (ppm) in more than two-thirds of all areas assessed including all occupied classrooms, indicating a lack of adequate air exchange in those areas of the building.

- Temperature was within or close to the lower end of the recommended range of 70°F to 78°F in all areas on the day of assessment.

- Relative humidity was below the recommended range of 40 to 60% in the areas tested which is typical during the heating season.

- Carbon monoxide levels were non-detectable in most areas tested. Low levels of carbon monoxide were detected in a few rooms on the first floor.

- Fine particulate matter (PM2.5) concentrations measured were below the National Ambient Air Quality (NAAQS) limit of 35 μg/m3 in the majority of areas tested.

## Ventilation

A heating, ventilating, and air conditioning (HVAC) system has several functions. First it provides heating and, if equipped, cooling. Second, it is a source of fresh air. Finally, an HVAC system will dilute and remove normally occurring indoor environmental pollutants by not only introducing fresh air, but by filtering the airstream and ejecting stale air to the outdoors via exhaust ventilation. Even if an HVAC system is operating as designed, point sources of respiratory irritation may exist and cause symptoms in sensitive individuals. (For a description of the HVAC system, please refer to the August 2017 IAQ assessment).

Based on air sampling, it appears that most classrooms with normal occupancy appeared to have a lack of air exchange provided by the HVAC system in its current operating mode as demonstrated by carbon dioxide levels above 800 ppm. Given the age and operation of the existing HVAC system, it may be necessary to use opening windows to supplement fresh air supply for classrooms.

The HVAC systems should be regularly maintained and operate continuously during occupied hours. It may be possible to adjust AHUs to allow more fresh air into the system, e.g. by opening supply louvers or adjusting the proportion of air exhausted rather than recirculated. Exhaust ventilation should also be checked periodically to ensure a draw of air from classrooms. It was noted that the cooking area (Room 17) lacked exhaust ventilation, which is particularly important in areas where pollutants would be generated. In some other classroom, exhaust ventilation is only activated on a switch, which should be turned on whenever the classroom is occupied (Table 2).

In order to have proper ventilation with a mechanical supply and exhaust system, these systems must be balanced to provide an adequate amount of fresh air while removing stale air from a room. It is recommended that existing ventilation systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994). It is unknown the last time these systems were balanced.

## Microbial/Moisture Concerns

The 1800’s and 1920’s building sections were constructed with materials that, for the most part, are not susceptible to mold growth. The majority of these building sections consist of brick, concrete, tile, plaster, and glass; none of which contain carbon and are resistant to mold growth even with chronic moistening. Hardwood is also highly resistant to microbial growth. Hardwood was observed throughout these sections in flooring, support beams, and trim.

Building renovations that occurred in later years added “porous” building materials such as carpeting, ceiling tiles, and gypsum wallboard. All of these materials contain carbon, which can support mold/microbial growth.

As reported by City of Lowell officials, original floors that were water-damaged were replaced with plywood and carpeted. An interior hallway adjacent to Room 105A has a water-damaged original floor that is likely the condition that required replacement with plywood (Picture 1). Room 105A has water-damaged wall plaster located behind a free-standing shelf (Picture 2), which may be the source of water that would be wetting the floor during/after wet weather.

Musty/stale odors were noted in a number of classrooms with wall-to-wall carpeting. Classrooms with either wood or tiled floors did not have the stale, musty odor. Wall-to-wall carpeting was also noted in offices as well as below grade spaces. Wall-to-wall carpeting is not recommended in school classrooms in general, due to the difficulty in maintaining in good condition, including wear, dirt and spills. Carpeting is also not recommended in below-grade areas due to the likelihood of moisture exposure from condensation forming on floors in contact with the ground during humid weather and/or ground or storm water infiltration. Roof leaks leading to stained ceiling tiles and water-damaged plaster can also be a source of water to moisten carpeting. Carpeting moistened periodically will be subject to microbial growth. The odors detected in these carpeted areas are likely from water damage that subsequently led to microbial colonization of carpeting, as well as a buildup of dirt and debris in older carpeting that could no longer be adequately cleaned. Some carpeting was visibly stained, wrinkled, or threadbare (Tables 1 and 2; Picture 3), indicating it was past its service life. The service life of carpeting in schools is approximately 10-11 years (IICRC, 2002). Aging carpet can produce fibers that can be irritating to the respiratory system. In addition, tears or lifting carpet can create tripping hazards. Carpeting should be cleaned annually or semi-annually in soiled high traffic areas as per the recommendations of the Institute of Inspection, Cleaning, and Restoration Certification (IICRC, 2012).

Water-damaged ceiling tiles and gypsum wallboard were observed in classrooms, offices, and hallways (Table 2). Damage to these materials indicates leaks from the building envelope or plumbing system. Ceiling tiles and gypsum wallboard should be replaced after the leak is found and repaired. In general, ceiling tiles have an open space above them (the ceiling plenum) and tend to dry out quickly, reducing the chance that they will be colonized with mold.

Measures should be taken to ensure water-damaged materials are cleaned, replaced, and/or repaired in a manner consistent with the U.S. Environmental Protection Agency’s guidelines (US EPA, 2008). The US EPA and the American Conference of Governmental Industrial Hygienists (ACGIH) recommend that porous materials (e.g., ceiling tiles, gypsum wallboard) be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2008; ACGIH, 1989). If not dried within this time frame they should be removed/discarded.

Water-damaged ceiling tiles need to be removed and replaced. In many areas, some ceiling tiles were also missing (Table 2). These need to be replaced to maintain a continuous ceiling plenum and prevent dust and debris from above the ceiling tiles entering occupied areas.

Water was observed leaking from a radiator into a bucket in Room 113; it was reported to be on a repair list. Until the piping can be repaired, this bucket, and any other water catch receptacle used in the building, needs to be emptied regularly and kept clean to prevent odors.

Windows open in most exterior classrooms. Open windows can be an additional source of fresh air. However, windows need to be tightly closed at the end of each day to prevent water infiltration and pest intrusion. Note that a few windows were found to be misaligned so that they would be difficult to close completely (Tables 1 and 2); these should be repaired/replaced.

Some areas in the buildings are equipped with air conditioning from the AHUs. Doors between these areas and non-air-conditioned areas should be kept closed to prevent condensation of humid air on chilled surfaces. A few other areas were equipped with portable or window air conditioners. It is important that these units have the ability to properly drain any condensation they generate so that it does not leak and moisten building materials.

## Other Conditions

Exposure to low levels of volatile organic compounds (VOCs) may produce eye, nose, throat, and/or respiratory irritation in some sensitive individuals. BEH/IAQ staff examined spaces for products containing VOCs, noting cleaning products, air fresheners, hand sanitizers and dry erase materials in a number of areas throughout the office space (Table 2). All of these products have the potential to be irritants to the eyes, nose, throat, and respiratory system of sensitive individuals. Other sources of total volatile organic compounds (TVOCs) include copy machines and laminators (Table 2). Excess heat, odors, VOCs and ozone can be produced by photocopiers, particularly if the equipment is older and in frequent use. Ozone is a respiratory irritant (Schmidt Etkin, 1992). Laminators produce TVOCs and plastic odors. This equipment should be used in well-ventilated areas away from occupants.

In many areas, items, including books, papers, and decorative items were observed on floors, windowsills, tabletops, counters, bookcases, and desks, which can make it more difficult for custodial staff to clean (Table 2). Many classrooms had personal fans and some of these had dusty blades. Many supply and exhaust vents were also observed to be dusty (Table 2). Dust on ventilation and fan equipment can be aerosolized when the units are activated.

# Conclusions/Recommendations

The following recommendations are made to assist in improving IAQ:

- For information regarding the roof and recommendations, please refer to the August 2017 IAQ assessment.

- Remove any water-damaged, musty, or worn carpeting and replace with non-porous flooring in classrooms and below-grade areas.

- Use openable windows to supplement fresh air during temperate weather. Ensure all windows are tightly closed at the end of the day. Inform occupants that windows should not be opened while the HVAC system is in cooling mode to avoid condensation.

- Consult with an HVAC contractor to thoroughly examine all HVAC system components to ensure proper function. Make any necessary repairs to ensure the system is working as designed. Assess whether adjustments can be made to allow more fresh air into the system.

- Operate all supply and exhaust ventilation equipment continuously during occupied periods. Do not block supply or exhaust vents with furniture or items. Check exhaust/return vents periodically for proper function. Where exhaust vents are switch-operated, ensure they are turned on when the room is occupied.

- Ensure areas which generate pollutants, such as cooking class areas, have operable exhaust functioning.

- Ensure that a system of regular “Operations and Maintenance” remains in place to keep HVAC systems in proper working order.

- Consider adopting a balancing schedule of every 5 years for all mechanical ventilation systems, as recommended by ventilation industrial standards (SMACNA, 1994).

- Repair water leaks in Room 105A. Repair plaster once water leak once repaired.

- Replace any water-damaged/mold-colonized porous building materials (e.g., ceiling tiles, gypsum wallboard) in classrooms, hallways and stairwell areas. Ensure water-damaged materials are cleaned, replaced, and/or repaired in a manner consistent with the U.S. Environmental Protection Agency’s guidelines (US EPA, 2008).

- Replace any missing or ajar ceiling tiles to avoid pathways to unconditioned areas.

- Ensure that a system of regular “Operations and Maintenance” remains in place to keep HVAC systems in proper working order.

- Ensure pipe leak in room 113 is repaired.

- Regularly inspect window and portable air conditioning units to ensure proper drainage of condensate and regular cleaning of filters.

- Ensure that doors are closed between areas with air conditioning and areas without air conditioning, to avoid condensation of humid air on chilled surfaces.

- Refrain from storing porous items (e.g., boxes, books, paper, clothing) directly on flooring, in below grade spaces, or under sink cabinets to avoid microbial colonization.

- Trim back trees/vegetation within 5′ of the building. Remove any vegetation (e.g., ivy) that is growing on the building to avoid damage to exterior from associated moisture.

- Reduce the use of products containing VOCs.

- Locate photocopiers and laminators in well ventilated areas away from occupants.

- Ensure Material Safety Sheets are available for all laboratory, maintenance and janitorial chemicals used in the building.

- Regularly clean supply/return vents and fans to avoid aerosolizing accumulated particulate matter.

- Consider reducing the amount of items stored in classrooms to make cleaning easier. Periodically move items to clean flat surfaces.

- Clean any remaining carpeting and area rugs annually or more often in high-traffic locations in accordance with IICRC recommendations (IICRC, 2012) and discard those that are worn out or too soiled to be cleaned.

- Encourage faculty to report classroom/building related issues via a tracking program.

- Continue to adopt the US EPA (2000) document, “Tools for Schools”, as an instrument for maintaining a good IAQ environment in the building available at: http://www.epa.gov/iaq/schools/index.html.

- Refer to resource manual and other related IAQ documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings. These documents are available at: http://mass.gov/dph/iaq.

# References

ACGIH. 1989. Guidelines for the Assessment of Bioaerosols in the Indoor Environment. American Conference of Governmental Industrial Hygienists, Cincinnati, OH.

ASHRAE. 2012. American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) Standard 52.2-2012 -- Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size (ANSI Approved). 2012.

IICRC. 2002. Institute of Inspection, Cleaning and Restoration Certification. A Life-Cycle Cost Analysis for Floor Coverings in School Facilities.

IICRC. 2012. Institute of Inspection, Cleaning and Restoration Certification. Carpet Cleaning: FAQ. Retrieved from http://www.iicrc.org/consumers/care/carpet-cleaning.

MDPH. 2015. Massachusetts Department of Public Health. “Indoor Air Quality Manual: Chapters I-III”. Available at: http://www.mass.gov/eohhs/gov/departments/dph/programs/environmental-health/exposure-topics/iaq/iaq-manual/.

Schmidt Etkin, D. 1992. Office Furnishings/Equipment & IAQ Health Impacts, Prevention & Mitigation. Cutter Information Corporation, Indoor Air Quality Update, Arlington, MA.

SMACNA. 1994. HVAC Systems Commissioning Manual. 1st ed. Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

US EPA. 1993. Radon Measurement in Schools, Revised Edition. Office of Air and Radiation, Office of Radiation and Indoor Air, Indoor Environments Division (6609J). EPA 402-R-92-014. https://www.epa.gov/sites/production/files/2014-08/documents/radon_measurement_in_schools.pdf

US EPA. 2000. Tools for Schools. Office of Air and Radiation, Office of Radiation and Indoor Air, Indoor Environments Division (6609J). EPA 402-K-95-001, Second Edition. http://www.epa.gov/iaq/schools/index.html.

US EPA. 2008. “Mold Remediation in Schools and Commercial Buildings”. Office of Air and Radiation, Indoor Environments Division, Washington, DC. EPA 402-K-01-001. September 2008. Available at: http://www.epa.gov/mold/mold-remediation-schools-and-commercial-buildings-guide.

Picture 1

Water-damaged floor of hall adjacent to room 105A

Picture 2

Water-damaged plaster in room 105A behind freestanding shelf

Picture 3

Worn, stained carpeting

| - Location | Windows Openable | Ventilation |  | Remarks |
| --- | --- | --- | --- | --- |
|  |  | Intake | Exhaust |  |
| 301 A (Main Area) |  |  |  | 6 WD CT |
| 301 A (Slattery Office) |  |  |  | Hole in wall-exposed fiberglass insulation |
| 304 |  | Y | Y | 12+ WD CT, tile floor, dry drain, PC |
| 305 A |  | Y | Y | Carpeted, dust/debris on vents, WD CP along windows/corner |
| 305 B |  | Y | Y | Carpeted, dust/debris on vents |
| 306 | Y | Y | Y | Musty carpet odor |
| 308 |  | Y | Y | 5 WD CT, carpeted, WD plaster |
| 310 | Y | Y | Y |  |
| 311 |  |  |  | WD CP, peeling paint, open pipe ceiling |
| 312 | Y | Y | Y | Storage/desk, 1 WD CT, carpeted, WD plaster |
| 313 | Y | Y | Y | Wood floor, dirty lights |
| 314 Chemistry | Y | Y | Y | Stored chemicals, chemical odors, HS, sinks, floor tiles damaged, WD ceiling |
| 314 Storage |  | N | N | 9 WD CT, tile floor |
| 315 |  |  |  | WD CP, peeling paint, PF |
| 318 |  | Y | Y | 2 WD CT and plaster, carpeted |
| 319 |  |  |  | PF |
| 320 |  | Y | N | Carpeted |
| 321 | Y | Y | Y | Tile floor, damaged, PF, DEM, science sinks and eyewash |
| 323 R |  |  |  | Carpeted, WAC |
| 324 Physics | Y | Y | Y | Carpeted, DEM |
| 325 |  | Y | Y | Exhaust vent obstructed w/file cabinet, WD CP and peeling paint |
| 326 |  | Y | Y | WD plaster, carpeted |
| 329 |  |  |  | WD CP and peeling paint, PF, ajar CT-wiring |
| 330 |  | Y | Y | 10+ WD CT, carpeted |
| 331 |  |  |  | WD CP and peeling paint, WD CT |
| 332 |  | Y | Y | 4 WD CT, carpeted |
| 333 | Y | Y | Y | Wood floor, PF |
| 334 |  | Y | Y | 4 WD CT, carpeted |
| 338 |  | Y | Y | wood floor |
| 346 | Y open | Y | Y | Carpet |
| 349 Computer Lab | Y open | Y | Y | Worn carpeting, numerous computers |
| 351 |  |  |  | Carpeted, WD CP and peeling paint, stained CP, 3 WD CTs |
| 389 | Y | Y | Y | WD CT, PC, worn carpeting |
| Boys Restroom | N | N | Y | WD plaster, broken urinal |
| Crowell Office |  |  |  | 3 WD CTs, WD CP along windows |
| Custodial Closet | N | N | Y | Slop sink, WD CP, open pipe, odors |
| Faculty Men’s Restroom | N | N | Y | WD ceiling plaster |
| Girls Restroom | N | N | Y | WD CP |
| Hallway (323) |  |  |  | Abandoned water fountain-covered w/trash bag |
| Stairwell B | N | N | N | WD CT, MT, dirty lights, |
| Teacher’s Center -Upstairs | N | Y | Y | Carpet, PC, plants, AI, DEM, mechanical room access |
| Teacher’s Center -Tile Side | N | Y | Y | NC, PF, CPs, WD CTs x 10, dusty vents, boxes stored on floor |
| Teachers Center Conference Area | Y | Y | Y | PC, carpeted |
| Teachers Center Food Area | Y | Y | Y | NC, 2 fridges, microwave |
| 201 B |  |  |  | Carpeted |
| 203 |  |  |  | Carpeted |
| 206 B | Y | Y | Y | Carpet, PF |
| 206 D |  | Y | Y | Carpet, PF, HS, AF |
| 207 A |  | Y | Y | Dust/debris on vents, portable AC unit |
| 207 B |  | Y | Y | Carpeted, window in disrepair-sign “do not touch window”, dust/debris on vents |
| 208 B | N | Y | Y | Carpet |
| 209 R | N | Y | Y | WD and MT, carpeted, DEM |
| 209 A | N | Y | Y | Carpet in waiting room area |
| 209 B | Y open | Y | Y | Hallways in this area are new Pergo flooring, this office is carpeted (new), window poorly sealed/off track |
| 209 E | N | Y | Y | New carpet |
| 210 | Y open | Y | Y | Carpet, DEM |
| 212 A |  | Y | Y | Carpeted |
| 213 |  |  |  | Carpeted, PF, WD CP and peeling paint/corner |
| 214 A | Y | Y | Y | Wood floor, WD CT |
| 214 B | Y open | Y | Y | Asphalt odor detected (roof below?), WD plaster ceiling |
| 215 | Y open | Y | Y | Wood floor |
| 216 |  | Y | Y | Wood floor |
| 217 |  |  |  | Carpeted, PF |
| 218 |  | Y | Y | Wood floor |
| 219 | Y open | Y | Y | WD CT, wood floor, PF |
| 220 |  | Y | Y | Carpeted |
| 223 | Y open | Y | Y | Wood floor |
| 226 |  | Y | Y | Wood floor |
| 227 |  |  |  | PF |
| 229 |  | Y | Y | Carpeted, PF, ajar CT, dust/debris on vents, WD CP and peeling paint |
| 230 |  | Y | Y | Wood floor |
| 231 |  |  |  |  |
| 232 |  | Y | Y | Carpeted |
| 235 |  |  |  | PFs |
| 236 |  |  |  | Custodial closet, odor of cleaners/mop |
| 237 Computer Lab |  | Y | Y | Dust/debris on vents |
| 239 |  |  |  | Peeling paint |
| 240 |  | y | y | carpeted no odor, 1 WD CT |
| 249 | Y open | Y | Y | 1 WD CT, carpet |
| 254 |  | Y | Y | 1 WD CT, carpeted floor |
| 255 |  | Y | Y | 1 WD CT, carpeted |
| 259 Hall |  | Y | Y | WD CT |
| Auditorium Upper Level | N | Y | Y | AC, carpet, upholstered chairs |
| Boys Restroom | N | N | Y | Many WD CT, CP, wall tiles |
| Español | Y open | Y | Y | Carpeted, DEM, cleaning products |
| Girls Restroom | N | N | Y | A few WD CT, CP |
| Girls Restroom |  | Y | Y | 5 WD CT, carpeted floor, WD GW ceiling |
| Men’s Faculty Restroom | N | N | Y | WD plaster |
| Mural room | N | N | N | Missing light cover |
| Second Floor Stairwell B | Y open | N | N |  |
| Womens restroom | Y open | Y | Y | Dusty vents |
| 101 |  | Y | Y | Carpeted |
| 101 Storage |  | Y | Y | 2 WD CT, WD GW, mold |
| 102 | Y | Y | Y | DEM, carpet |
| 105 |  |  |  | Carpeted, PF, severely damaged wall and ceiling plaster/corner |
| 106 | Y | Y | Y | DEM, newer carpet, , WAC, microwave/fridge, PC, reports of previous flood from 3rd floor, slight foul odor |
| 106 A | N | Y | Y | Carpet |
| 107 | Y open | Y | Y | Carpet, PFs, WD GW ceiling, carpeted |
| 109 | Y open | Y | Y | DEM, carpet w/stains |
| 110 |  | Y | Y | Wood floor |
| 112 | Y | Y | Y | Carpet, mini fridge, computer lab |
| 114 |  | Y | Y | Wood floor |
| 115 |  | Y | Y | 1 WD CT, wood floor |
| 116 | Y | Y | Y | AI, carpet |
| 117 | Y | Y | Y | Portable AC - on, new carpet, fridge and microwave |
| 118 |  | Y | Y | Tile floor, WD plaster and peeling paint |
| 119 |  | Y | Y | Wood floor |
| 120 B | Y | Y | N | CPs, carpet, UF |
| 120 E | N | Y | N | MT, DEM |
| 122 | Y | Y | Y | Carpet (musty odor), DEM, debris on carpet |
| 123 |  | Y | Y | Wood floor |
| 126 A | Y | Y | Y | Storage, old carpet, ajar CT, wood floor |
| 126 B | Y | Y | Y | SPED sensory room, upholstery and cloth items, tile floor |
| 128 |  |  |  | Cobwebs near windowsill |
| 131 |  |  |  | Carpeted, PF |
| 132 |  |  |  |  |
| 133 |  |  |  | Carpeted, PF |
| 134 |  | Y | Y | Carpeted, PF, dust/debris on vents |
| 137 |  |  |  | Utility hole in wall |
| 139 |  |  |  | Carpeted, ajar CT |
| 144 |  | Y | Y | Carpeted, 4 WD CTs, dust/debris on vents, filter in ceiling vent, PC |
| 145 Computer Lab |  | Y | Y | Carpeted, dust/debris on vents, 3 WD CTs, filter in ceiling vent |
| 147 |  | Y | Y | Carpeted, dust/debris on vents, WD CT |
| 199 | Y open | Y | Y | Carpet |
| Auditorium Lower Level | N | Y | Y |  |
| B House | Y | Y | N | PC, Carpet, gap around utilities in CT |
| Boys Restroom |  |  | Y | Dust/debris on vents, WD CP and peeling paint |
| Girls Restroom | N | Y | Y |  |
| Staff/SPED Restroom |  |  | Y | Air filter, WD ceiling, toileting materials |
| Stage |  |  |  | Wood floor |
| Womens Restroom | N | N | Y | WD plaster, cleaning products |
| 004 |  | Y | Y | 1 WD CT, carpeted, WD plaster |
| 009 Courtyard Restaurant |  | Y | Y | Dust/debris on vents |
| 010 |  | Y | Y | 3 WD CT, carpeted |
| 012 | Y | Y | Y | Musty odor, tile floor, WD CTs x 4, PF, CPs, sinks |
| 012 |  | Y | Y | 1 WD CT, tile floor |
| 012 Kitchen Area | Y | Y | Y | Dirty supply vents/ghosting, DEM |
| 013 |  |  |  | WD CTs, missing light cover |
| 016 |  | Y | Y | Tile floor |
| 017 | Y | Y | Y | NC, sinks, fridge, stoves |
| 019 | Y | Y | Y | NC, FCU in ceiling, sinks |
| 020 | N | Y | Y | Tile floor, DEM |
| 021 | Y | Y | Y | WD CT, stained carpeting |
| 021 Laundry | N | Y | Y | MT, WD ceiling, ceiling-mounted AC/FCUs |
| 024 |  | Y | Y | Carpeted, WD/moldy CTs |
| 025 |  | Y | Y | Carpeted, dust/debris on vents |
| 026 Music |  | Y | Y | Stained CT and dust |
| 028 | N | Y | Y | Carpet, cleaner odors, WD CT, microwave |
| 028 Waiting Room | N | Y | Y | NC |
| 038 |  | Y | Y |  |
| 039 |  | Y | Y | Carpeted, dust/debris on vents, PF |
| Band Storage Room |  |  |  |  |
| Basement Girls Restroom | N | Y | Y | Sink, WD ceiling plaster, broken toilet |
| Boys Restroom |  |  | Y | WD ceiling |
| Mailroom |  | Y | Y | Tile floor |
| Music | N | Y | Y | Carpet, musty odor, MTs x 5, WD plaster ceiling above |
| Music-Office | N | Y | Y | WD CT, costumes, musty odor |

| - Location | Carbon Dioxide (ppm) | Carbon Monoxide (ppm) | Temp (°F) | Relative Humidity (%) | PM2.5 (µg/m3) | Occupants in Room | Windows Openable | Ventilation |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Supply | Exhaust |  |
| Background | 331 | ND | 51 | 67 | 23 |  |  |  |  | Rain, sleet, wind |
| Third Floor |  |  |  |  |  |  |  |  |  |  |
| Teacher’s center |  |  |  |  |  |  |  |  |  |  |
| Workroom | 878 | ND | 68 | 28 | 47 | 1 | Y | Y | Y | PC, carpet, one window ajar |
| Workroom classroom | 971 | ND | 69 | 29 | 9 | 0 | Y | Y | Y | Carpet, vending machine |
| Women’s restroom |  |  |  |  |  | 0 | N | Y | Y |  |
| Book storage | 1003 | ND | 70 | 27 | 7 | 0 | N | Y | Y | Books, some on floor |
| Upper level area |  |  |  |  |  |  |  |  |  |  |
| P161 | 896 | 1.8 | 72 | 32 | 11 | 1 | N | Y | Y |  |
| East | 846 | 1.8 | 69 | 30 | 9 | 0 | N | Y | Y |  |
| West | 826 | 2 | 66 | 28 | 7 | 0 | N | Y | Y | 11 WD CT |
| Third floor main area |  |  |  |  |  |  |  |  |  |  |
| 304A | 1128 | ND | 72 | 28 | 7 | 19 | Y | Y | Y | Tile, DEM, CPs |
| 305 A | 982 | ND | 70 | 29 | 7 | 11 | Y | Y | Y | Carpet, dust/debris on vents |
| 306 | 1118 | ND | 70 | 27 | 5 | 0 | Y | Y | Y | Carpet |
| 308 | 853 | ND | 70 | 27 | 17 | 1 | Y | Y | Y | 2 WD-CTs, WD wall plaster, DEM |
| 309 | 911 | ND | 71 | 28 | 6 | 9 | Y | Y | Y | Carpet, PF, 7 WD CTs, 2 PCs |
| 309 Office | 909 | ND | 70 | 29 | 6 | 0 | N | Y | N | Carpet |
| 310 | 1300 | ND | 72 | 34 | 18 | 25 | Y 3/5 open | Y | Y | DEM, clutter, plants, DO |
| 311 | 1309 | ND | 71 | 33 | 9 | 20 | Y | Y | Y | DO, WD CP, PFs |
| 312 | 831 | ND | 71 | 23 | 19 | 0 | Y | Y | Y | 29 computers, WD ceiling plaster |
| 313 | 1167 | ND | 71 | 33 | 8 | 19 | Y | Y | Y | DEM, wood floor |
| 314 | 830 | ND | 71 | 26 | 16 | 0 | Y | Y | Y | WD ceiling plaster, DEM, cleaning products |
| 315 | 1492 | ND | 72 | 35 | 7 | 23 | Y | Y | Y | PFs, WD CP |
| 316 | 1983 | ND | 72 | 34 | 9 | 16 | Y | Y | Y | Carpet, DEM |
| 317 storage/prep |  |  |  |  |  |  |  | Y | Y | Wood floor and cabinets, science items, dusty fan |
| 318 | 2208 | ND | 72 | 37 | 8 | 22 | Y | Y | Y | Hardwood floor |
| 319 | 1375 | ND | 71 | 32 | 8 | 25 | Y | Y | Y | DO, PF, WD CT |
| 320 | 1383 | ND | 72 | 28 | 5 | 3 | Y | Y | Y | DEM, old carpet |
| 321 | 1086 | ND | 72 | 38 | 7 | 24 | Y | Y | Y | Tile floor, portable AC, DEM |
| 323 | 712 | ND | 70 | 25 | 9 | 0 | N | Y | Y | Carpet, DO |
| 323 R | 578 | ND | 70 | 24 | 8 | 0 | Y | Y | Y | Carpet, AC |
| 324 | 954 | ND | 72 | 35 | 8 | 0 |  |  |  | Carpet, DEM, PF |
| 324 | 946 | ND | 72 | 27 | 18 | 16 | Y | Y | Y | DEM, PF, DO, WD wall plaster |
| 325 | 722 | ND | 70 | 29 | 7 | 15 | Y | Y | Y | DO, cracked window, WD CT, WD CP/peeling paint, area rug |
| 326 | 1044 | ND | 71 | 23 | 3 | 0 | Y | Y | Y | Old carpet, blocked gravity exhaust |
| 329 | 765 | ND | 70 | 28 | 7 | 22 | Y | Y | Y | Cracked window, PF |
| 330 | 1640 | ND | 72 | 30 | 10 | 7 | Y | Y | Y | DEM, old carpet |
| 331 | 1470 | ND | 70 | 33 | 11 | 21 | Y | Y | Y | Wood floor, DEM, chalk |
| 331 | 1499 | 1.2 | 69 | 37 | 8 | 5 | Y | y | Y |  |
| 332 | 1248 | 1.3 | 73 | 30 | 7 | 29 | Y | Y | Y | Carpet |
| 333 | 973 | ND | 69 | 25 | 8 | 0 | Y | Y | Y | Wood floor, DEM, PF - dusty |
| 333 | 928 | 0.8 | 69 | 29 | 7 | 30 | Y | Y | Y |  |
| 334 | 1660 | ND | 72 | 34 | 7 | 29 | Y | Y | Y | Carpet |
| 338 | 1246 | ND | 72 | 31 | 5 | 18 | Y | Y | Y | Carpet |
| 346 | 1112 | 1.8 | 71 | 30 | 3 | 26 | Y | Y | Y | Carpet |
| 348 | 1295 | ND | 72 | 30 | 14 | 0 some just left | Y | Y | Y | DEM, carpet, plant |
| 348 | 1458 | ND | 72 | 32 | 9 | 28 | Y | Y | Y | Carpet |
| 351 | 1112 | ND | 72 | 25 | 8 | 0 | Y | Y | Y | Carpet, damaged wall, 6 WD CT, DEM |
| 351 | 1089 | 1.6 | 71 | 27 | 5 | 0 | Y | Y | Y | Carpet, 5 WD CT |
| 352 | 1252 | 1.4 | 72 | 29 | 11 | 0 | Y | Y | Y | Carpet |
| Clark Office | 970 | ND | 71 | 26 | 7 | 11 | N | Y | Y | Carpet, 3 WD CT, PF |
| Coburn break area | 1104 | ND | 70 | 28 | 7 | 1 | Y | Y | Y | Soiled carpet |
| Coburn computer area | 830 | ND | 70 | 26 | 7 | 1 | Y | Y | Y | Soiled carpet |
| Coburn Teachers Area | 1211 | ND | 68 | 31 | 8 | 0 | Y | Y | Y | carpet |
| Cromwell Guidance | 1182 | ND | 69 | 28 | 9 | 0 | Y | Y | Y | DEM, 1 WD CT, WAC, carpet, WD ceiling plaster next to windows |
| custodial, electric near 324 |  |  |  |  |  |  |  |  |  |  |
| custodian closet near 321 |  | ND |  |  |  |  | N | N | N | Moldy smell, wet mop bucket, water damaged wall plaster and ceiling |
| Director of curriculum | 823 | ND | 69 | 27 | 17 | 0 | Y | Y Dusty | Y | DO, High efficiency particulate arrestance air purifier, plants, DEM, 4 WD-CTs |
| E house Dean | 1074 | ND | 68 | 27 | 7 | 2 | Y | Y | Y | Carpet |
| E house office left office | 1083 | ND | 69 | 28 | 7 | 0 | Y | Y | Y | Carpet, water cooler on carpet |
| E house reception | 1080 | ND | 69 | 28 | 6 | 2 | N | Y | Y | Carpet |
| Entry foyer | 579 | ND | 70 | 42 | 12 | 11 | N | Y | Y |  |
| Staff bathroom |  |  | 70 | 29 | 18 | 0 | Y | N | Y Dusty |  |
| Teachers Area office | 1130 | ND | 68 | 31 | 6 | 1 | N | Y | Y | PF |
| Women’s’ room |  |  | 70 | 28 | 17 |  |  | N | Y |  |
| Second Floor |  |  |  |  |  |  |  |  |  |  |
| Auditorium Balcony | 573 | ND | 71 | 26 | 5 | 0 | N | Y | Y |  |
| 201B | 770 | ND | 69 | 331 | 7 | 11 | Y | Y | Y | Carpet |
| 202 | 718 | ND | 70 | 31 | 6 | 0 | Y | Y | Y | Carpet |
| 204 U | 1678 | ND | 70 | 34 | 6 | 28 | Y | Y | Y | Carpet |
| 207B | 898 | ND | 68 | 32 | 6 | 5 | Y | Y | Y | Carpet |
| 208B | 831 | ND | 68 | 34 | 6 | 28 | Y | Y | Y | Carpet |
| 209A | 789 | ND | 67 | 31 | 8 | 0 | Y | Y | Y |  |
| 210 | 1256 | ND | 70 | 33 | 4 | 11 | Y | Y | Y | DEM, carpeting, active leak in overhead pipe |
| 212A | 1409 | ND | 70 | 33 | 7 | 23 | Y | Y | Y | Carpet, DEM |
| 213 | 1183 | ND | 71 | 27 | 7 | 1 | Y | Y | Y | Carpet, PF, plants |
| 214 | 1539 | ND | 68 | 35 | 5 | 15 | Y | Y | Y | Carpeting, DEM |
| 214A | 1060 | ND | 68 | 30 | 2 | 22 gone 25 min | Y | Y | Y gravity | Wood floor, HS, PF |
| 215 | 1290 | ND | 73 | 31 | 9 | 25 | Y | Y | Y | DO |
| 216 | 1056 | ND | 71 | 28 | 17 | 1 |  | Y | Y | PF, cleaning products, WD CP, DEM |
| 217 | 1247 | ND | 72 | 32 | 9 | 27 | Y | Y | Y | Carpet, DEM, plants, HS |
| 218 | 1541 | ND | 70 | 37 | 15 | 25 | Y | Y | Y |  |
| 219 | 1300 | ND | 73 | 31 | 10 | 22 | Y | Y | Y | DO |
| 220C | 1546 | ND | 70 | 34 | 14 | 8 | Y | Y | N | Carpet |
| 220B | 1307 | ND | 69 | 30 | 15 | 0 | N | N | Y |  |
| 220 | 1206 | ND | 69 | 37 | 13 | 0 | N | Y | Y | DO |
| 223 | 1171 | ND | 72 | 30 | 7 | 10 | Y | Y | Y |  |
| 224 | 1208 | ND | 71 | 30 | 10 | 21 | Y | Y | Y | Carpet, PF |
| 224 | 1355 | ND | 70 | 32 | 5 | 19 | Y | Y | Y | HS, DEM, carpeting, PF |
| 226 | 1179 | ND | 66 | 32 | 2 | 22 gone 10min | Y | Y | Y | DEM, HS |
| 227 | 1385 | ND | 70 | 30 | 6 | 22 | Y | Y | Y | Wood floor, chalk, DEM |
| 229 | 1079 | ND | 70 | 26 | 25 | 5 | Y | Y | Y | DEM, carpet, chalk |
| 230 | 1401 | ND | 68 | 35 | 13 | 22 | Y | Y | Y | DEM, HS |
| 231 | 836 | ND | 70 | 36 | 7 | 2 | Y | Y | Y | Wood floor, DEM, fridge, chalk |
| 232 | 1344 | ND | 70 | 34 | 15 | 26 | Y | Y | Y | WD ceiling plaster, DO, DEM, carpet |
| 234 | 986 | ND | 69 | 29 | 19=4 | 0 | Y | Y | Y | PF, DEM, refrigerator, DO |
| 235 | 1021 | ND | 69 | 17 | 6 | 6 | Y | Y | Y | DEM, PF, wood floor, fridge, chalk |
| 235 | 887 | ND | 68 | 30 | 7 | 7 | Y | Y | Y | Carpet |
| 237 | 965 | ND | 69 | 26 | 7 | 15 | Y | Y | Y | Wood floor, books on floor, DEM, chalk |
| 239 | 1237 | ND | 69 | 31 | 8 | 2 | Y | Y | Y | Wood floor, DEM |
| 248 | 674 | ND | 70 | 24 | 7 | 11 | Y open | Y | Y | DEM, Carpet, DO |
| 249 | 1360 | ND | 770 | 30 | 8 | 21 | Y | Y | Y | Computers, carpet, DEM |
| 251 | 1641 | ND | 70 | 31 | 5 | 24 | Y* | Y | Y | Old carpet, DEM, *windows don’t open (inoperable) |
| 254 | 1074 | ND | 71 | 28 | 15 | 0 | Y | Y | Y | DEM |
| First Floor |  |  |  |  |  |  |  |  |  |  |
| Auditorium | 550 | ND | 69 | 25 | 5 | 0 | Y | Y | Y | Some carpet |
| Auditorium lobby | 715 | ND | 66 | 28 | 7 | 1 | Y | Y | Y | Doors to street |
| 101 | 865 | ND | 71 | 32 | 6 | 32 | Y | Y | Y | WD plaster and floor |
| 105A | 805 | ND | 69 | 31 | 7 | 1 | Y | Y | Y |  |
| 106 | 854 | ND | 66 | 36 | 8 | 28 | Y | Y | Y | Carpet |
| 106A | 609 | 1.2 | 69 | 30 | 6 | 2 | Y | Y | Y | Carpet |
| 106A | 656 |  | 71 | 28 | 6 | 2 | Y | N | N | Carpet |
| 107 | 733 | 1 | 69 | 30 | 6 | 0 | Y | Y | Y | 2 WD CT |
| 108A | 568 | ND | 66 | 30 | 6 | 1 | Y | Y | Y | Carpet |
| 109 | 798 | 1.8 | 69 | 32 | 7 | 19 | Y 1 open | Y | Y |  |
| 113 | 837 | ND | 66 | 30 | 8 | 1 | Y | Y | Y | Carpet, DO, radiator leaks-buckets (on repair list) |
| 115 | 1121 | ND | 71 | 31 | 8 | 23 | Y | Y | Y | wood floor, DEM, small fridge, food |
| 117 | 1301 | ND | 68 | 33 | 10 | 2 | Y | Y | Y | Carpet |
| 119 | 1269 | ND | 71 | 32 | 7 | 23 | Y | Y | Y | Chalk, DEM, wood floor, built in cabinets |
| 121 | 931 | ND | 70 | 31 | 10 | 17 | Y | Y | Y | Carpet, plants |
| 123 | 1074 | ND | 70 | 29 | 8 | 23 | Y | Y | Y | Wood floor, DEM, HS |
| 125 | 679 | ND | 69 | 27 | 10 | 6 | Y | Y | Y | Carpet, duct tape window |
| 126B | 990 | ND | 68 | 29 | 7 | 0 |  |  |  | “snooze” room, bedding and soft furniture |
| 131 | 907 | ND | 70 | 31 | 9 | 14 | Y | Y | Y | Carpet |
| 133 | 794 | ND | 67 | 28 | 8 | 0 | Y | Y | Y | DEM, carpet, chalk |
| 135 stage | 895 | ND | 68 | 28 | 7 | 10 | N |  |  |  |
| 137 | 633 | ND | 69 | 28 | 8 | 10 | Y | Y | Y | Carpet |
| 139 | 703 | ND | 67 | 27 | 7 | 0 | Y | Y | Y | Carpet, AT, DEM, PS |
| 145 | 767 | ND | 65 | 30 | 9 | 0 | Y | Y | Y |  |
| 147 | 796 | ND | 67 | 30 | 9 | 18 | Y | Y | Y |  |
| Basement |  |  |  |  |  |  |  |  |  |  |
| Band | 628 | ND | 70 | 28 | 3 | 22 | N | Y | Y | DEM, carpet |
| Restaurant | 768 | ND | 70 | 28 | 5 | 4 | N | Y | Y | Carpeting |
| Weight room | 908 | ND | 67 | 34 | 13 | 12 | N | N | Y | WD ceiling |
| Gym office/storage | 862 | ND | 67 | 34 | 11 | 0 | N | N | Y |  |
| 12 | 834 | ND | 67 | 32 | 3 | 10 | N | Y | Y | Tile |
| 13 | 873 | ND | 69 | 32 | 4 | 22 | N | Y | Y | FCUs, tile, art supplies |
| 14 | 1122 | ND | 65 | 36 | 3 | 19 | N | Y | Y | Rubber mats |
| 16 | 930 | ND | 68 | 34 | 4 | 9 | N | Y | Y | DEM, tile |
| 17 cooking class | 618 | ND | 70 | 26 | 3 | 3 | N | Y | N* | *Need exhaust ventilation, DEM, HS, food odors |
| 18 | 768 | ND | 67 | 30 | 3 | 1 | N | Y | Y | DEM, odor |
| 19 | 645 | ND | 69 | 27 | 5 | 5 | N | Y | Y | HS, DEM, plants, laminate floor, FCU off, cleaning products |
| 20 | 717 | ND | 68 | 30 | 3 | 6 | N | Y | Y | DEM, tile |
| 21 | 1243 | ND | 68 | 32 | 3 | 6 | N | Y | Y | HS, carpet soiled |
| 22 office coordinator | 619 | ND | 68 | 26 | 13 | 2 | N | N | Y Switch activate | DO, transom |
| 22 social workers | 560 | ND | 67 | 25 | 14 | 0 | Y | Y | Y | Passive door |
| 22 main | 618 | ND | 67 | 26 | 14 | 1 | Y | Y | N |  |
| 22 quiet room | 709 | ND | 67 | 25 | 12 | 0 | N | N | Y Switch activate |  |
| 22 nurse main office | 589 | ND | 67 | 25 | 12 | 0 | Y | Y | Y |  |
| 22 exam room 1 | 659 | ND | 68 | 26 | 11 | 0 | Y | N | Y Switch activate |  |
| 24 | 578 | ND | 68 | 25 | 2 | 0 | N | Y | Y | Carpet |
| 22 exam room 2 | 749 | ND | 67 | 26 | 12 | 0 | N | N | Y Switch activate |  |
| 28 | 1048 | ND | 70 | 29 | 12 | 14 | Y | Y | Y | Food storage, DEM, refrigerator, 2 WD-CT |
| 28 language director | 1065 | ND | 70 | 29 | 10 | 1 | N | N | N | 2 MT, 1 WD-CT, CPs |
| 29 Band | 478 | ND | 69 | 27 | 3 | 0 | N | Y | Y | FCUs, carpet, MTs |
| 30 | 696 | ND | 69 | 25 | 5 | 17 | N | Y | Y | Carpet, WD CT |
| 37 | 736 | ND | 69 | 26 | 16 | 17 | Y | Y | Y Dusty | 4 MT, 7 WD-CT |
| 39 | 645 | ND | 70 | 27 | 14 | 0 | Y | Y | Y |  |
| Old building |  |  |  |  |  |  |  |  |  |  |
| 001 back storage | 648 | ND | 63 | 32 | 14 | 0 | N | N | N | WD ceiling, WD CT, MT, predominately storage |
| ROTC uniform room | 433 | ND | 71 | 29 | 17 | 0 | Y | Y | Y | Musty odors, 3 MT, dehumidifiers |