INDOOR AIR QUALITY ASSESSMENT

Lunenburg High School

1079 Massachusetts Avenue

Lunenburg, Massachusetts

Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health Assessment

February 2008

# Background/Introduction

At the request of John Londa, Director of Facilities and Grounds for the Lunenburg School Department, the Massachusetts Department of Public Health (MDPH), Bureau of Environmental Health (BEH) provided assistance and consultation regarding indoor air quality at the Lunenburg High School, 1079 Massachusetts Avenue, Lunenburg, Massachusetts.

On November 20, 2007, a visit to conduct an indoor air quality assessment was made to this school by Michael Feeney, Director of BEH’s Indoor Air Quality (IAQ) Program, and Susan Koszalka, the Northeast Regional Inspector within BEH’s IAQ Program.  Mr. Feeney and Ms. Koszalka were accompanied by Mr. Londa during the assessment. The building was previously visited by BEH staff in November 2001. A report was issued detailing conditions observed at the time of the visit (MDPH, 2001).  Appendix A is a summary of actions taken in response to the previous assessment.

Methods

Air tests for carbon monoxide, carbon dioxide, temperature and relative humidity were taken with the TSI, Q-Trak, IAQ Monitor, Model 8551.  BEH staff also performed a visual inspection of the building materials for water damage and microbial growth.

Results

The school houses approximately 550 students in grades 9 through 12 and approximately 70 staff members.  The tests were taken during normal operations at the school.  Test results appear in Table 1.

Discussion

Ventilation

It can be seen from the Table 1 that carbon dioxide levels were elevated above 800 parts per million of air (ppm) in 38 of 48 areas surveyed, indicating inadequate fresh air ventilation in most areas tested.  Fresh air in classrooms is supplied by a unit ventilator (univent) system (Figure 1).  Univents draw air from outdoors through a fresh air intake located on the exterior walls of the building and return air through an air intake located at the base of each unit.  The mixture of fresh and return air is drawn through a filter and heating coil, and is then expelled from the univent by motorized fans through fresh air diffusers.  Obstructions to airflow, such as papers and books stored on univents and bookcases, carts, desks and other materials in front of univent returns were seen in a number of classrooms.  Some univents also contained accumulated dirt/debris.  These univents should be cleaned before operating to prevent aerosolization of this material.  In order for univents to provide fresh air as designed, intakes must remain free of obstructions.  Importantly, the units must remain “on” and allowed to operate while these rooms are occupied.

Univent fresh air intakes in several locations (i.e. the enclosed courtyard, outer exterior wall of the building) are located within subterranean, cement-walled pits (Picture 1).  An accumulation of leaves and debris was observed below a number of these fresh air intakes.  Wet leaves can provide a source for mold growth and odors that can be entrained into the building by the air handling equipment.

Exhaust ventilation in classrooms is provided by a mechanical system consisting of ducted, grated wall vents.  Exhaust ventilation was not operating efficiently in some areas during the assessment.  Several exhaust vents were blocked by desks or other items.  In order for exhaust ventilation to function as designed, vents must be activated and remain free of obstructions.

To maximize air exchange, the MDPH recommends that both supply and exhaust ventilation operate continuously during periods of school occupancy.  In order to have proper ventilation with a univent and exhaust system, the systems must be balanced to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room.  According to school department officials, the date of the last balancing of these systems was not available at the time of the assessment.  It is recommended that existing ventilation systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).

The Massachusetts Building Code requires a minimum ventilation rate of 15 cubic feet per minute (cfm) per occupant of fresh outside air or have openable windows in each room (SBBRS, 1997; BOCA, 1993).  The ventilation must be on at all times that the room is occupied.  Providing adequate fresh air ventilation with open windows and maintaining the temperature in the comfort range during the cold weather season is impractical.  Mechanical ventilation is usually required to provide adequate fresh air ventilation.

Carbon dioxide is not a problem in and of itself.  It is used as an indicator of the adequacy of the fresh air ventilation.  As carbon dioxide levels rise, it indicates that the ventilating system is malfunctioning or the design occupancy of the room is being exceeded.  When this happens a buildup of common indoor air pollutants can occur, leading to discomfort or health complaints.  The Occupational Safety and Health Administration (OSHA) standard for carbon dioxide is 5,000 parts per million parts of air (ppm).  Workers may be exposed to this level for 40 hours/week, based on a time weighted average (OSHA, 1997).

The MDPH uses a guideline of 800 ppm for publicly occupied buildings.  A guideline of 600 ppm or less is preferred in schools due to the fact that the majority of occupants are young and considered to be a more sensitive population in the evaluation of environmental health status.  Inadequate ventilation and/or elevated temperatures are major causes of complaints such as respiratory, eye, nose and throat irritation, lethargy and headaches. For more information concerning carbon dioxide, please see Appendix B.

Temperature readings ranged from 66o F to 73 o F, which were within or close to the lower end of the MDPH recommended comfort level.  The MDPH recommends that indoor air temperatures be maintained in a range between 70 o F to 78 o F in order to provide for the comfort of building occupants.  It is difficult to control temperature and maintain comfort without the ventilation equipment operating as designed.  In many cases concerning indoor air quality, fluctuations of temperature in occupied spaces are typically experienced, even in a building with an adequate fresh air supply.  Lack of ventilation can lead to poor indoor air quality and comfort complaints.  While temperature readings outside the recommended range are generally not a health concern, decreased temperature can affect the relative humidity in a building.

The relative humidity measurements ranged from 23 percent to 39 percent, below the MDPH recommended comfort range.  The MDPH recommends a comfort range of 40 to 60 percent for indoor air relative humidity.  Relative humidity levels in the building would be expected to drop during the winter months due to heating.  The sensation of dryness and irritation is common in a low relative humidity environment.  Low relative humidity is a very common problem during the heating season in the northeast part of the United States.

Microbial/Moisture Concerns

Plants were noted throughout the school.  A number of classrooms have water damaged windowsills that appear to have resulted from over watering of plants . In several rooms, large plants are located on wall-to-wall carpeting (Picture 2).  Plants should be properly maintained and equipped with drip pans.  Plants should be located away from ventilation sources (e.g., air intakes, univent diffusers) to prevent the entrainment and/or aerosolization of dirt, pollen or mold.

Water-damaged ceiling tiles were observed in several areas (Table 1), which can indicate leaks from the roof or plumbing system.  Water-damaged ceiling tiles can provide a source for mold growth and should be replaced after a water leak is discovered and repaired. Water-damaged ceiling materials, some of which appeared to be constructed of gypsum wallboard, were observed in several classrooms and offices.

The US Environmental Protection Agency (US EPA) and the American Conference of Governmental Industrial Hygienists (ACGIH) recommend that porous materials be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2001; ACGIH, 1989).  If not dried within this time frame, mold growth may occur.  Once mold has colonized porous materials, they are difficult to clean and should be removed/discarded.

Within the central courtyard is a greenhouse.  Also within this area is a compost heap in close proximity to a classroom fresh air intake.  Compost heaps may be a source of odors as materials degrade, particularly if the piled materials are not turned regularly.  As with shrubbery, compost heaps can be a source of odor, particulates and microbes that can be entrained by the univents in the courtyard.

Other Concerns

A number of other conditions that can affect indoor air quality were noted during the assessment.  An odor was detected in Room 222.  This odor was traced to a storage closet, containing ductwork from the water heater (Picture 3), which is located in the crawlspace below room 222.  The seams to the exhaust ductwork were not sealed with mastic.  When the exhaust system for the water heater is activated, combustion products are driven up the ductwork.  As a result, the vent becomes pressurized.  Therefore, if any unsealed holes or seams exist in the ductwork, the combustion products from the gas-fired water heater can escape from the ductwork.  No measurable levels of carbon monoxide were detected in Room 222 or its closet during this assessment.

BEH staff examined the hot water heater (Picture 4) and detected a noticeable metallic taste when in close proximity to the water heater, while the exhaust system was deactivated.  Metallic tastes are an unusual occurrence; this may indicate a malfunction in the water heater that is producing metal fume during its operation.  Metal fumes may also enter Room 222 via holes or seams in the ductwork or migration the spaces between the ducts and the floor in the closet.  Products of combustion and metal fumes can be sources of eye, nose and throat irritation.

A strong sewage odor was observed in the area where the sewage ejector pumps are located.  As reported by Mr. Londa, a backhoe breached a PVC pipe that encloses the telephone lines located outside the building.  The breach resulted in water penetration to the sewage ejector room (Picture 5).  In order for water to drain from this room, a jerry-rigged drain system was installed in the sewage collect tank, thereby allowing odors to escape from the sewage ejector system.  In this condition, groundwater and odors from the broken pipe and the sewage ejector system could all be sources of odor in this room.  An exhaust fan was installed in this room, but it was deactivated at the time of the assessment.

The chemistry classroom contains a chemical fume hood.  The efficacy of the draw of air through this equipment could not be determined.  In addition, no record of the last date of calibration of the chemical hood was readily apparent.  Chemical hoods should be calibrated on an annual basis to ensure proper function.  No dated inspection sticker indicating such could be found on the hood.

A number of food containers being reused in several classrooms were noted. No labeling on the containers was observed.  Exposed food products and reused food containers can attract a variety of pests.  The presence of pests inside a building can produce conditions that can degrade indoor air quality.  For example, rodent infestation can result in indoor air quality related symptoms due to materials in their wastes.  Mouse urine is known to contain a protein that is a known sensitizer (US EPA, 1992).  A sensitizer is a material that can produce symptoms in exposed individuals, including nose irritations and skin rashes.  Pest attractants should be reduced/eliminated.  Proper food storage is an integral component in maintaining indoor air quality.  Food should be properly stored and clearly labeled.  Reuse of food containers (e.g., for art projects) is not recommended since food residue adhering to the container surface may serve to attract pests.

Several abandoned sinks and one abandoned eyewash station were observed. The traps for these drains can dry out which can lead to sewer gas odors penetrating the room through unsealed traps. Sewer gas odors can be irritating to the eyes, nose, and throat.

A chemistry storage area on the lower level contained a standard-sized refrigerator with small containers in the freezer; the freezer’s ice buildup was evident. In order for a refrigerator system to work properly, the freezer should be defrosted and cleaned according to manufacturer’s instructions.  A smaller refrigerator was also present in the area.  An electrical smell was detected.

The gymnasium had cracked block windows, as originally noted in the BEH assessment of 2001 (Picture 6).  Glass window blocks were heavily damaged by vandalism in many classrooms.  Exterior surfaces of glass blocks are either broken or cracked.  Several glass blocks were broken in a manner to allow for water to accumulate within the block, creating an “aquarium-like” appearance..  Damage to blocks can lead to water penetration through masonry and serve as a potential microbial growth source.  Moistened cardboard can be a mold growth medium.  Standing water in these blocks can stagnate leading to bacterial growth, mold growth and possible nuisance odors.

Most classrooms contained dry erase boards and dry erase markers.  Materials such as dry erase markers and dry erase board cleaners may contain VOCs, (e.g., methyl isobutyl ketone, n-butyl acetate and butyl-cellusolve) (Sanford, 1999).  Several cans of air freshener were observed in various areas of the school, including some classrooms.  Air fresheners and dry erase markers can be irritants to the eyes, nose and respiratory system.

A number of areas are cooled using wall or window-mounted air conditioners (WMAC).  Some air conditioners have the capacity to introduce fresh air, however the majority of installed machines recycle indoor air only.

Conclusions/Recommendations

The conditions noted at the Lunenburg High School raise several indoor air quality concerns.  A two-phase approach is required to adequately address overall indoor air quality concerns.  This approach consists of short-term measures to improve air quality and long-term measures that will require planning and resources.  In view of the findings at the time of the visits, the following recommendations are made:

Short Term Recommendations

- The jerry-rigged drain system for the broken PVC telephone wire should be rendered air tight and all seams in the sewage ejector system should be sealed.  The exhaust fan in the room should be operating during school operating hours at minimum.

- Seal all the seams and holes in all ductwork in the room 222 closet with an appropriate sealing compound.  Spaces between the floor and duct should also be sealed.  Consider consulting a ventilation engineer to identify the metal fume source in the water heater.  Consideration should be give to relocating the exhaust vent motor to the roof so that the water heater exhaust vent is internally depressurized.

- Remove leaves and other debris from univent fresh air intake subterranean pits, clean and inspect periodically.

- Ensure classroom doors are closed to maximize air exchange.

- Operate both supply and exhaust ventilation continuously during periods of school occupancy independent of classroom thermostat control to maximize air exchange.

- Examine each univent for function.  Survey classrooms for univent function to        ascertain if an adequate air supply exists for each room.  Operate fresh air supply univents while classrooms are occupied.  Consider consulting a heating, ventilation and air conditioning (HVAC) engineer concerning the calibration of univent fresh air control dampers school-wide.

- Remove all blockages from univents and exhaust vents.

- Consult a ventilation engineer concerning re-balancing of the ventilation systems.  Ventilation industrial standards recommend that mechanical ventilation systems be balanced every five years (SMACNA, 1994).

- For buildings in New England, periods of low relative humidity during the winter are often unavoidable.  Therefore, implementation of scrupulous cleaning practices should be implemented.  This will minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low.  Use of vacuum cleaning equipment outfitted with a high efficiency particulate arrestance (HEPA) filter is recommended.  Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

- Move plants away from univents in classrooms.  Ensure plants have drip pans, and examine drip pans for mold growth and disinfect areas of water leaks with an        appropriate antimicrobial where necessary.

- Relocate compost pile from inner courtyard.

- Remove plants from floor with wall-to-wall carpeting.  Consider reducing the number of plants.

- Cut shrubbery in a manner to maintain a space of 3 feet from univent fresh air         intakes.

- Defrost refrigerator and remove chemical containers.  If containers are damaged, dispose of chemicals in a manner consistent with Massachusetts hazardous waste        laws and regulations.

- Refrain from using strongly scented materials (e.g., air fresheners).

- Ensure chemical fume hoods in the science areas are operating properly.  Science staff should work with school administration and their HVAC vendor to develop a preventative maintenance program for all local exhaust equipment (e.g. lab hoods, prep rooms).

- Refrain from re-using food containers.

Long Term Recommendations

- Examine the feasibility of replacing damaged gymnasium block windows.

- Repair the broken PVC telephone conduit.

References

ACGIH.  1989.  Guidelines for the Assessment of Bioaerosols in the Indoor Environment.  American Conference of Governmental Industrial Hygienists, Cincinnati, OH.

BOCA.  1993.  The BOCA National Mechanical Code/1993.  8th ed.   Building Officials and Code Administrators International, Inc., Country Club Hill, IL.  Section M-308.1.1.

MDPH. 2001.Indoor Air Quality Assessment: Lunenburg High School, Lunenburg, Massachusetts, November 2001. http://mass.gov/Eeohhs2/docs/dph/environmental/iaq/towns_i_m/lunenburg_hs01.pdf

OSHA.  1997.  Limits for Air Contaminants.  Occupational Safety and Health Administration.  Code of Federal Regulations.  29 C.F.R 1910.1000 Table Z-1-A.

Sanford.  1999.  Material Safety Data Sheet (MSDS No: 198-17).  Expo Dry Erase Markers Bullet, Chisel, and Ultra Fine Tip.  Sanford Corporation.  Bellwood, IL.

SBBRS.  1997.  Mechanical Ventilation.  State Board of Building Regulations and Standards.  Code of Massachusetts Regulations.  780 CMR 1209.0

SMACNA.  1994.  HVAC Systems Commissioning Manual.  1st ed.  Sheet Metal and Air Conditioning Contractors’ National Association, Inc

US EPA.  1992.  Indoor Biological Pollutants.  US Environmental Protection Agency, Environmental Criteria and Assessment Office, Office of Health and Environmental Assessment, research Triangle Park, NC.  EPA 600/8-91/202 January 1992.

US EPA.  2001.  Mold Remediation in Schools and Commercial Buildings. US Environmental Protection Agency, Office of Air and Radiation, Indoor Environments Division, Washington, D.C.  EPA 402-K-01-001.  March 2001.

Picture 1

Cement Lined Pit Containing Univent Fresh Air Intake

Picture 2

Plant On Carpet

Picture 3

Ductwork In Closet, Room 222

Picture 4

Water Heater

Picture 5

Telephone Conduit Leaking Water In Sewage Ejector Room

Picture 6

Damaged Glass Block, Gymnasium

| # Location | Carbon Dioxide (ppm) | Temp (°F) | Relative Humidity (%) | Occupants in Room | Windows Openable | Ventilation |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Supply | Exhaust |  |
| Outside (Background) | 401 | 34 | 87 |  |  |  |  | Snow/mist |
| 229 | 1290 | 66 | 39 | 0 | Y | Y | Y | Dry erase markers, 2 water-damaged ceiling tiles |
| 230 | 1282 | 73 | 29 | 18 | Y | Y | Y | Door open |
| 228 | 1381 | 71 | 28 | 22 | Y | Y | Y | Dry erase markers, door open |
| 227 | 1582 | 71 | 29 | 20 | Y | Y | Y | Dry erase markers |
| 226 | 1323 | 71 | 27 | 18 | Y | Y | Y | Dry erase markers |
| Library | 762 | 71 | 23 | 4 | Y | Y | Y | Ceiling repair |
| Computer Room | 857 | 72 | 24 | 4 | Y | Y | Y | 30 Computers, door open, personal fan, dry erase markers, water-damaged ceiling tiles |
| Conference Room | 864 | 69 | 24 | 0 | N | N | N | Door vent, dry erase markers, water-damaged ceiling tiles |
| Guidance Office | 871 | 69 | 24 | 1 | Y | N | N | Window air conditioner, plants on floor |
| Mrs. Tousignant’s Office | 840 | 68 | 24 | 0 | N | Y | Y | Draft in exhaust vent, door vent, supply and exhaust off |
| Technology Room | 756 | 72 | 24 | 1 | Y | N | N | Window air conditioner, water-damaged ceiling tiles |
| 201 | 832 | 71 | 25 | 5 | Y | Y | Y | Photocopier, plants on carpet, dry erase markers, window air conditioner |
| 202 | 830 | 70 | 28 | 0 | Y | Y | Y | Dry erase markers, food container reuse, hole in ceiling, clean fish tank |
| 203 | 798 | 69 | 27 | 0 | Y | Y | Y | Dry erase marker, clutter |
| 205 | 524 | 69 | 23 | 0 | Yo | Y | Y | Window open, dry erase markers |
| 204 | 970 | 71 | 28 | 15 | Y | Y | Y | Dry erase markers, 31 computers |
| 207 | 563 | 69 | 23 | 0 | Y | Y | Y | Holes in ceiling, glue on ceiling, dry erase markers |
| 206A | 1054 | 68 | 30 | 3 | Y | N | Y | Glue and repair on ceiling, dry erase markers, personal fan |
| 208 | 861 | 68 | 27 | 19 | Y | Y | Y | Dry erase markers |
| 209 | 1304 | 68 | 32 | 18 | Y | Y | Y | Ceiling repair, dry erase markers, clutter on univent, plants on univent |
| 211 | 978 | 68 | 28 | 11 | Y | Y | Y | Boxes near exhaust, plants on floor, plants near univent, dry erase marker, ceiling repair |
| 212 | 798 | 70 | 26 | 1 | Y | Y | Y | Ceiling repair, water-damaged ceiling, ceiling repair, dry erase markers |
| 213 | 1255 | 71 | 30 | 16 | Y | Y | Y | Objects on and near univent, holes in walls, personal fan, dry erase markers |
| 214 | 816 | 71 | 26 | 0 | Y | Y | Y | Books on univent, exhaust partially blocked, air fresheners, ceiling repair, dry erase markers, plants near univent |
| 215 | 1611 | 70 | 30 | 20 | Y | Y | Y | Dry erase markers, clutter on univent, books on overhead light fixture, exhaust partially blocked by paper |
| 216 | 1682 | 70 | 32 | 19 | Y | Y | Y | Dry erase markers, clutter on univent, plant on floor, exhaust weak and partially blocked |
| 218 | 1612 | 70 | 33 | 18 | Y | Y | Y | Dry erase markers near univent, plant on floor, exhaust partially blocked by desk |
| 217 | 1237 | 71 | 29 | 19 | Y | Y | Y | Dry erase markers |
| 219 | 888 | 71 | 26 | 0 | Y | Y | Y | Clutter around univent, dry erase markers, exhaust partially blocked |
| Teachers’ Dining | 940 | 70 | 26 | 3 | Y | N | Y | Door vent, ceiling repair, personal fan, radiator, musty odor |
| Café | 1186 | 69 | 28 | 150+ | Y | Y | Y |  |
| Gym | 835 | 68 | 26 | 16 | N | Y | Y | Broken block windows |
| Weight Room | 586 | 67 | 24 | 0 | Y | Y | Y |  |

| # Location | Carbon Dioxide (ppm) | Temp (°F) | Relative Humidity (%) | Occupants in Room | Windows Openable | Ventilation |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Supply | Exhaust |  |
| 201 | 832 | 71 | 25 | 5 | Y | Y | Y | Photocopier, plants on carpet, dry erase markers, window air conditioner |
| 202 | 830 | 70 | 28 | 0 | Y | Y | Y | Dry erase markers, food container reuse, hole in ceiling, clean fish tank |
| 203 | 798 | 69 | 27 | 0 | Y | Y | Y | Dry erase marker, clutter |
| 205 | 524 | 69 | 23 | 0 | Yo | Y | Y | Window open, dry erase markers |
| 204 | 970 | 71 | 28 | 15 | Y | Y | Y | Dry erase markers, 31 computers |
| 207 | 563 | 69 | 23 | 0 | Y | Y | Y | Holes in ceiling, glue on ceiling, dry erase markers |
| 206A | 1054 | 68 | 30 | 3 | Y | N | Y | Glue and repair on ceiling, dry erase markers, personal fan |
| 208 | 861 | 68 | 27 | 19 | Y | Y | Y | Dry erase markers |
| 209 | 1304 | 68 | 32 | 18 | Y | Y | Y | Ceiling repair, dry erase markers, clutter on univent, plants on univent |
| 211 | 978 | 68 | 28 | 11 | Y | Y | Y | Boxes near exhaust, plants on floor, plants near univent, dry erase marker, ceiling repair |
| 212 | 798 | 70 | 26 | 1 | Y | Y | Y | Ceiling repair, water-damaged ceiling, ceiling repair, dry erase markers |

*ppm = parts per million in air

| # Location | Carbon Dioxide (ppm) | Temp (°F) | Relative Humidity (%) | Occupants in Room | Windows Openable | Ventilation |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Supply | Exhaust |  |
| 213 | 1255 | 71 | 30 | 16 | Y | Y | Y | Objects on and near univent, holes in walls, personal fan, dry erase markers |
| 214 | 816 | 71 | 26 | 0 | Y | Y | Y | Books on univent, exhaust partially blocked, air fresheners, ceiling repair, dry erase markers, plants near univent |
| 215 | 1611 | 70 | 30 | 20 | Y | Y | Y | Dry erase markers, clutter on univent, books on overhead light fixture, exhaust partially blocked by paper |
| 216 | 1682 | 70 | 32 | 19 | Y | Y | Y | Dry erase markers, clutter on univent, plant on floor, exhaust weak and partially blocked |
| 218 | 1612 | 70 | 33 | 18 | Y | Y | Y | Dry erase markers near univent, plant on floor, exhaust partially blocked by desk |
| 217 | 1237 | 71 | 29 | 19 | Y | Y | Y | Dry erase markers |
| 219 | 888 | 71 | 26 | 0 | Y | Y | Y | Clutter around univent, dry erase markers, exhaust partially blocked |
| Teachers’ Dining | 940 | 70 | 26 | 3 | Y | N | Y | Door vent, ceiling repair, personal fan, radiator, musty odor |
| Café | 1186 | 69 | 28 | 150+ | Y | Y | Y |  |
| Gym | 835 | 68 | 26 | 16 | N | Y | Y | Broken block windows |
| Weight Room | 586 | 67 | 24 | 0 | Y | Y | Y |  |
| Music Room | 1363 | 69 | 34 | 3 | N | Y | Y | Dry erase markers, univent on ceiling |
| 220 | 1299 | 70 | 38 | 1 | Y | Y | Y | Dry erase markers, washer/dryer, electric stove, univent-partially blocked |
| 221 | 1507 | 71 | 38 | 21 | Y | Y | Y | Dry erase markers |
| 222 | 1814 | 69 | 34 | 24 | Y | Y | Y | Dry erase markers, books on univent, plant near univent |
| Storage off 222 | 1106 | 70 | 32 | 0 | N | N | N | Drain, hot water exhaust. Odor noted. |
| Auditorium | 1112 | 70 | 28 | 0 | N | Y | Y | Recirculated air |
| 223-Art Room | 1090 | 71 | 26 | 7 | Y | Y | Y | Kiln, univent partially blocked |
| Art Supply Closet | 1072 | 70 | 27 | 0 | N | N | N | 12, 1 gallon containers of rubber cement; Hexane spray-fix |
| Art Classroom | 1276 | 70 | 30 | 21 | Y | Y | Y | Ceiling repair, dry erase markers, univent partially blocked |
| 101-Industrial Arts | 677 | 68 | 25 | 14 | Y | Y | Y | Univent noisy, paint cans and wood present, exhaust venting to outside |
| 103-Film Developing area |  |  |  | 0 | N | N | N | Sulfur odor noted, two abandoned sinks with dry drain traps |
| 105 | 488 | 70 | 23 | 0 | Y | Y | Y | Window air conditioner, abandoned eyewash |
| 104-Chemistry | 1036 | 70 | 27 | 24 | Y | Y | Y | Acid storage cabinet and Flammable Storage cabinet present |
| 107 | 1492 | 69 | 31 | 17 | Y | Y | Y | Dry erase markers, food containers |
| 106 | 1063 | 69 | 28 | 0 | N | N | N | Dry erase markers, food containers, plants near univent |
| 108 | 948 | 69 | 27 | 1 | Y | Y | Y | Dry erase markers |
| 109 | 1014 | 70 | 28 | 14 | Y | Y | Y | Dry erase markers, empty soda bottles |
| Mechanical Room | 563 | 71 | 24 | 0 | N | Y | Y | Metallic taste noted by large capacity hot water heater |

Appendix A

Actions on Previous MDPH Recommendations

The following is a status report of actions taken on MDPH recommendations (in

bold).  The summary is based on reports from Lunenburg High School Department Officials, as well as photographs and observations made by MDPH staff.

- Remove leaves and other debris from univent fresh air intake subterranean pits, clean & inspect periodically.

Action Taken:  Leaves are removed from the fresh air intake subterranean pits annually after leaf fall is complete.

- Disconnect the flammable storage cabinet from the PVC pipes and reseal the cabinet with its original bunghole caps.

Action Taken: Completed.

- Disconnect the vent attached to the chemical hood duct. Render the chemical hood duct airtight.

Action Taken: Completed.

- Repair back-drafting exhaust vents.

Action Taken: As denoted in report, exhaust vents were not operating in some locations due to motor malfunction at time of this assessment.

- Remove/relocate compost pile from inner courtyard.

Action Taken: Compost heap remain in courtyard.

- Remove plants from floor with wall-to-wall carpeting. Move plants away from univents in classrooms. Ensure plants have drip pans. Examine drip pans periodically for mold growth and disinfect with an appropriate antimicrobial where necessary. Consider reducing the number of plants in certain areas.

Action Taken:  Plants remain on carpeting, see report.

- Vent clothes dryers directly outdoors.

Action Taken: Completed.

- Repair water damaged sink countertops.

Action Taken: Completed.

- Install guard along edge of chemical storage area shelves.

Action Taken: Completed.

- Defrost refrigerator and remove chemical. If containers are damaged, dispose of chemicals in a manner consistent with Massachusetts hazardous waste laws and regulations.

Action Taken: Not completed by science faculty.

- Remove mold colonized materials from the fall out shelter. Disinfect non-porous surfaces with an appropriate antimicrobial.

Action Taken: Completed.

Long Term Recommendations

- Examine the feasibility of providing local exhaust ventilation for printing press machines and photocopying equipment in graphics classroom. If not feasible, consider moving graphic arts to another room where local exhaust ventilation can be provided.

Action Taken: Press machines and photocopying equipment removed.

- Examine the feasibility of replacing damaged gymnasium block windows.

Action Taken: See report.

- Examine the feasibility of restoring exhaust ventilation for room 239.

Action Taken:  Completed