| UST Owner/Operator Requirements: - Manual tank gauging shall be conducted every 30 days. - Manual tank gauging shall be conducted in accordance with 310 CMR 80.26(8)(b). - A release or leakage shall be suspected if the variation between the beginning and ending measurements exceed the Monthly Standard of: Nominal Tank Capacity; Monthly Standard (Average of Four Tests). More than 1,000 gallons; 7 gallons plus 2 gallons for every additional 1000 gallons capacity. - Within 72 hours of suspected release or leakage: - Check inventory input and output records for mathematical error; and - Check inventory for error in measurements. - If suspected release or leakage cannot be reconciled, the UST system shall be tightness tested within 72 hours of the suspected release or leakage not being reconciled. - Any failed tightness test requires compliance with 310 CMR 80.33 within 24 hours of obtaining knowledge of a release, or 72 hours of obtaining knowledge of leakage. - Maintain all records in a hard copy or electronic log for a minimum of four years. Note: These tanks and pumps are required to conduct an annual tightness test in accordance with 310 CMR 80.32. (310 CMR 80.26(8)) |
| --- |
| Facility Name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | UST ID# |  |  |  |  |  |  |
| Tank # |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Beginning Reading Date |  |  |  |  |  |  |  | Beginning Reading Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Beginning Reading #1 |  |  |  |  | Beginning Reading #2 |  |  |  |  |  |  |  | Beginning Reading Avg. |  |  |  |  |  |  |  |  |  |  |
| Ending Reading Date |  |  |  |  |  |  |  | Ending Reading Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ending Reading #1 |  |  |  |  | Ending Reading #2 |  |  |  |  |  |  |  | Ending Reading Avg. |  |  |  |  |  |  |  |  |  |  |
| Does the variation between the beginning and ending measurements exceed the Monthly Standard? If Yes, tightness testing is required within 72 hours. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes No |  |  |  |
| If Required, Tightness Test Date |  |  |  |  |  |  |  |  | Attach Test Results |  |  |  |  |  |  | Pass |  |  |  | Fail: Release |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Fail: Leakage |  |  |  |
| Failed Test: Release |  | All product removed from UST within 24 hours of failed test? |  |  |  |  |  |  |  | Yes |  | No |  | Date Removed (HW Manifest attached) |  |  |  |  |  |  |  |  |  |
| Failed Test: Leakage |  | All product removed from UST within 72 hours of failed test? |  |  |  |  |  |  |  | Yes |  | No |  | Date Removed (HW Manifest attached) |  |  |  |  |  |  |  |  |  |
| Facility Name |  |  |  |  |  |  |  |  |  |  |  |  |  |  | UST ID# |  |  |  |  |  |  |  |  |
| Tank # |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Beginning Reading Date |  |  |  |  |  |  |  | Beginning Reading Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Beginning Reading #1: |  |  |  |  | Beginning Reading #2: |  |  |  |  |  |  |  | Beginning Reading Avg. |  |  |  |  |  |  |  |  |  |  |
| Ending Reading Date |  |  |  |  |  |  |  | Ending Reading Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ending Reading #1: |  |  |  |  | Ending Reading #2: |  |  |  |  |  |  |  | Ending Reading Avg. |  |  |  |  |  |  |  |  |  |  |
| Does the variation between the beginning and ending measurements exceed the Monthly Standard? If Yes, tightness testing is required within 72 hours. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| If Required, Tightness Test Date |  |  |  |  |  |  | Attach Test Results |  |  |  |  |  |  |  |  | Pass |  |  | Fail: Release |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Fail: Leakage |  |  |  |  |
| Failed Test: Release |  | All product removed from UST within 24 hours of failed test? |  |  |  |  |  |  |  | Yes |  | No |  | Date Removed (HW Manifest attached): |  |  |  |  |  |  |  |  |  |
| Failed Test: Leakage |  | All product removed from UST within 72 hours of failed test? |  |  |  |  |  |  |  | Yes |  | No |  | Date Removed (HW Manifest attached): |  |  |  |  |  |  |  |  |  |
| Tank # |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Beginning Reading Date |  |  |  |  |  |  |  | Beginning Reading Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Beginning Reading #1: |  |  |  |  | Beginning Reading #2: |  |  |  |  |  |  |  | Beginning Reading Avg. |  |  |  |  |  |  |  |  |  |  |
| Ending Reading Date |  |  |  |  |  |  |  | Ending Reading Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ending Reading #1: |  |  |  |  | Ending Reading #2: |  |  |  |  |  |  |  | Ending Reading Avg. |  |  |  |  |  |  |  |  |  |  |
| Does the variation between the beginning and ending measurements exceed the Monthly Standard? If Yes, tightness testing is required within 72 hours. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| If Required, Tightness Test Date |  |  |  |  |  |  | Attach Test Results |  |  |  |  |  |  |  |  | Pass |  |  | Fail: Release |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Fail: Leakage |  |  |  |  |
| Failed Test: Release |  | All product removed from UST within 24 hours of failed test? |  |  |  |  |  |  |  | Yes |  | No |  | Date Removed (HW Manifest attached): |  |  |  |  |  |  |  |  |  |
| Failed Test: Leakage |  | All product removed from UST within 72 hours of failed test? |  |  |  |  |  |  |  | Yes |  | No |  | Date Removed (HW Manifest attached): |  |  |  |  |  |  |  |  |  |
| Tank # |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Beginning Reading Date |  |  |  |  |  |  |  | Beginning Reading Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Beginning Reading #1: |  |  |  |  | Beginning Reading #2: |  |  |  |  |  |  |  | Beginning Reading Avg. |  |  |  |  |  |  |  |  |  |  |
| Ending Reading Date |  |  |  |  |  |  |  | Ending Reading Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ending Reading #1: |  |  |  |  | Ending Reading #2: |  |  |  |  |  |  |  | Ending Reading Avg. |  |  |  |  |  |  |  |  |  |  |
| Does the variation between the beginning and ending measurements exceed the Monthly Standard? If Yes, tightness testing is required within 72 hours. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes No |  |  |  |  |
| If Required, Tightness Test Date |  |  |  |  |  |  | Attach Test Results |  |  |  |  |  |  |  |  | Pass |  |  | Fail: Release |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Fail: Leakage |  |  |  |  |
| Failed Test: Release |  | All product removed from UST within 24 hours of failed test? |  |  |  |  |  |  |  | Yes |  | No |  | Date Removed (HW Manifest attached): |  |  |  |  |  |  |  |  |  |
| Failed Test: Leakage |  | All product removed from UST within 72 hours of failed test? |  |  |  |  |  |  |  | Yes |  | No |  | Date Removed (HW Manifest attached): |  |  |  |  |  |  |  |  |  |