[image: image3.png]") Bing Maps - Mozilla Firefox - =l8lx]

Signiny  Rewards O Boston, Massachusetts Preferences

Maps
Road






Background/Introduction

In response to a request from Bruce Tebo, Project Manager, Division of Capital Asset Management (DCAM), the Massachusetts Department of Public Health (MDPH), Bureau of Environmental Health (BEH) conducted post-occupancy indoor air quality (IAQ) testing at the Department of Children and Family (DCF), 3 Ferry St, Haverhill, Massachusetts.  This evaluation was conducted as part of enhanced efforts to assess the air quality of office space leased by Massachusetts state agencies pre- and post-occupancy.  On May 10, 2011, a visit to conduct an IAQ assessment was made by Sharon Lee, an Environmental Analyst/Inspector within BEH’s IAQ Program.
The building is a two-story structure located in a strip mall in Haverhill.  Other tenants at this location include a Curves Fitness Center, a Latitude Sports Club, Papa Gino’s Pizza and an unoccupied commercial space.  The DCF originally occupied only the second floor at this location.  Following renovations, DCF now occupies a portion of a first floor space as well as the original second floor space.
Methods

Air tests for carbon monoxide, carbon dioxide, temperature and relative humidity were taken with the TSI, Q-Trak, IAQ Monitor 7565.  Air tests for airborne particle matter with a diameter less than 2.5 micrometers were taken with the TSI, DUSTTRAK™ Aerosol Monitor Model 8520.  BEH staff also performed visual inspection of building materials for water damage and/or microbial growth and other conditions that may potentially impact indoor air quality.
Results

The DCF offices have a combined employee population of approximately 135.  Tests were taken during normal operations approximately four weeks after occupancy.  Results appear in Table 1.
Discussion

Ventilation

It can be seen from Table 1 that carbon dioxide levels were below 800 parts per million (ppm) in all but six of seventy locations at the time of assessment, indicating good air exchange throughout the building.  It is important to note, however, that a number of areas were empty or sparsely populated during this visit, which can greatly reduce carbon dioxide levels.  Carbon dioxide levels would be expected to be higher with full occupancy.
Fresh air is provided by rooftop air-handling units (AHUs).  Fresh air is drawn into the AHUs through a bank of air filters, heated or cooled and delivered to occupied areas via ducted air diffusers.  Return air is drawn into an above ceiling plenum and ducted back to the rooftop AHUs through exhaust vents.  
In order to have proper ventilation with a mechanical supply and exhaust system, the systems must be balanced to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room.  It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).  It was reported that the system was balanced prior to occupancy in late February of 2011. 
The Massachusetts Building Code requires a minimum ventilation rate of 20 cubic feet per minute (cfm) per occupant of fresh outside air or openable windows (SBBRS, 1997; BOCA, 1993).  The ventilation must be on at all times that the room is occupied.  Providing adequate fresh air ventilation with open windows and maintaining the temperature in the comfort range during the cold weather season is impractical.  Mechanical ventilation is usually required to provide adequate fresh air ventilation.

Carbon dioxide is not a problem in and of itself.  It is used as an indicator of the adequacy of the fresh air ventilation.  As carbon dioxide levels rise, it indicates that the ventilating system is malfunctioning or the design occupancy of the room is being exceeded.  When this happens, a buildup of common indoor air pollutants can occur, leading to discomfort or health complaints.  The Occupational Safety and Health Administration (OSHA) standard for carbon dioxide is 5,000 parts per million parts of air (ppm).  Workers may be exposed to this level for 40 hours/week, based on a time-weighted average (OSHA, 1997).

The MDPH uses a guideline of 800 ppm for publicly occupied buildings.  A guideline of 600 ppm or less is preferred in schools due to the fact that the majority of occupants are young and considered to be a more sensitive population in the evaluation of environmental health status.  Inadequate ventilation and/or elevated temperatures are major causes of complaints such as respiratory, eye, nose and throat irritation, lethargy and headaches.  For more information concerning carbon dioxide, please see Appendix A.

Indoor temperatures ranged from 69°F to 74°F (Table 1), which were close to or within the MDPH recommended comfort range with one exception, an unoccupied conference room which had a temperature of 66°F.  The MDPH recommends that indoor air temperatures be maintained in a range of 70 oF to 78 oF in order to provide for the comfort of building occupants.  In many cases concerning indoor air quality, fluctuations of temperature in occupied spaces are typically experienced, even in a building with an adequate fresh air supply.  

Relative humidity measurements ranged from 31 to 41 percent (Table 1), which were within or slightly below the lower end of the MDPH recommended comfort range.  The MDPH recommends a comfort range of 40 to 60 percent for indoor air relative humidity.  Several building occupants expressed that the building air felt dry.  The sensation of dryness and irritation is common in a low relative humidity environment.  Low relative humidity is a very common problem during the heating season in the northeast part of the United States.
Microbial/Moisture Concerns

In order for building materials to support mold growth, a source of water exposure is necessary.  Staining and water damage was observed on the wall and floor of the men’s bathroom on the second floor (Pictures 1 and 2).  At the time of assessment, BEH staff did not detect any moisture.  A crawlspace is located next to the bathroom and, as confirmed by the building’s landlord, is the source causing damage to this space.  As reported by the landlord, a leak discovered in the crawlspace was subsequently repaired in February.  No additional leaks were reportedly observed following the repair.  

The US Environmental Protection Agency (US EPA) and the American Conference of Governmental Industrial Hygienists (ACGIH) recommends that porous materials be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2001; ACGIH, 1989).  If porous materials are not dried within this time frame, mold growth may occur.  Water-damaged porous materials cannot be adequately cleaned to remove mold growth.  The application of a mildewcide to moldy porous materials is not recommended.  
As indicated, GW was not moist at the time of assessment.  However, since it is unclear how long GW had been wet and the drying time is also unknown, measures should be taken to remove and replace damaged GW in accordance with US EPA (2001) recommendations.  Replacement of damaged wallboard will also allow for more easy identification of water damage in the future.
In a pre-occupancy memo, BEH recommended that a door sweep be installed on the exterior door of the conference room to prevent pests from entering the building.  At the time of this assessment, no door sweep was observed.  As discussed previously, rodents can penetrate a building through spaces of less than one-quarter inch.

Plants were observed in a couple of areas (Table 1).  Plants can be a source of pollen and mold which can be respiratory irritants to some individuals.  Plants should be properly maintained and equipped with drip pans and should be located away from supply vents to prevent the aerosolization of dirt, pollen and mold.  Drip pans should be examined periodically to prevent buildup of materials.
Other IAQ Evaluations
Indoor air quality can be negatively influenced by the presence of respiratory irritants, such as products of combustion.  The process of combustion produces a number of pollutants.  Common combustion emissions include carbon monoxide, carbon dioxide, water vapor, and smoke (fine airborne particle material).  Of these materials, exposure to carbon monoxide and particulate matter with a diameter of 2.5 micrometers (μm) or less (PM2.5) can produce immediate, acute health effects upon exposure.  To determine whether combustion products were present in the indoor environment, BEH staff obtained measurements for carbon monoxide and PM2.5.  

Carbon Monoxide
Carbon monoxide is a by-product of incomplete combustion of organic matter (e.g., gasoline, wood and tobacco).  Exposure to carbon monoxide can produce immediate and acute health affects.  Several air quality standards have been established to address carbon monoxide and prevent symptoms from exposure to these substances.  The MDPH established a corrective action level concerning carbon monoxide in ice skating rinks that use fossil-fueled ice resurfacing equipment.  If an operator of an indoor ice rink measures a carbon monoxide level over 30 ppm, taken 20 minutes after resurfacing within a rink, that operator must take actions to reduce carbon monoxide levels (MDPH, 1997).

The American Society of Heating Refrigeration and Air-Conditioning Engineers (ASHRAE) has adopted the National Ambient Air Quality Standards (NAAQS) as one set of criteria for assessing indoor air quality and monitoring of fresh air introduced by HVAC systems (ASHRAE, 1989).  The NAAQS are standards established by the US EPA to protect the public health from six criteria pollutants, including carbon monoxide and particulate matter (US EPA, 2006).  As recommended by ASHRAE, pollutant levels of fresh air introduced to a building should not exceed the NAAQS levels (ASHRAE, 1989).  The NAAQS were adopted by reference in the Building Officials & Code Administrators (BOCA) National Mechanical Code of 1993 (BOCA, 1993), which is now an HVAC standard included in the Massachusetts State Building Code (SBBRS, 1997).  According to the NAAQS, carbon monoxide levels in outdoor air should not exceed 9 ppm in an eight-hour average (US EPA, 2006).
Carbon monoxide should not be present in a typical, indoor environment.  If it is present, indoor carbon monoxide levels should be less than or equal to outdoor levels.  Outdoor carbon monoxide concentrations ranged was non-detectable (ND) on the day of assessment (Table 1).  No measureable levels of carbon monoxide were detected in the building (Table 1).  
Particulate Matter

The US EPA has established NAAQS limits for exposure to particulate matter.  Particulate matter is airborne solids that can be irritating to the eyes, nose and throat.  The NAAQS originally established exposure limits to particulate matter with a diameter of 10 μm or less (PM10).  According to the NAAQS, PM10 levels should not exceed 150 micrograms per cubic meter (μg/m3) in a 24-hour average (US EPA, 2006).  These standards were adopted by both ASHRAE and BOCA.  Since the issuance of the ASHRAE standard and BOCA Code, US EPA established a more protective standard for fine airborne particles.  This more stringent PM2.5 standard requires outdoor air particle levels be maintained below 35 μg/m3 over a 24-hour average (US EPA, 2006).  Although both the ASHRAE standard and BOCA Code adopted the PM10 standard for evaluating air quality, MDPH uses the more protective PM2.5 standard for evaluating airborne particulate matter concentrations in the indoor environment.

On the day of assessment, outdoor PM2.5 was measured at 5 μg/m3 (Table 1).  PM2.5 levels measured indoors ranged from 2 to 5 μg/m3 (Table 1), which were below the NAAQS PM2.5 level of 35 μg/m3.  Frequently, indoor air levels of particulates (including PM2.5) can be at higher levels than those measured outdoors.  A number of mechanical devices and/or activities that occur in buildings can generate particulate during normal operations.  Sources of indoor airborne particulates may include but are not limited to particles generated during the operation of fan belts in the HVAC system, use of stoves and/or microwave ovens in kitchen areas; use of photocopiers, fax machines and computer printing devices; operation of an ordinary vacuum cleaner and heavy foot traffic indoors.  
Other Concerns
Musty odors were observed in some of bathrooms at the DCF offices.  These bathrooms have switch-activated exhaust systems that are connected to the lights.  The lights were not on in each of the cases odors were detected.  Fans in these spaces should remain on during standard hours of operation, so either the lights should remain on or separate switches for lights and fans should be installed to ensure odors are removed.
Conclusions/Recommendations

In general, conditions in the building after build-out both before and after one month’s occupancy were adequate in terms of air exchange and temperature control.  With the exception of the men’s bathroom on the second floor, there was no other evidence of moisture problem, water damage or other potential indoor air quality concerns.  In view of the findings at the time of the visit, the following recommendations are made:

1. Install a door sweep on the exterior door of the conference room.

2. Replace/repair water-damaged wallboard and grout in the second floor men’s bathroom.  Continue to monitor for signs of damage.

3. Work with staff to identify areas of uneven heating/cooling to determine appropriate heating/cooling settings. 

4. Change filters for air-handling equipment as per the manufacturer’s instructions or more frequently if needed.  
5. For buildings in New England, periods of low relative humidity during the winter are often unavoidable.  Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low.  To control for dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended.  Avoid the use of feather dusters.  Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).

6. Consider adopting a balancing schedule of every 5 years for all mechanical ventilation systems, as recommended by ventilation industrial standards (SMACNA, 1994).

7. Ensure bathroom exhaust fans are operating during work hours.

8. Refer to resource manual and other related indoor air quality documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings.  These documents are available at: http://mass.gov/dph/iaq. 
References

ACGIH.  1989.  Guidelines for the Assessment of Bioaerosols in the Indoor Environment.  American Conference of Governmental Industrial Hygienists, Cincinnati, OH. 

ASHRAE.  1989.  Ventilation for Acceptable Indoor Air Quality.  American Society of Heating, Refrigeration and Air Conditioning Engineers.  ANSI/ASHRAE 62-1989.

BOCA.  1993.  The BOCA National Mechanical Code/1993.  8th ed.  Building Officials and Code Administrators International, Inc., Country Club Hill, IL.

MDPH.  1997.  Requirements to Maintain Air Quality in Indoor Skating Rinks (State Sanitary Code, Chapter XI).  105 CMR 675.000.  Massachusetts Department of Public Health, Boston, MA.

OSHA.  1997.  Limits for Air Contaminants.  Occupational Safety and Health Administration.  Code of Federal Regulations.  29 C.F.R 1910.1000 Table Z-1-A.

SBBRS.  1997.  Mechanical Ventilation.  State Board of Building Regulations and Standards.  Code of Massachusetts Regulations.  780 CMR 1209.0

SMACNA.  1994.  HVAC Systems Commissioning Manual.  1st ed.  Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA. 
US EPA.  2001.  Mold Remediation in Schools and Commercial Buildings. US Environmental Protection Agency, Office of Air and Radiation, Indoor Environments Division, Washington, D.C.  EPA 402-K-01-001.  March 2001.

US EPA.  2006.  National Ambient Air Quality Standards (NAAQS).  US Environmental Protection Agency, Office of Air Quality Planning and Standards, Washington, DC.  http://www.epa.gov/air/criteria.html.

Picture 1

[image: image1.jpg]



Stained grout and visible water damage to wall/paint

Picture 2

[image: image2.jpg]



Water-damaged wall/paint

	Location
	Carbon

Dioxide

(ppm)
	Carbon Monoxide

(ppm)
	Temp

(°F)
	Relative

Humidity

(%)
	PM2.5

(µg/m3)
	Occupants

in Room
	Windows

Openable
	Ventilation
	Remarks

	
	
	
	
	
	
	
	
	Supply
	Exhaust
	

	Background
	509
	ND
	60
	44
	5
	
	
	
	
	Overcast

	2nd Floor
	
	
	
	
	
	
	
	
	
	

	ATTY
	728
	ND
	73
	32
	3
	0
	N
	Y
	Y
	

	LEAD
	682
	ND
	74
	32
	4
	1
	N
	Y
	Y
	

	PACT
	751
	ND
	74
	32
	3
	2
	N
	Y
	Y
	

	PAYA
	751
	ND
	73
	32
	3
	0
	N
	Y
	Y
	

	PC-RSRC Mgr
	731
	ND
	74
	32
	3
	0
	Y
	Y
	Y
	

	Reception
	812
	ND
	72
	35
	3
	3
	Y
	Y
	Y
	

	Waiting room
	620
	ND
	72
	34
	3
	2
	
	Y
	Y
	

	2nd floor breakroom
	1051
	ND
	71
	41
	3
	0
	
	Y
	Y
	

	2nd floor copy room
	748
	ND
	73
	34
	5
	2
	N
	Y
	N
	PC

	2nd floor women’s room
	709
	ND
	74
	33
	3
	0
	N
	Y
	Y
	

	2nd floor men’s room
	872
	ND
	74
	33
	5
	0
	N
	Y
	Y
	WD-walls; GW dry; damaged floor grout

	12 (waiting room bathroom)
	595
	ND
	70
	36
	4
	0
	N
	Y
	Y
	DO

	14
	611
	ND
	72
	34
	3
	2
	N
	Y
	Y
	DO

	16
	595
	ND
	71
	34
	3
	0
	N
	Y
	Y
	DO

	18
	590
	ND
	71
	34
	3
	0
	N
	Y
	Y
	DO

	20
	592
	ND
	70
	36
	3
	0
	N
	Y
	Y
	DO

	21
	577
	ND
	69
	35
	3
	0
	N
	Y
	Y
	DO

	22
	561
	ND
	69
	35
	3
	0
	N
	Y
	Y
	DO

	28
	642
	ND
	71
	34
	3
	0
	N
	Y
	Y
	DO

	34 (MDF room)
	720
	ND
	70
	33
	2
	0
	N
	N
	N
	Wall AC

	35
	792
	ND
	74
	32
	4
	0
	N
	Y
	Y
	DO

	36
	706
	ND
	74
	31
	3
	0
	N
	Y
	Y
	DO

	38
	748
	ND
	74
	31
	3
	0
	N
	Y
	Y
	DO

	39
	771
	ND
	75
	31
	3
	2
	N
	Y
	Y
	DO

	40
	790
	ND
	74
	32
	3
	1
	N
	Y
	Y
	

	41
	797
	ND
	74
	32
	4
	1
	N
	Y
	Y
	

	45
	722
	ND
	74
	32
	3
	0
	N
	Y
	Y
	DO

	47
	765
	ND
	74
	33
	4
	0
	N
	Y
	Y
	DO

	47
	774
	ND
	74
	33
	4
	0
	N
	Y
	N
	

	48
	814
	ND
	74
	32
	4
	2
	N
	Y
	Y
	

	49
	802
	ND
	74
	32
	4
	1
	N
	Y
	Y
	DO

	51
	671
	ND
	71
	35
	3
	0
	N
	Y
	N
	DO

	52
	721
	ND
	71
	36
	3
	1
	N
	Y
	N
	DO

	53
	671
	ND
	71
	36
	4
	3
	N
	Y
	Y
	DO

	56
	718
	ND
	73
	32
	3
	0
	Y
	Y
	N
	DO

	57
	744
	ND
	74
	32
	3
	0
	Y
	Y
	N
	DO

	58
	721
	ND
	74
	31
	3
	0
	Y
	Y
	N
	DO, plants

	59
	734
	ND
	74
	31
	3
	0
	Y
	Y
	N
	DO

	201
	737
	ND
	73
	33
	3
	1
	Y
	Y
	Y
	

	202
	737
	ND
	73
	33
	4
	1
	Y
	Y
	Y
	

	203
	713
	ND
	74
	32
	3
	0
	N
	Y
	Y
	

	204
	689
	ND
	73
	32
	3
	0
	N
	Y
	Y
	

	205
	757
	ND
	74
	32
	4
	0
	N
	Y
	Y
	

	206
	787
	ND
	74
	32
	5
	3
	N
	Y
	Y
	

	208
	769
	ND
	74
	32
	4
	1
	Y
	Y
	Y
	

	1st Floor
	
	
	
	
	
	
	
	
	
	

	Conference room
	633
	ND
	71
	34
	4
	1
	N
	Y
	Y
	No door sweep on exterior door

	Gally kitchen
	621
	ND
	72
	33
	4
	0
	N
	Y
	Y
	

	Hallway
	669
	ND
	72
	34
	5
	0
	N
	N
	N
	

	PC-coach
	640
	ND
	71
	34
	4
	1
	N
	Y
	Y
	

	Stairwell
	815
	ND
	71
	35
	5
	0
	N
	N
	N
	

	1st Floor Women’s Single Bathroom
	
	ND
	73
	33
	4
	0
	N
	Y
	Y
	Switch activated exhaust, musty

	1st Floor Men’s Single Bathroom
	
	ND
	73
	33
	4
	0
	N
	Y
	Y
	

	1st floor Men’s  Room
	626
	ND
	72
	35
	4
	0
	N
	Y
	Y
	

	1st floor Women’s Room
	624
	ND
	72
	33
	4
	0
	N
	Y
	Y
	

	62
	640
	ND
	73
	33
	4
	1
	N
	Y
	N
	DO

	63
	677
	ND
	72
	33
	4
	0
	N
	Y
	N
	

	69
	664
	ND
	73
	33
	4
	0
	N
	Y
	N
	

	70
	677
	ND
	71
	35
	4
	1
	N
	Y
	N
	DO

	72
	623
	ND
	73
	33
	4
	0
	N
	Y
	N
	Plants

	73
	672
	ND
	72
	34
	4
	3
	N
	Y
	Y
	

	74
	615
	ND
	72
	34
	4
	0
	N
	Y
	N
	

	75
	612
	ND
	71
	34
	4
	0
	N
	Y
	N
	DO

	80
	612
	ND
	71
	34
	4
	1
	N
	Y
	N
	DO

	81
	603
	ND
	71
	34
	4
	0
	N
	Y
	N
	

	82
	593
	ND
	72
	33
	4
	0
	N
	Y
	N
	

	109
	631
	ND
	73
	32
	4
	3
	N
	Y
	N
	

	110
	625
	ND
	73
	33
	4
	1
	N
	Y
	Y
	

	111
	626
	ND
	72
	34
	4
	2
	N
	Y
	Y
	

	112
	622
	ND
	71
	34
	4
	1
	N
	Y
	Y
	

	113
	617
	ND
	71
	34
	4
	1
	N
	Y
	Y
	

	114
	619
	ND
	72
	34
	4
	3
	N
	Y
	Y
	Plants

	115
	622
	ND
	71
	34
	5
	0
	N
	Y
	y
	

















INDOOR AIR QUALITY


POST-OCCUPANCY ASSESSMENT








Massachusetts Department of Children and Family


3 Ferry St


Haverhill, MA 01835




















�























Prepared by:


Massachusetts Department of Public Health


Bureau of Environmental Health


Indoor Air Quality Program


September 2011











8
11

