# Draft for Public Hearing and Comment

# Draft

# Prevention of Significant Deterioration (PSD) Fact Sheet

# Issued by MassDEP on April 20, 2016

MATEP Limited Partnership

Medical Area Total Energy Plant

474 Brookline Avenue

Boston, MA 02215

# Transmittal No. X259947

Application No. NE-14-013

TABLE OF CONTENTS

- General Information									3

- Project Location									4

- Proposed Project									4

- PSD Program Applicability and Review						6

- PSD Applicability									7

- BACT Analysis									9

- Monitoring and Testing								15

- Impact Analysis Based on Modeling						15

- Mass Based Emission Limits							21

- Environmental Justice								21

- National Historic Preservation Act, Endangered Species Act,

Tribal Consultation									24

- Comment Period, Hearings and Procedures for Final Decision			25

- MassDEP Contacts									26

I.	General Information

Name of Source:	Medical Area Total Energy Plant - Combined Heat and Power Facility Upgrade Project

Location:				Boston, Massachusetts

Applicant’s Name and Address:	MATEP Limited Partnership (MATEP LP)

474 Brookline Avenue

Boston, MA 02215

Application Prepared By:		Epsilon Associates, Inc.

3 Clock Tower Place, Suite 250

Maynard, MA 01754

# Draft Prevention of Significant

Deterioration/Major Comprehensive

Plan Application

# Transmittal Number:		X259947

Application Number:		NE-14-013

# Massachusetts Department of

Environmental Protection (MassDEP)

# MassDEP Contact:			Edward J. Braczyk

MassDEP Northeast Regional Office

205B Lowell Street

Wilmington, MA 01887

(978) 694-3200

Edward.Braczyk@state.ma.us

On August 26, 2014, MATEP Limited Partnership (MATEP LP or Applicant or Permittee) submitted an initial Application to MassDEP requesting a Prevention of Significant Deterioration (PSD) Permit and a 310 Code of Massachusetts Regulations (CMR) 7.02 Major Comprehensive Plan Application Approval (Plan Approval) for a new 14.4 megawatt (MW) combined heat and power (CHP) unit (Project), which will combust natural gas as a primary fuel and ultra low sulfur diesel (ULSD) as a back-up fuel, designated CTG-3/HRSG-3000. This unit will be located at the existing Medical Area Total Energy Plant (MATEP or Facility), 474 Brookline Avenue in Boston Massachusetts. On September 11, 2015, MassDEP issued a Technical Deficiency Letter upon completing a preliminary review of MATEP LP’s major Comprehensive Plan Application. On October 1, 2015, MATEP submitted additional information to address the deficient items that are outlined in the technical deficiency letter. Beginning on November 3, 2015 and on various subsequent dates, the Applicant submitted letters with supplemental technical information addressing the technical deficiency letter including start-up and shutdown values for PM2.5, while firing natural gas and ULSD, and the use of clean fuels. These submittals constitute amendments to the Application, and MassDEP is treating them as such.

Based on all submittals, MassDEP has concluded that the Permittee’s PSD Application is complete and provides the necessary information showing that the Project meets federal PSD regulations. The Permittee’s supplemental technical Project information is part of the official record for this Fact Sheet and PSD Permit. After reviewing the August 26, 2014 Application and all of the additional information, MassDEP prepared this Fact Sheet and Draft PSD Permit and issues these documents for a 30 day public comment period as required by the PSD Delegation Agreement and 40 CFR Part 124 – Procedures for Decision Making.

The Project is also subject to the MassDEP Plan Approval and Emission Limitations requirements under 310 CMR 7.02. MassDEP is concurrently issuing the Proposed Plan Approval and the Draft PSD Permit. The Proposed Plan Approval regulates all pollutants emitted by the Project, including those Criteria Pollutants that triggered PSD review and are regulated under the PSD Permit. MATEP LP must ensure that its Project complies with the federal PSD Permit and MassDEP’s Plan Approval, as well as other applicable federal and state requirements.

II.	Project Location

The Project is located in an urban area at 474 Brookline Avenue in Boston, Massachusetts, where the existing MATEP Combined Heat and Power Plant is operating to generate electricity and steam for the medical area facilities such as the Dana-Farber Cancer Institute, Joslin Diabetes Center, and Boston Children’s Hospital. The Project location is classified as either “attainment” or “unclassifiable” with respect to the National Ambient Air Quality Standards (NAAQS) for sulfur dioxide (SO2), nitrogen dioxide (NO2), carbon monoxide (CO), particulate matter with diameters less than 10 microns (PM10) and 2.5 microns (PM2.5) and lead. Therefore, the Project may be subject to PSD review for these pollutants.

III.	Proposed Project

# MATEP LP currently operates two combustion turbine generators with HRSGs (CHP units). The project consists of a third CHP unit, a 14.4 MW electric power output-rated Solar Titan 130 combustion turbine generator (CTG-3), with natural gas primary and ultra low sulfur diesel (ULSD) backup fuel. Combustion turbine exhaust gases will pass through a heat recovery steam generator (HRSG-300) equipped with a natural gas fired duct burner rated at 38.8 million Btu per hour (mmBtu/hr) maximum fuel input rate. The combustion turbine will feature a Dry Low NOx (DLN) combustor for natural gas and ULSD. The HRSG exhaust will be equipped with a selective catalytic reduction (SCR) system and an oxidation catalyst for post-combustion control of NOx and CO, respectively. CTG-3/HRSG-300 will be housed entirely within the existing Facility.

MATEP LP has requested, based upon a review of Best Available Control Technology (BACT) for Clean Fuels, that the proposed turbine be permitted for year-round operation on natural gas with ultra low sulfur distillate (ULSD) to be used as a backup fuel for up to 720 hours per 12-month rolling period, when natural gas is not available or as stipulated in the Special Conditions section of the PSD Permit.

The Facility currently houses several heat and power generating emission units identified in Table 1 below:

| Table 1. Existing Emission Units at Facility |
| --- |
| EU# | Description of EU | EU Design Capacity |
| PSG-1 | Victory Energy Type O Boiler | 214 mmBtu/hr (gas) 205 mmBtu/hr (oil) |
| PSG-2 | Riley Boiler No. 2 | 244 mmBtu/hr |
| PSG-3 | Riley Boiler No. 3 | 244 mmBtu/hr |
| Zurn-1 | Zurn Afterburner and HRSG No. 1 | 225 mmBtu/hr |
| Zurn-2 | Zurn Afterburner and HRSG No. 2 | 225 mmBtu/hr |
| DEG-1 | Mirrlees Diesel Engine Generator No. 1 | 63.8 mmBtu/hr |
| DEG-2 | Mirrlees Diesel Engine Generator No. 2 | 63.8 mmBtu/hr |
| DEG-3 | Mirrlees Diesel Engine Generator No. 3 | 63.8 mmBtu/hr |
| DEG-4 | Mirrlees Diesel Engine Generator No. 4 | 63.8 mmBtu/hr |
| DEG-5 | Mirrlees Diesel Engine Generator No. 5 | 63.8 mmBtu/hr |
| DEG-6 | Mirrlees Diesel Engine Generator No. 6 | 63.8 mmBtu/hr |
| CTG-1 | Alstom Gas Combustion Turbine No. 1 | 152.6 mmBtu/hr |
| CTG-2 | Alstom Gas Combustion Turbine No. 2 | 152.6 mmBtu/hr |
| HRSG-100 | ERI HRSG No. 1 serving CTG-1 | 75 mmBtu/hr |
| HRSG-200 | ERI HRSG No. 2 serving CTG-2 | 75 mmBtu/hr |
| EDG-1 | 210 KW Emergency Diesel Generator | 2.94 mmBtu/hr |
| EDG-2 | 410 KW Emergency Diesel Generator | 5.47 mmBtu/hr |

# Table 1 Key:

# EU = emission unit

HRSG= heat recovery steam generator

DEG = diesel engine generator

CTG = combustion turbine generator

EDG = emergency diesel generator

PSG = pressure steam generator

mmBtu/hr = million Btu per hour

KW = kilowatt

No. = number

IV.	PSD Program Applicability and Review

MassDEP administers the PSD program in accordance with the provisions of the April 11, 2011 PSD Delegation Agreement between MassDEP and EPA which states that MassDEP agrees to implement and enforce the federal PSD regulations as found in 40 CFR 52.21 and 40 CFR Part 124 regarding permit issuance, modification and appeals.

The PSD regulations at 40 CFR 52.21 require that a major new stationary source of a regulated New Source Review (NSR) pollutant, or a major modification with respect to a regulated NSR pollutant, undergo a PSD review and that a PSD Permit be granted before commencement of construction, except with respect to a project located in a nonattainment area for the particular pollutant.

40 CFR 52.21(b)(1) of the federal PSD regulations defines a “major stationary source” as either (a) any of 28 designated stationary source categories with potential emissions of 100 tons per year (tpy) or more of any regulated NSR pollutant, or (b) any other stationary source with potential emissions of 250 tpy or more of any regulated NSR pollutant. MATEP is an existing major stationary source as defined by source category and emission thresholds.

In addition, a project at an existing major stationary source is subject to PSD review if the project would result in a significant emissions increase and a significant net emissions increase of a regulated NSR pollutant.

The Project will result in a significant emissions increase and a significant net emissions increase for PM10 and PM2.5.  Therefore, the project is subject to PSD review as a major modification.

If a project is subject to the PSD program, the owner or operator must apply for and obtain a PSD Permit that meets regulatory requirements including:

- Best Available Control Technology (BACT) requiring sources to minimize emissions to the greatest extent practical;

- An ambient air quality analysis to ensure that the emission increases do not cause or contribute to a violation of any applicable PSD increments or NAAQS;

- An additional impact analysis to determine direct and indirect effects of the proposed source on industrial growth in the area, soil, vegetation and visibility; and

- Public comment including an opportunity for a public hearing.

Since potential greenhouse gas (GHG) emissions from the project will exceed 75,000 tpy, GHG emissions must also be included in the determination of Best Available Control Technology (BACT).

V.	PSD Applicability

The existing facility includes fossil-fuel boilers totaling more than 250 million Btu per hour heat input and has potential emissions of CO, NOx and SO2 each greater than 100 tons per year.  Therefore, it is considered a major stationary source, as defined pursuant to 40 CFR Part 52, section 52.21(b)(1).

The Project is a major modification as defined pursuant to 40 CFR Part 52, section 52.21(b)(2).  Potential emissions from the proposed CHP equipment are significant for three different PSD pollutants: PM10, PM2.5 and GHG.  Table 2 shows potential emissions from the proposed new equipment at the site relative to the PSD significance thresholds.

The emissions from the Project are compared to the PSD thresholds in Table 2 below:

| Table 2 Project Potential to Emit |
| --- |
| Pollutant | Project Potential to Emit (in tpy) | PSD Significant Emission Rate (in tpy) | PSD Review Applies? |
| NOx | 7.79 | 40 | No |
| CO | 5.84 | 100 | No |
| VOC | 2.5 | 40 | No |
| PM | 18.8 | 25 | No |
| PM10 | 18.81 | 15 | Yes3 |
| PM2.5 | 18.81 | 10 | Yes3 |
| SO2 | 2.56 | 40 | No |
| GHG as CO2e2 | 108,500 | 75,000 | Yes3 |
| Lead | 0.1 | 0.6 | No |
| Fluorides | Negligible | 3 | No |
| Sulfuric Acid Mist | 2.55 | 7 | No |
| Hydrogen Sulfide | None expected | 10 | No |
| Total reduced sulfur | None expected | 10 | No |
| Reduced sulfur compounds | None expected | 10 | No |

Table 2 Notes:

1The projected annual emissions of PM10 and PM2.5 have been calculated based on worst case conditions. The worst case assumption for projected annual emissions for PM2.5 is that all particulate matter emitted is PM2.5. The worst case assumption for projected annual emissions for PM10 is that all particulate matter emitted is PM10.

2GHG emissions are expressed in terms of CO2 equivalent emissions (CO2e).

3 The proposed project exceeds the PSD significance thresholds for PM10, PM2.5.and GHG as CO2e. As such, the PSD permit will address these pollutants.

# Table 2 Key:

# CT = Combustion Turbine

tpy = tons per year

NOx = Nitrogen Oxides

CO = Carbon Monoxide

VOC = Volatile Organic Compounds

SO2 = Sulfur Dioxide

PM10 = Particulate Matter less than or equal to 10 microns in diameter

PM2.5 = Particulate Matter less than or equal to 2.5 microns in diameter

H2SO4 = Sulfuric Acid

Pb = Lead

GHG = Greenhouse Gases

CO2e = Greenhouse Gases expressed as Carbon Dioxide equivalent and calculated by multiplying each of the six greenhouse gases (Carbon Dioxide, Nitrous Oxide, methane, Hydrofluorocarbons, Perfluorocarbons, Sulfur Hexafluoride) mass amount of emissions, in tons per year, by the gas’s associated global warming potential published at Table A-1 of 40 CFR Part 98, Subpart A and summing the six resultant values.

VI.	BACT Analysis

As required pursuant to 40 CF R 52.21(j) (3), the Project is required to comply with BACT for the PM10, PM2.5 and GHG emissions from the new turbine and duct burner.

BACT is defined as, “an emissions limitation ... based on the maximum degree of reduction for each pollutant subject to regulation under [the Clean Air] Act which would be emitted from any proposed major stationary source or major modification which the Administrator, on a case-by-case basis, taking into account energy, environmental, and economic impacts and other costs, determines is achievable for such source or modification through application of production processes or available methods, systems and techniques … for control of such pollutant.” 40 CFR 52.21(b)(12); Clean Air Act (CAA) 169(3).

BACT determinations under PSD review must follow the following five step “top-down” methodology as outlined in several EPA policy memoranda.

- Identify all control technologies. Identify all possible control options, including inherently lower emitting processes and practices, add-on control equipment, or combination of inherently lower emitting processes and practices and add-on control equipment.

- Eliminate technically infeasible options. Eliminate technically infeasible options based on physical, chemical and engineering principles.

- Rank remaining control technologies by control effectiveness. Rank the remaining control options by control effectiveness, expected emission reduction energy impacts, environmental impacts, and economic impacts.

- Evaluate most effective controls and document results. Determine the economic, energy and environmental impacts of the control technology on a case-by-case basis.

- Select the BACT. Select the most effective option not rejected as the BACT.

The results of the BACT analyses for the proposed Project are presented below for PM10, PM2.5 and GHG emissions.

# Combustion Turbine and Duct Burner

# Clean Fuels

For the project, a major element of the BACT analysis is the use of clean fuels. This Fact Sheet discusses the BACT analysis for fuels here, rather than repeating it for each individual emissions unit and pollutant. MATEP LP has proposed to burn natural gas and ULSD in the combustion turbine, and combust natural gas only in the duct burner. ULSD will be used for a maximum of 720 hours per 12-month rolling period, only when natural gas is unavailable or as stipulated in the Special Conditions section of the PSD Permit.

# Step 1: Identify all control technologies.

Since this section is focusing on fuels, the identified control technologies are:

- Use of natural gas only; and

- Use of natural gas as primary fuel with ULSD as a backup fuel (limited to 720 hours per 12-month rolling period, which is equivalent to 878,400 gallons ULSD).

# Step 2: Eliminate technically infeasible options.

The use of natural gas as the only fuel is not technically feasible. The Project has no direct connections to major regional natural gas pipelines and will be supplied by National Grid via Boston-area distribution points supplied by the Algonquin pipeline network. The Algonquin pipeline network has experienced physical delivery constraints in recent years during peak demand periods.

MATEP LP has a firm gas transportation contract with National Grid. National Grid places restrictions on the amount of natural gas that can be delivered on days when the heating degree day (HDD) is forecast to be greater than or equal to 50 in accordance with their tariff. During the winter of 2014-15, temperature data from Logan airport (Boston) weather station indicates an HDD of 50 or above occurred on 8 days.

During anticipated or actual high demand periods or as a result of other delievery constrainsts, operational flow orders (OFOs) may be issued on critical days for the Algonquin pipeline network that  impose economic penalties for exceeding certain usage tolerances.

The Facility and Project will also be periodically affected by planned and unplanned gas compressor maintenance outages that will physically prevent the turbine from combusting natural gas. These outages have an estimated duration and frequency of one (1) hour per month.

# Step 3: Rank remaining control technologies by control effectiveness.

With respect to pollutant emissions, natural gas is the cleanest fuel identified. ULSD has higher emissions than natural gas, but their emissions profile are similar.

Natural gas is a cleaner fuel than ULSD; it therefore ranks higher in control effectiveness. The BACT process requires the reviewing authority to consider energy impacts, environmental, and economic impacts of natural gas to the use of ULSD.

# Step 4: Evaluate most effective controls and document results.

Energy Impacts – Availability of natural gas may be affected by the type of natural gas service, firm or non-interruptible service or the less expensive, interruptible natural gas service. On some infrequent natural gas distribution bottleneck days, natural gas cannot be purchased at any price.

Economic Impacts – Under certain market condition, even when natural gas is available, it may still be more expensive than ULSD. This can be attributed to whether a Facility/Project uses an interruptible or firm natural gas contract, or if there is a shortage of natural gas. The price of firm natural gas will always be high but is always available, but interruptible natural gas will always be lower than a firm gas contract, except on the rare occasion when the spot market natural price could exceed the firm gas price. This price discrepancy would however occur only on those rare days when natural gas deliveries are affected or gas supplies are limited.

Environmental Impacts – The expected PM10 and PM2.5 emission rate when burning ULSD is approximately 73 percent higher than combusting natural gas. Similarly, Greenhouse Gas (CO2e) emissions are also increased when combusting ULSD. The emissions data clearly illustrate that natural gas is the cleanest fuel.

# Step 5: Select BACT.

MassDEP is proposing to allow MATEP LP to combust ULSD as a backup fuel, but only under specifically defined circumstances that constrain its usage to those situations where not allowing ULSD firing would impair the Project’s ability to operate. These situations include:

a. natural gas curtailment by the natural gas supplier or distributor;

b. instructed/mandated by the system operator, ISO-New England;

c. conducting emissions testing; or

d. conducting required equipment maintenance and testing.

The total number of hours of firing ULSD cannot exceed 720 hours per rolling 12-month period, equivalent to 878,400 gallons of ULSD. These fuel use limits are provided in Table 6, Special Terms and Conditions, of the PSD Permit.

# PM10/PM2.5

Emissions of particulate matter result from trace quantities of ash (non-combustibles) in the fuel as well as from the products of incomplete combustion. The two main technologies/strategies to control and/or limit the emission of particulate matter from the Project are post-combustion controls and the use of clean fuels and good combustion control. MATEP LP reviewed the EPA RACT/BACT/LAER Clearinghouse and other on-line data sources including LAER determinations. The BACT analysis performed in section 5.2 of the MATEP LP’s PSD Application demonstrates the technical infeasibility of post-combustion controls. As such, MATEP LP proposes to minimize particulate matter emissions from the proposed combustion turbine addition through the use of clean fuels and clean combustion. The BACT analysis and Supplemental BACT – Technical Deficiency Response (October 1, 2015) provides a summary of the effectiveness of clean fuels and combustion including economic, environmental, and energy impacts.

Natural gas will be used as the primary fuel for the turbine as it is the lowest ash-content fuel available. However, due to the critical nature of the Facility to supply electricity, steam, heat and chilled water to primary care medical facilities in the Longwood Medical Area, Ultra Low Sulfur Diesel (ULSD) is required as an alternative fuel. MATEP LP will limit the use of ULSD fuel to a usage equivalent of 720 hours of full-load ULSD operation (878,400 gallons of ULSD per 12-month rolling period). MATEP LP conservatively presumes that all particulate matter (PM) emissions from the new combustion turbine addition will be less than 2.5 microns in diameter (PM2.5). MATEP proposes a BACT emission limit for PM10, and PM2.5 of 0.02 pounds per million British thermal unit (lb/mmBtu) when firing natural gas and 0.034 lb/mmBtu when firing ULSD. These proposed emission limits represent the maximum degree of reduction that is achievable, taking into account the scarcity of comparable units with emission limits that are demonstrated in practice and the limited technical opportunities to directly control and reduce particulate emissions.

MATEP LP’s BACT analysis identifies 10 facilities that are similar to the proposed combustion turbine addition (turbines firing natural gas or distillate oil, operating in combined-cycle or CHP mode, sized smaller than 25 MW with facilities that only have filterable particulate matter limits being excluded). The limits that MATEP LP proposes for this new combustion turbine addition, stated above, are comparable or slightly lower than recent projects of similar size such as Cornell, UMass Amherst, Gillette, and Harvard.

Natural gas will be the only fuel utilized for the duct burner as it is the lowest ash-content fuel available. Consistent with the PM10 and PM2.5 BACT review conducted for the combustion turbine, post combustion control technology is not feasible. MATEP LP presumes that all particulate matter emitted from the duct burner will be less than 2.5 microns in diameter (PM2.5). MATEP LP proposes a BACT emission limit for PM10, and PM2.5 of 0.02 pounds per million British thermal unit (lb/mmBtu) firing natural gas. The emission limit that MATEP LP proses for the duct burner is consistent with the emission limits established as BACT for similar size duct burner projects.

# Greenhouse Gas Emissions (GHG)

For PSD permitting from combustion sources, GHGs are the aggregate of three pollutants: carbon dioxide (CO2), methane (CH4), and nitrous oxide (N2O).  Since each pollutant has a different effect on global warming, PSD applicability is based on a carbon dioxide equivalent (CO2e), determined by multiplying each pollutant by its global warming potential. Like other combustion sources, the main constituent of GHG for a combined cycle turbine is carbon dioxide.  The N2O will be controlled as NOx by the SCR and the CH4 will be controlled by good combustion practices. This BACT analysis focuses on CO2 emissions as the primary GHG component. Emissions calculations are as CO2–equivalent, or CO2e.

For natural gas combustion, the calculated CO2e emission factor used is 119 lb/mmBtu. This emission factor is based on a CO2 emission factor of 118.9 lb/mmBtu calculated from Equation G-4 of 40 CFR Part 75 Appendix G plus an emission factor of 0.1 lb/mmBtu for other greenhouse gases (methane and nitrous oxide) calculated utilizing the emission factors for these two pollutants from Table C-2 of 40 CFR Part 98 Subpart C and the global warming potentials for these two pollutants from Table A-1 of 40 CFR Part 98 Subpart A.

For fuel oil combustion, the calculated CO2e emission factor used is 166 lb/mmBtu. The CO2e emission factor for fuel oil is calculated utilizing the emission factors for CO2, methane and nitrous oxide from Table C-2 of 40 CFR Part 98 Subpart C and the global warming potentials for methane and nitrous oxide found in Table A-1 of 40 CFR Part 98 Subpart A. Using Part 75 methodology would yield a slightly less conservative emission factor than Part 98.

The most stringent control technology for control of GHG from a combustion turbine combined cycle unit is by means of carbon capture sequestration (CCS). MATEP evaluated the technical feasibility of CCS based upon the following four steps. The first step is the capture or removal of carbon (i.e., CO2) from the exhaust gas. The capture system requires the use of an absorption system, which requires the use of ammonia, monoethanolamine, or other amine solution. The use of these chemicals in an urban setting is prohibitive. In addition, the required size of this adsorption system prohibits it use in the limited area of MATEP LP’s Facility. The second step of CCS is the compression of the CO2. The third step is the transport of the captured CO2 to a suitable disposal site. The fourth step is the actual disposal of CO2, normally deep underground in geological formations such as coal seams and oil and gas explorations. MATEP LP pointed out that since most or all steps in the CCS are not technically feasible to the Project, CCS is not technically feasible. MassDEP agrees that CCS is not feasible at this site.

MATEP LP has proposed to use a combination of approaches to achieve BACT for GHG including all of the following elements.

- MATEP LP proposes to use natural gas as the primary fuel of use, the lowest carbon emitting fuel for a fossil fuel project and ULSD, as a backup fuel for a maximum of 720 hours per rolling 12-month period.

- MATEP LP has chosen to install a Solar Titan 130 combustion gas turbine, which has a highly energy efficient heat rate of 10,230 kilojoules per kilowatt-hour (kJ/kWh). This heat rate closely matches the most energy efficient turbines available, where the heat rate ranges from 10,230 to 11,465 kJ/kWh, where the lower the heat rate means a higher efficiency turbine. The thermal efficiency of the proposed heat recovery steam generator (HRSG) is significantly higher than for similarly sized stand-alone boiler. MATEP LP expects a 95 percent thermal efficiency in the final design: MATEP LP plans to minimize parasitic loads such as support equipment necessary for overall plant operation.

- MATEP LP proposes to implement energy efficiency improvements to the Facility’s operations, including replacing the existing water treatment system pump motors with variable frequency drives (VFDs), replacing two cooling tower fan motors with VFDs and converting a large constant volume ventilation exhaust fan serving the plant’s diesel engine bay to variable air volume.

# Startup and Shutdown Emissions

Startup and shutdown emissions were evaluated for PM emissions. MATEP LP proposes to comply with BACT for startup and shutdown by employing good operating practices (by following the combustion turbine manufacturer’s recommendations during startup and by limiting startup time.

The proposed startup and shutdown emission limits for PM10/PM2.5 are subject to PSD review as presented in Table 3.

| Table 3 Turbine Startup and Shutdown Emission Limits (pounds per event) |
| --- |
| Pollutant | Fuel | Startup (duration 3 hours) | Shutdown (duration 1 hour) |
| PM10/PM2.5 | Natural gas | 12.3 | 4.1 |
|  | ULSD | 21.3 | 7.1 |

VII.	Monitoring and Testing

MATEP LP will be performing an initial emissions test to measure PM2.5 and PM10 emissions in the flue gas from the turbine and heat recovery steam generator. The emissions testing program shall generate PM data in accordance with the EPA Reference Test Methods of 40 CFR Part 60 Appendix A and 40 CFR Part 51 Appendix M. This data can be directly compared to the permit emission limits to determine compliance.

MATEP LP is required to monitor and keep records of the amount of sulfur in the natural gas that is combusted in the combined cycle turbines pursuant to New Source Performance Standards

40 CFR Part 60 Subpart KKKK.

MATEP LP is required to conduct emissions tests for PM10, PM2.5 and CO2 emissions within 180 days of initial firing and continuous operation of the turbine and heat recovery steam generator.

VIII.	Impact Analysis Based on Modeling

As part of its Application, MATEP LP submitted a dispersion modeling analysis that met the requirements of 40 CFR Part 51, Appendix W.

MATEP LP’s consultant (Epsilon) conducted a refined dispersion modeling analysis to determine impact concentrations at receptors located along the Facility property line and beyond.  The refined analysis was based on proposed worst case facility emission rates and 5 years (2009-2013) of meteorological conditions.  The analysis was conducted in accordance with EPA’s “Guideline on Air Quality Models” (November 2005) and Guidance for PM2.5 Permit Modeling (May 2014), as well as MassDEP’s “Modeling Guidance for Significant Stationary Sources of Air Pollution” (June 2011) and as described in the Air Quality Modeling Protocol submitted to MassDEP on August 26, 2014.  The EPA-recommended AERMOD model (current at the time AERMOD version 14134, AERMAP version 11103, AERMET version 14134) was used to perform the dispersion modeling.

The meteorological data was collected at the Boston Logan Airport National Weather Service (NWS) Automated Surface Observing System (ASOS) station, which is the closest first order NWS station to MATEP.  It is located approximately 5.3 miles to the east-northeast of MATEP.  The station is representative of the Project area since they are both located in the city of Boston and exposed to the same weather systems and conditions such as urban heat island effects and coastal air-land-sea interactions.  Therefore, MATEP LP was not required to perform one year of on-site monitoring of meteorological conditions before conducting dispersion modeling. Default processing options were used in the AERMET processing for this analysis. The preferred ASOS 1-minute wind data was used in the processing to reduce the number of calm hours input to the model.

The dispersion modeling results for the Project are provided in Table 4 along with the corresponding Significant Impact Levels (SILs) established by EPA.  According to EPA guidance, compliance with the NAAQS and PSD Increments is demonstrated for all pollutants and averaging periods for which impacts are below the SILs.

| Table 4 Project Maximum Predicted Impact Concentrations Compared to Significant Impact Levels (micrograms/cubic meter) |
| --- |
| Pollutant | Averaging Period | Maximum Predicted MATEP Turbine Project Impact | SIL |
| PM10 | 24-Hour | 1.092 | 5 |
| PM2.5 | 24-Hour | 0.829 | 1.2 |
|  | Annual | 0.060 | 0.3 |

The modeling results in the table show maximum predicted impact concentrations are below the SILs for the two pollutants modeled. Therefore, the required dispersion modeling demonstrates compliance with 24-hour and annual PM2.5 and 24-hour PM10 NAAQS.  In addition, compliance with PSD Increments is also demonstrated for these pollutants.

# Preconstruction Monitoring Analysis

Ambient background monitoring data from MassDEP’s Boston Kenmore Square monitoring site for the three (3) year period of 2010 through 2012 were used to characterize criteria pollutant ambient air impacts. PSD regulations allow proposed sources to use existing monitoring data in lieu of PSD preconstruction monitoring requirements for a pollutant if the source can demonstrate that its ambient air impact is less than a de minimis amount (also called a significant monitoring concentration or SMC) as specified in those regulations. As shown in Table 5 below, dispersion modeling conducted by MATEP LP predicted maximum Project impact concentrations well below corresponding SMC levels for all pollutants for which SMCs exist.

| Table 5 Preconstruction Monitoring – Significant Monitoring Concentration |
| --- |
| Pollutant | Averaging Period | SMC (ug/m3) | Maximum Predicted Project Impact (ug/m3) |
| PM10 | 24-Hour | 10.0 | 1.092 |
| PM2.5 | 24-Hour | N/A | 0.829 |
| PM2.5 | Annual | N/A | 0.060 |

Table 5 Key:

SMC = Significant Monitoring Concentration

ug/m3 = micrograms per cubic meter

N/A = Not Available

EPA had established an SMC for PM2.5 but this SMC was remanded by the United States Court of Appeals for the DC Circuit on January 22, 2013 (No. 10-1413, Sierra Club v. EPA). On March 4, 2013, the EPA Office of Air Quality Planning and Standards issued guidance to applicants and regulators with regard to the ramifications of the January 22, 2013 Appeals Court decision. The pertinent excerpt of this recent EPA guidance is as follows:

As a result of the Court’s decision, Federal PSD Permits issued henceforth by either the EPA or a delegated state permitting authority pursuant to 40 CFR 52.21 should not rely on the PM2.5 SMC to allow applicants to avoid compiling air quality monitoring data for PM2.5. Accordingly, all applicants requesting a federal PSD Permit, including those having already applied for but have not yet received the permit, should submit ambient PM2.5 monitoring data in accordance with the Clean Air Act requirements whenever either direct PM2.5 or any PM2.5 precursor is emitted in a significant amount. In lieu of applicants setting out PM2.5 monitors to collect ambient data, applicants may submit PM2.5 ambient data collected from existing monitoring networks when the permitting Authority deems such data to be representative of the air quality in the area of concern for the year preceding receipt of the application. We believe that applicants will generally be able to rely on existing representative monitoring data to satisfy the monitoring data requirement.

The Kenmore Square monitoring site, located approximately one mile from MATEP, is representative of the Facility site due to its close proximity. It was representative in the year preceding receipt of the application and continues to be representative.  Use of the data from this monitoring site is representative of the background ambient air levels for the Boston area, and the Project location in particular.  In addition, the data represents background concentrations that are conservative because they reflect impacts from facility emissions that are also included in the modeling.

For the reasons set forth above, in accordance with the PSD regulations and recent EPA guidance, MassDEP has determined that preconstruction monitoring is not required.

# Justification for Using Significant Impact Levels (SILs) for PM2.5

Despite the fact that the PSD regulations addressing SILs for PM2.5 were partially vacated and remanded (at EPA’s request) in the January 22, 2013 Appeals Court decision, the use of the PM2.5 SILs is still valid in certain circumstances in which ambient background concentrations are relatively low. EPA did not concede that it lacked authority to promulgate SILs and the Court found that it was not necessary to address the question of whether EPA had such authority. In fact, the SILs were vacated and remanded in only PSD sections 40 CFR 51.166(k)(2) and 52.21(k)(2) but were not vacated in 40 CFR 51.165(b)(2). This is most likely because the text of this latter regulation does not exempt a source from ambient air quality analysis but states that if a source located in an attainment area exceeds a SIL in a nonattainment area (or predicted nonattainment situation), it is deemed to have contributed to or caused a violation of a NAAQS.

Key examples in the Appeals Court decision supporting the vacature and remand involved cases in which the ambient air quality background is very close to the NAAQS. This is not the case in the Boston area where the PM2.5 background (24-hour averaging time) is only slightly over half of the NAAQS, 21.7 ug/m3 vs. 35 ug/m3. Likewise, the annual PM2.5 background is about three quarters of the NAAQS, 9.2 ug/m3 vs. 12 ug/m3, a difference that is fully 9 times the remanded annual SIL value of 0.3 ug/m3.  Therefore, use of the prior PM2.5 SILs is appropriate in the case of the ambient air quality impact analysis for MATEP LP’s Project because the background concentrations plus the SILs still leave a significant margin before the NAAQS would come close to being jeopardized.

Use of the prior PM2.5 SILs is also consistent with the recent EPA guidance on this matter which states:

- The EPA does not interpret the Court’s decision to preclude the use of SILs for PM2.5 entirely but additional care should be taken by permitting authorities in how they apply those SILs so that the permitting record supports a conclusion that the source will not cause or contribute to a violation of the PM2.5 NAAQS.

- PSD permitting authorities have the discretion to select PM2.5 SIL values if the permitting record provides sufficient justification for the SIL values that are used and the manner in which they are used to support a permitting decision.

- The PM2.5 SIL values in the EPA’s regulations may continue to be used in some circumstances if permitting authorities take care to consider background concentrations prior to using these SIL values in particular ways.

- Because of the Court’s decision vacating the PM2.5 SMC, all applicants for a federal PSD Permit should include ambient PM2.5 monitoring data as part of the air quality impacts analysis. If the preconstruction monitoring data shows that the difference between the PM2.5 NAAQS and the monitored PM2.5 background concentrations in the area is greater than the EPA’s PM2.5 SIL value, then the EPA believes it would be sufficient in most cases for permitting authorities to conclude that a proposed source with a PM2.5 impact below the PM2.5 SIL value will not cause or contribute to a violation of the PM2.5 NAAQS and to, therefore, forego a more comprehensive cumulative modeling analysis for PM2.5.

- As part of a cumulative analysis, the applicant may continue to show that the proposed source does not contribute to an existing violation of the PM2.5 NAAQS by demonstrating that the proposed source’s PM2.5 impact does not significantly contribute to an existing violation of the PM2.5 NAAQS. However, permitting authorities should consult with the EPA before using any of the SIL values in the EPA’s regulations for this purpose (including the PM2.5 SIL value in section 51.165(b)(2), which was not vacated by the Court).

# Secondary PM2.5 Impacts

EPA (2013) has recently adopted guidance regarding secondary PM2.5 formation in PSD dispersion modeling analyses.

- Case 1: If PM2.5 emissions < 10 tpy and NOx & SO2 emissions < 40 tpy, then no PM2.5compliance demonstration is required.

- Case 2: If PM2.5 emissions > 10 tpy and NOx & SO2 emissions < 40 tpy, then PM2.5 compliance demonstration is required for direct PM2.5 emission based on dispersion modeling, but no analysis of precursor emissions from the project source is necessary.

- Case 3: If PM2.5 emissions > 10 tpy and NOx &/or SO2 emissions > 40 tpy, then PM2.5 compliance demonstration is required for direct PM2.5 emission based on dispersion modeling, AND the applicant must account for impact of precursor emissions from the project source.

- Case 4: If PM2.5 emissions < 10 tpy and NOx &/or SO2 emissions > 40 tpy, then PM2.5 compliance demonstration not required for direct PM2.5 emissions, BUT the applicant must account for impact of precursor emissions from the project source.

Since the Project falls into Case 2, only direct emissions of PM2.5 were modeled.  Note that while impacts of secondary PM2.5 emissions have not been explicitly quantified and modeled, sufficient margin is available between the predicted impact concentrations from direct PM2.5 emissions and the NAAQS, that the NAAQS would not be threatened by additional secondary PM2.5 emissions.  This conclusion is further supported by the fact that the maximum PM2.5 impacts are predicted relatively close to MATEP, wherein the secondary formation of PM2.5 takes time and distance and would have maximum impact well downwind from the Facility.

# Impairment to Visibility, Soils and Vegetation

40 CFR 52.21(o) requires the Applicant to conduct an analysis of the air quality impact and impairment to visibility, soils, and vegetation that would occur as a result of the Project and general commercial, residential, industrial, and other growth associated with the project.

The Lye Brook Wilderness Area in southern Vermont is the closest Class I area to MATEP. Lye

Brook is located approximately 175 km to the northwest of MATEP. Based on the proposed emission rates and distance to the nearest Class I location, it is not expected that impacts from the Project will have an adverse effect on visibility in the Class I area. Therefore, a visibility modeling analysis of the proposed MATEP modification was not conducted.

The EPA guidance document for soils and vegetation, “A Screening Procedure for the Impacts of Air Pollution Sources on Plants, Soils, and Animals” (EPA Screening Procedure) (EPA 450/2-81-078) established a screening methodology for comparing air quality modeling impacts to “vegetation sensitivity thresholds.”  As an indication of whether emissions from the Project will significantly impact the surrounding vegetation (i.e., cause acute or chronic exposure to each evaluated pollutant), the modeled emission concentrations have been compared against both a range of injury thresholds found in the guidance, as well as those established by the NAAQS secondary standards.  Since the NAAQS secondary standards were set to protect public welfare, including protection against damage to crops and vegetation, comparing modeled emissions to these standards provides some indication of whether potential impacts are likely to be significant.  Table 6 lists the project impact concentrations and compares them to the vegetation sensitivity thresholds and NAAQS secondary standards.  All pollutant impact concentrations are below the vegetation sensitivity thresholds.

| Table 6. Vegetation Impact Screening Thresholds |
| --- |
| Pollutants | Averaging Period | Max Impacts (Facility + Bkgd) (µg/m3) | Secondary NAAQS (µg/m3) | EPA’s 1980 Screening Concentrations (µg/m3) |
| PM10 | 24-hour | 45.8 | 150 | None |
| PM2.5 | 24-hour | 23.8 | 35 | None |
|  | Annual | 9.4 | 15 |  |

IX.	Mass Based Emission Limits

To ensure the NAAQS and PSD increment are not violated, a PSD Permit must contain enforceable permit terms and conditions which ensure the mass flow rates for each modeled pollutant are not exceeded.  This is accomplished by establishing mass-based emission limits for the modeled pollutant PM10/PM2.5 with or without the use of Continuous Emissions Monitors (CEMS). Since CEMS will not be used for establishing compliance, the applicable stack test method establishes the averaging by default.

The PSD Permit contains the mass-based emission limits the Permittee used in demonstrating compliance with the NAAQS and PM2.5 increment, and are therefore enforceable emission limits in the PSD Permit.

The mass-based emission limits for GHG were not used in the impact analysis for modeling since there is no NAAQS or increment for GHG to protect. The PSD Permit does contain the mass-based emission limits for GHG which are representative of BACT for the Project.

X.	Environmental Justice

MATEP LP addressed the PSD Environmental Justice (EJ) requirements in its PSD permit application. The documentation that is provided in the PSD permit application enabled MassDEP to fulfill its obligation under the provisions of the April 11, 2011 PSD Delegation Agreement between the EPA and MassDEP to “identify and address, as appropriate high and adverse human health or environmental effects of federal programs, policies and activities on minority and low income populations” in accordance with Executive Order 12898 (February 11, 1994). The Executive Order was designed to ensure that each federal agency “make achieving environmental justice part of its mission by identifying and addressing, as appropriate, disproportionately high and adverse human health or environmental effects of its programs, policies and activities on minority and low-income populations.”

The EPA defines EJ as “the fair treatment and meaningful involvement of all people regardless of race, color, national origin or income with respect to the development, implementation, and enforcement of environmental laws, regulations and policies. Fair treatment means that no group of people, including a racial, ethnic, or socioeconomic group, should bear a disproportionate share of the negative environmental consequences resulting from industrial, municipal, and commercial operations or the execution of federal, state, local, and tribal programs and policies.”

The assessment of environmental justice (EJ) considers the following:

- The areas in which the proposed Project may result in significant adverse environmental effects;

- The presence and characteristics of potentially affected minority and/or low-income populations (“communities of concern”) residing in these study areas; and

- The extent to which these communities are disproportionately affected in comparison to the effects experienced by the population of the greater geographic area within which the affected area is located is determined.

The air quality dispersion modeling analysis conducted for the PSD application documents that there will be no disproportionately high and adverse human health or environmental effects of the Project on areas with minority populations and low-income populations, because all predicted Project impacts are below Significant Impact levels (SILs).

# Public Participation

MATEP LP will publish the Notice of Public Hearing and Public Comment Period on the Draft PSD Permit in English, Spanish, Portuguese and Chinese and Russian.  Translators will be provided at the Public Hearing. Upon request, copies of the public record will be provided in Spanish, Portuguese, Chinese, and Russian.

MATEP LP will post electronic copies of the Notice of Public Hearing and Public Comment Period, Proposed Plan Approval, Draft PSD Permit and Draft PSD Fact sheet on its website.

# A summary of the public outreach previously conducted by MATEP LP is given below.

- Notification of Filing an Expanded Environmental Notification Form (EENF) under the Massachusetts Environmental Policy Act (MEPA) and Public Scoping – December 2014

MATEP LP consulted with the EOEEA Environmental Justice Director on December 5, 2014 regarding the overall public outreach approach for the EENF. MATEP LP’s outreach efforts are described below.

MATEP LP requested and received an extended public notice period for the Massachusetts Environmental Policy Act (MEPA) Expanded Environmental Notification Form (ENF). The Expanded ENF was submitted December 16, 2014 and noticed in the December 24, 2014 Environmental Monitor. It was noticed again in the Environmental Monitor on January 7, 2015 as well as in the Boston Herald.

Following notice in the Environmental Monitor, MATEP LP published a two-page fact sheet describing the Project and options for comment in the three most common non-English languages spoken in the zip code areas adjacent to the Project site (02215, 02115, 02120, 02446). The fact sheet was published in English in the Mission Hill Gazette on January 9, 2015, in Spanish in El Mundo Boston on January 15, 2015, in Chinese in Sampan on January 21, 2015 and in Russian in the Boston Russian Bulletin on February 1, 2015. The fact sheets, along with a news announcement, were published on

MATEP LP’s website. The MEPA Office accepted comments in all languages through February 6, 2015.

A public scoping session was held to hear comments on the proposed Project from 5:00 to 7:00 p.m. on January 28, 2015 at the Inn at Longwood (342 Longwood Ave., Boston). MATEP LP provided interpretation services in Spanish, Russian and Chinese at the public meeting.

- Notification of Filing a Single Environmental Impact Report under the Massachusetts Environmental Policy Act (MEPA) – May 2014

The submittal of the Single Environmental Impact Report (EIR) was announced in the Environmental Monitor on May 20, 2015. MATEP LP published the notification of the availability of the Single EIR in English in the Boston Herald on May 15, 2015 and the Mission Hill Gazette on June 12, 2015, in Spanish in El Mundo Boston on May 14, 2015, in Chinese in Sampan on May 8, 2015 and in Russian in the Boston Russian Bulletin on February 1, 2015. The Single EIR was provided to the Boston Public Library central and Parker Hill (Mission Hill neighborhood) branches. Members of the public were able request copies through the MEPA Office. Fact sheets in English, Chinese, Spanish, Russian and Portuguese were placed at the above-noted branches of the Boston Public Library.  The Single EIR was included the PSD permit application as an electronic attachment.

- Longwood Medical Area (LMA) Forum Meeting - September 2015

At a joint meeting of the Medical, Academic and Scientific Community Organization (MASCO) and the Boston Redevelopment Authority (BRA) on September 28, 2015, MATEP presented plans for the combined heat and power facility upgrade project. In addition to MASCO and BRA, the meeting was attended by representatives of institutions within the Longwood Medical Area (LMA) served by MATEP and neighboring residents.

# Conclusion

MassDEP hereby finds that there will be no disproportional adverse health or environmental impact on areas with minority populations and low-income populations. MATEP LP has demonstrated that emissions from the proposed Project itself will be well within the NAAQS, which are designed to be health-protective of the most sensitive populations.

The above-discussed analyses and actions fulfill MassDEP’s obligations under the Delegation Agreement and EPA Environmental Justice Policy.

XI.	National Historic Preservation Act, Endangered Species Act, Tribal Consultation

Section IV of the PSD Delegation Agreement contains the requirements for Applicants (e.g., MATEP), MassDEP, and EPA with regards to the PSD Program. Under the PSD Delegation Agreement, EPA must engage in consultation as required by federal law before MassDEP issues PSD Permits.

Section IV.H.3. states that “If EPA requires more time to consult with an Indian tribe before issuance of a Draft PSD Permit, refrain from issuing the Draft PSD Permit until EPA informs MassDEP that it may do so.” In addition, Section IV.H.4. states that “In all cases, MassDEP will refrain from issuing any Final PSD Permit until EPA has notified MassDEP that EPA has satisfied its NHPA, ESA, and Tribal consultation responsibilities with respect to that Permit.”

The following sections outline how the NHPA, ESA, and Tribal consultation requirements identified under the PSD Delegation Agreement have been met.

# National Historic Preservation Act

On August 25, 2014, Epsilon submitted a letter to the Massachusetts Historic Commission (MHC) notifying the MHC of MATEP LP’s submittal of a PSD Permit Application for the proposed Project.  The letter explained that Epsilon has provided an enclosed Project Notification Form to initiate review in compliance with Section 106  of the National Historic Preservation Act (36 CFR 800) and the State Register Review (950 CMR 71). In a December 9, 2015 letter to MassDEP, EPA stated that NHPA consultation requirements for the proposed Project have been satisfied.

# Endangered Species Act

Section 7 of the Endangered Species Act (ESA) requires that certain federal actions such as federal PSD Permits address the protection of endangered species in accordance with the ESA.

On October 29, 2015 Epsilon submitted a letter to Thomas R. Chapman, Supervisor, New England Fish and Wildlife Service (FWS) field office notifying the FWS office of MATEP LP’s submittal of the PSD Permit Application for the proposed Project.  The letter stated that

MATEP LP is aware of and understands current ESA consultation procedures outlined on the FWS website. The website provides an endangered species consultation process in which the Applicant conducts the initial consultation. Epsilon reviewed the data for part of Suffolk County and identified three potential endangered species, the piping plover, Red Knot (migratory only), and Northern Long-eared Bat.  The Piping Plover is found only in Revere and Winthrop and thus does not reside near the MATEP project. The Red Knot is a migratory listing only and is scattered along the coast in small numbers and not near the Facility in Boston. Finally, the Northern Long-eared Bat resides statewide in mines, caves and forested habitats, none of which match the MATEP area.

In a December 9, 2015 letter to MassDEP, EPA stated that ESA consultation requirements for the proposed Project have been satisfied.

# Tribal Consultation

On August 26, 2014, Epsilon submitted separate letters to the Tribal Environmental Directors and the Tribal Historic Preservation Officers for the Wampanoag Tribe of Gay Head (Aquinnah) and Mashpee Wampanoag Tribe.  The letters notified the Tribes of the proposed Project’s PSD Permit Application and described how the proposed Project will support system reliability, expand service, and improve energy efficiency. As of this date, the Tribal Environmental Directors for the two tribes have not responded to the letters. EPA finds that the submittal of the separate letters to the Tribal Environmental Directors satisfies its tribal consultation for the MATEP LP PSD permit.

In a December 9, 2015 letter to MassDEP, EPA stated that Tribal consultation requirements for the proposed Project have been satisfied.

XII.	Comment Period, Hearings and Procedures for Final Decisions

All persons, including Applicants, who believes any condition of the Draft Permit is inappropriate is required to raise all issues and submit all available arguments and all supporting material for their arguments in full by the close of the public comment period, 5:00 p.m. on Tuesday, May 24, 2016, to Edward J. Braczyk of MassDEP at the address listed in Section XIII of this Fact Sheet.

[Note: the language below would appear in any PSD Permit issued by MassDEP.  It is being provided in this Draft PSD Fact Sheet so that interested persons will understand the applicable appeal process for any PSD Permit that may issue following the Public Hearing and Comment Period.]

Along with the PSD Permit, each person is being notified of their right to appeal, in accordance with 40 CFR 124.15 and 124.19 via the following language:

- Within 30 days after the final PSD Permit decision has been issued under 40 CFR 124.15, any person who filed comments on the Draft Permit or participated in any public hearing may petition EPA’s Environmental Appeals Board to review any condition of the Permit decision.

- The effective date of the Permit is 30 days after service of notice to the Applicant and commenters of the final decision to issue, modify, or revoke and reissue the Permit, unless review is requested on the Permit under 40 CFR 124.19 within the 30 day period.

- If an appeal is made to the EAB, the effective date of the Permit is suspended until the appeal is resolved.

XIII.	MassDEP Contacts

Additional information concerning the Draft PSD Permit may be obtained between the hours of 9:00 a.m. and 5:00 p.m., Monday through Friday, excluding holidays from:

# Edward J. Braczyk

MassDEP Northeast Regional Office

205B Lowell Street

Wilmington, MA 01887

(978) 694-3200

edward.braczyk@state.ma.us

In addition, information on the Project and the Draft PSD Permit may be obtained through the MassDEP website at:  http://www.mass.gov/eea/agencies/massdep/about/contacts/matep.html .

# Footnotes

.   EPA, Office of Air Quality Planning and Standards, “Circuit Court Decision on PM2.5 Significant Impact Levels and Significant Monitoring Concentration – Questions and Answers”, March 4, 2013.

http://www.epa.gov/nsr/documents/20130304qa.pdf