## Slide 1: Decarbonizing the State
Leading By Example Council Meeting
May 12th, 2026
Presented by
Department of Energy Resources, Leading By Example Division
05/12/2026

## Slide 2: Agenda
Time | Topic
10:00AM – 10:10AM | Introduction & Agenda
10:10AM – 10:25AM | Department of Conservation and Recreation Speakers: JP Allen, Project Manager, DCR ¦ Ryan Kingston, Decarbonization Program Manager, DCR
10:25AM – 10:40AM | UMass Boston Speaker: James O’Day, Director of Facilities
10:40AM – 10:55AM | UMass Dartmouth Speaker: David Gingerella, Vice Chancellor of Administration & Facilities, UMD
10:55AM – 11:10AM | UMass Amherst Speaker: Raymond Jackson, Executive Director of Facilities Management, UMA
11:10AM – 11:25AM | DCAMM Speakers: Jessica Swenson & Fred Mitchell
11:25AM – 11:40AM | Q&A
11:40AM – 12:00PM | In the News, Reminders and Updates
12:00PM | Closing

## Slide 3: Decarbonizing DCR
LBE Council Meeting
LBE Council Meeting
May 12, 2026
Massachusetts Department of Conservation and Recreation
Ryan Kingston, Decarbonization Planning Manager
JP Allen, Project Manager – Architecture Section

## Slide 4: DCR’s Net Zero Goals
EVs
Replace vehicles with EVs
Install charging stations
Public charging
Strategic planning
Partner with other agencies, leasees
Buildings
Deploy heat pumps
Weatherization and insulation
Target net-zero for new construction
Solar
Maximize solar potential
Secure grants and other funding
Operations
Information-sharing
Electric landscaping equipment
Pollinator habitats
Net Zero Goals adopted by DCR leadership in 2022 to put directives of EO594 into action

## Slide 5: DCR’s Emissions Profile
Chart: FY2024* onsite FF emissions
| Vehicle | Fuel Oil | Natural Gas | Other (Onsite) | Propane
FY24 | 4669.2271 | 1830.2121 | 1701.4888 | 278.5902 | 131.1797
Just under half of DCR’s onsite fossil fuel emissions come from buildings
Of the emissions that come from buildings, over half come from just 10 locations
  5 rinks
  3 maintenance facilities
  1 administrative building
  1 island
Largest electric accounts are a mix of various use-cases – streetlights, campgrounds, buildings
  The highest-use buildings include rinks and maintenance facilities
*Awaiting data on some FY25 delivered fuels, but general proportions of each fuel likely similar to FY24
Chart: Building Onsite Emissions Top 10 vs remainder
| Top 10 | Next 10 | Remainder
 | 1432.6286 | 469.6154 | 826.5915

## Slide 6: Decarbonize Everything…

## Slide 7: Building Decarbonization Efforts
Small sites
“ASHP Installation Reports”
Swap-out heating systems as they approach end of life
Large sites
Conduct study (e.g. House Doctors, PRF74, etc)
Implement recommendations depending on scope (e.g. Ch 149, maintenance contracts)
Rinks
Southwest Corridor

## Slide 8: DCR Rinks & Cass
DCR rinks responsible for about 1/3rd of DCR’s building fossil fuel emissions
MEP study completed in 2024 provided general recommendations for heating system replacements
Design completed in 2025 detailed layout, sizing, etc, of proposed upgrades including ASHP, HRV, and electric resistance
RFP to implement work to be released soon, with 1-2 projects completed per year for the next 2-3 years
Notes: In 5 rinks, waste heat reuse; Zambonis release heat, this is recovered for reuse around building

## Slide 9: Southwest Corridor Park Headquarters: Deep Energy Retrofit 38 New Heath Street - BOSTON
Southwest Corridor Park Headquarters:
Sole maintenance facility for the 4.7-mile long urban park know as Southwest Corridor Park
8 full time Operations Staff and 2 Seasonal Staff deployed from this building
During severe weather events, occupied 24 hours/day; additional 4-6 DCR personnel serve as dispatch for "MA Emergency Storm Center"
Nestled at intersection of Mission Hill, Jamaica Plain, and Fort Hill neighborhoods of Boston
Once an industrial park, now one of the most rapidly growing residential neighborhoods

## Slide 10: Southwest Corridor Park Headquarters: Deep Energy Retrofit Existing Air Leakage and Thermal Bridging [FEASIBILITY STUDY]
Why this one...
A feasibility study was performed in 2021 to identify four of DCR's highest energy users
This study included Fall River Heritage State Park, Waquoit Bay Gate & Boat Houses, and the Southwest Corridor Park Headquarters
This study examined yearly utility bills and thermal imaging to determine the most urgent need.
Location was also a determining factor to ensure that our decarbonization efforts would have the greatest local impact.
  “The least efficient heating system, in one of the worst performing envelopes” - Ryan Kingston

## Slide 11: Southwest Corridor Park Headquarters: Deep Energy Retrofit Roof Mounted Photovoltaic Array – 97.5 kWdc
Strategy One: Tighten up the building!
Perform blower door test
Design thoughtfully
Building Science based solutions
Strategy Two: Lower grid consumption!
10,721 sf of available roof, unobstructed by other urban infrastructure – PV projected to produce 97.5 kWdc
Transition from electrical resistance to ASHP
White PVC Roof Membrane
Strategy Three: Give a little back!
Timber [Accoya] cladding has a more residential character
Low embodied and operational carbon
Accoya is farmed from sustainable sources
Accoya can be returned to the earth
Timber sequesters carbon

## Slide 12: Southwest Corridor Park Headquarters: Deep Energy Retrofit Blower Door Test [PRE-CONSTRUCTION]
HVAC Exhaust [wrapped for airtightness] - Typical
HVAC Exhaust [wrapped for airtightness] – Roof Insulation Fail

## Slide 13: Southwest Corridor Park Headquarters: Deep Energy Retrofit Blower Door Test [PRE-CONSTRUCTION] (2)
A blower door test was performed to calculate the existing buildings air leakage.
Test was performed under positive pressure at 75 pascals
Result – 0.753 CFM/sf
Code – 0.35 CFM/sf
Equivalent Area = 16.2 sf
Main Entry - Northeast
Rear Entry - Southwest

## Slide 14: Southwest Corridor Park Headquarters: Deep Energy Retrofit Existing Air Leakage and Thermal Bridging [PRE-CONSTRUCTION]

## Slide 15: Southwest Corridor Park Headquarters: Deep Energy Retrofit Existing Air Leakage and Thermal Bridging [PRE-CONSTRUCTION]

## Slide 16: Southwest Corridor Park Headquarters: Deep Energy Retrofit Building Envelope Improvements
New Envelope Strategies:
Masonry Repairs
Liquid Applied Air barrier & Waterproof Flashing
Continuous Exterior Building Insulation
Closed Rainscreen Assembly
Double Glazed Windows
Insulated Overhead Doors w/ Sensors
New Interior Envelope Zone
Existing Roof R-Value – R 22
Code Roof R-Value – R 30
New Roof R-Value – R 44 to R 77
Existing Wall R-Value – R 2.5
Code Wall R-Value – R 20
New Wall R-Value – R 30

## Slide 17: Southwest Corridor Park Headquarters: Deep Energy Retrofit
BEFORE...
AFTER...

## Slide 18: Thank You.

## Slide 19: UMass Boston Decarbonization Plan May 2026

## Slide 20: Fossil Fuel Energy Use
Central Utilities Plant
  Burns natural gas for heating the campus
Electricity used for building functions
  Inefficient electrical systems heat some heritage buildings
  Use large electrically driven chillers to cool the campus
Minimum amount of gasoline, diesel, propane from generators, a small fleet of vehicles, and various other uses
Chart: Energy Use in 2022, MMBTU
| Natural Gas for Buildings | Grid Electricity | Gasoline for Vehicles | Other (Diesel & Propane)
129,265 | 129265.4982 | 143995.5407 | 1510.9938 | 343.4714

## Slide 21: How does the Central Utilities Plant (CUP) Work?
High-Temperature Water loop, heats to 170-190°F
Most buildings on campus are connected
Heating: Boilers- Consists of four natural gas-fired hot water boilers that pump HTHW to the buildings
Cooling: Chillers- use sea water and cooling towers for condenser water
Solar/Battery

## Slide 22: Our Plan
How will we use energy?

## Slide 23: Load Profile Analysis

## Slide 24: Recommendations & Results
Reduce energy demand in current buildings
Use & Build Renewable Energy
Build highly efficient new buildings
Electrify central utilities plant
Incorporate resiliency
Energy & Carbon Master Plan
Published Fall 2023
To decarbonize onsite: Utilize our unique Saltwater Pump House (SWPH) ocean thermal energy (similar to geothermal). In Phase 2 and on we will eliminate natural gas boilers over time.
To reduce energy use and lower carbon: Invest in updates to heritage buildings and system controls.
Office
Notes: Energy & Carbon Master Plan can change and has changed since being published

## Slide 25: Thermal Energy Phase 1: Utilities Cooling Capacity
Currently happening to expand cooling.
The Saltwater Pump House (SWPH) provides the equivalent of 50% of the cooling tower capacity to the campus’ central cooling system.
  The Campus has a deficit of cooling capacity on high temperature days, the number of which are increasing annually.
  The SWPH is a single point of failure for a large portion of the cooling capacity to the Campus.
  This project adds cooling capacity for a warming climate and expansion in the future. It is also creating redundancy in the cooling system

## Slide 26: Thermal Energy Phase 2: Heat Shift Chillers
In design phase currently.
Replace natural gas fired boilers with heat shift chillers for both heating and cooling.
New heat shift chillers will use heat rejection in winter to help provide heat to Campus buildings.
In the cooling season the process is reversed, and the heat shift chillers provide cooling to the Campus buildings.
This allows for a phased retirement of the gas fired boilers reducing carbon emissions.
Received $5.3M from State agencies (LBE, DOER)
Air sourced heat pumps
+
Saltwater Pumphouse Heat Shift Chiller

## Slide 27: Appendix A.1 - Heat Shift Chiller Operating Modes
Existing Seawater HX x4
SWS
SWD
CWS
CWR
600 ton HSC (Recovery Mode) (typ.)
CHWS 44F
CHWR 56F
Low Temp HWS (120F)
Low Temp HWR (50F)
Booster Heat Pumps (typ.)
High Temp HWS (180F)
High Temp HWR (160F)
Glycol Optional
Existing ISC Cooling Tower
Existng Water cooled Chiller
Existing Free Cooling HX
Common Heating/Cooling piping
1,100 ton HSC
(Heating Mode) (typ.)
Air to Water Heat Pumps
(Heating Optimized) (typ.)
1,100 ton HSC
(Heating Mode) (typ.)
No flow in this branch during HR mode
Seasonal switchover
for free cooling during heating season
Key/Legend -
CHWS - Chilled Water Supply CHWR - Chilled Water Return HSC - Heat Shift Chiller
HWS - Hot Water Supply HWR - Hot Water Return SWS - Seawater Supply
SWR - Seawater Return/Discharge
Heating + Recovery Mode
No flow in this branch during Heating Mode
Existing Boilers x4
New Existing
New Existing
New
Existing
- 3 Way Valve (Field Installed)
Glycol Required

## Slide 28: Layout of New Plant
7
5
6
DN
DN
UP
DN
UP
UP
UP
FM
FM
TS
FM
FM
FM
T
FM
FM
FM
FM
FM
FM
FM
H
H
G.5
G.5
G
G
F.5
F.5
7
D3
D3
1
1
5
9
11
13
13
15
15
17
17
4
4
5.6
5.6
6.8
6.8
1.8 2
1.8 2
HW-S2
HW-S1
HW-P1
HW-P3
HW-P4
B-3
B-2
B-1
B-4
FM
CHWP-2
CHWP-1
AIR AIR
COMPRESSOCROMPRESSOR
#1 #2
CWP-2
CWP-3
CWP-1
RE-3
RE-2
CH-1
CH-2
CH-3
CH-4
ET-H
ET-H
ET-H
ET-H
ET-H
ET-H
ET-H
ET-H
ET-CW
ET-H
ET-H
ET-H
ET-H
ET-H
ET-H
ET-H
ET-H
ET-CHW-1 ET-CHW-1 ET-CHW-1
CWP-5
CWP-4
CHWP-3
CWP-7
CWP-6
RE-1
RINK
H/X
COND-H/X
F
F
E
E
E.5
E.5
6
8
10
8 9 10 11
12
12
14
14
16
16
HW-S3
CHWP-4
CHWP-5
EF-1
CHW-H/X
AS-H
SF-PKG-100
VFC
HW-P2
VFC
VFC
VFC
VFC
VFC
VFC
VFC
VFC
VFC
VFC
VFC
VFC
AS-CW
AS-CHW-1
N
DATE
CHECKED
JOB NO.
SCALE
DRAWN
BVH
integrated
services
50 Griffin Road South Bloomfield, CT 06002 Tel: (860) 286-9171 Fax: (860) 242-0236
CIVIL, STRUCTURAL, MECHANICAL, ELECTRICAL,
COMMISSIONING AND TECHNOLOGY
CONFORM SET BID PACKAGE NO.1
6 4 P l e a s a n t S t r e e t , W a t e r t o w n , M a s s 0 2 4 7 2 U S A
t 6 1 7 9 2 6 3 3 0 0 f 6 1 7 9 2 4 2 7 4 8 w w w w . s a s a k i . c o m
UMBA PROJECT #10-B1
100 Morrissey Blvd.
Boston, MA 02125
2/14/2013 1:22:10 PM
E:\Revit Local Files\2111184\2111184 - SMEP - 2012 (JWB).rvt
1/8" = 1'-0"
SHEET TITLE:
PHASE 3 HVAC PART PLAN 'A'
DRAWING NO.
H-201.3
UTILITY PLANT RENOVATIONS
UMASS BOSTON UTILITY CORRIDOR AND ROADWAY
UNIVERSITY OF MASSACHUSETTS
9/14/12
JNR
AV
21-11-184
HVAC GENERAL NOTES
1. SEE H-300.3 FOR CORRESPONDING HOT WATER RISER DIAGRAM.
2. SEE H-301.3 FOR CORRESPONDING CHILLED WATER RISER DIAGRAM.
HVAC DRAWING NOTES
PROVIDE NEW PUMP AND ASSOCIATED PIPING.
PROVIDE NEW FAN.
PROVIDE NEW HEAT EXCHANGER AND ASSOCIATED PIPING.
PROVIDE NEW EXPANSION TANKS.
EXISTING EXPANSION TANKS ON HOT WATER SYSTEM RELOCATED FOR USE WITH CHILLED WATER SYSTEM.
PROVIDE 1"X1" STAINLESS STEEL MESH ON BOHT SIDES OF THE EXISTING 20" X 56" OPENING.
PROVIDE NEW 72" X 60" OPENING THEN BOTTOM OF WHICH IS 16" AFF. PROVIDE 72" x 60" FLAT FILTER BOX WITH 9 - 24" x 20" x2" MERV 5 FILTERS ACCESSIBLE FROM
EXPANSION TANK ROOM. PROVIDE A 1" X 1" WIRE MESH ON THE ELECTRICAL ROOM SIDE OF THE OPENING.
ATTACHED TO THE EXISTING 72" x 60" OPENING PROVIDE A 72" x 60" FLAT FILTER BOX WITH 9 - 24" x 20" x 2" MERV 5 FILTERS ACCESSIBLE FROM EXPANSION TANK ROOM.
EXISTING OPENING WITH FIRE DAMPER.
1
2
3
4
5
DEMO PIPE ADJACENT TO BOILER #3 ISOLCATION VALVES. PROVIDE NEW TEE FITTING WITH ISOLATION VALVES ON EACH SIDE OF THE NEW TEE.
PROVIDE TWO (2) 12" MANUALLY OPERATED BUTTERFLY VALVES ON THE HYDRONIC HEATING WATER SUPPLY & RETURN MAINS WITHIN THE PLANT.
PROVIDE TWO (2) 6" TAPS, ONE ON EACH OF THE SUPPLY & RETURN MAINS JUST NORTH OF THE NEW MAIN ISOLATION VALVES.
CONNECT PIPING TO EXISTING DISCHARGE AND SUCTION OF EXISTING PUMP, P- 9.
TERMINATE HW PIPES 5' FROM WALL TO ALLOW FOR FUTURE WALL PENETRATIONS TO ACCOMODATE FUTURE CAMPUS LOOP PIPING.
INSTALLATION OF FIRE PUMP MUFFLER FURNISHED AS PART OF THE WORK OF DIVISION 21 AND INSTALLED AS PART OF THE WORK OF DIVISION 23.
CONNECT TO 3" CWF. CONNECTION TO PLUMBING BY HVAC CONTRACTOR.
TERMINATE 24" CHW PIPES 3' FROM SOUTH WALL, WITH ELBOW DIRECTED DOWN, WITH A BLIND FLANGE.
10 EXISTING OPENING WITH EXISTING FIRE SMOKE DAMPER.
PROVIDE AIR SEPARATOR MOUNTED ON HOUSE KEEPING PAD.
PROVIDE SUSPENDED AIR SEPARATOR.
19
20
11 RE-3. REMOVE PNEUMATIC CONTROL DAMPER ACTUATORS (QTY 4) AN REPLACE WITH MANUAL DAMPER OPERATORS. BALANCE AIR FLOWS TO VALUES LISTED ON21 PLAN. NOTE THAT THE ELECTRIC ACTUATORS CONTROL THE SMOKE DAMPER TO REMAIN.
22
23 RECONFIGURE PIPING, SEE MUA-1 PIPING SCHEMATIC ON DRAWING H-401.2.
6
7
8
9
REMOVE EXISTING GROOVED COUPLINGS AND REPLACE WITH FLANGED OR WELDED COUPLINGS ALLOWING THE PIPING SYSTEM TO OPERATE AT A CONTINUOUS 225°F.
16" BRIDGE FOR HEATING LOOP
6" STANDBY HEADER.
INSTALL 30" MANUALLY OPERATED BUTTERFLY VALVES IN THE CHWS&R MAINS JUST NORTH OF COLUMN LINE H AS SHOWN ON PLAN.
24 CONNECT TO EXISTING RINK H/X PIPING. SEE DWG H-301.1 FOR CORRESPONDING CHW RISER DIAGRAM.
25
26
27
18 PROVIDE TWO (2) 12" TAPS, ONE EACH ON THE CHWS&R MAINS JUST NORTH OF 28 THE NEW ISOLATION VALVES. SEE NOTE 17 ABOVE.
NEW 30" ISOLATED VALVES PHASE 1.
NEW 10" ISOLATION VALVES PHASE 1.
NEW 12" TAPS AND ISOLATION VALVES PHASE 1.
REMOVE 6" GROOVED TAPS BY REPLACING SECTION OF PIPE AND REWELDING.
30 MOTORIZED VALVE.
31 NEW 3" ISOLATED VALVES PHASE 1.
32
33
34 NEW 10" TAP[S AND ISOLATION VALVES PHASE 1.
35
36
KEY PLAN
REVISIONS
NO.
1
DATE ISSUE
10/12/12 Addendum #2
2
1/28/2013 ESI #002
2/15/13 CONFORM SET
L: 17' 10"
W: 12' 1"
H:10' 8"
400 Ton York SCYK
17'-10"
12'-1"
3'-0"
6'-0"
6'-0"
14'-0"
2200 Ton Trane CVVH
L: 17' 5"
W: 11' 6"
H:11' 10"
17'-5"
11'-6"
4'-0"
3'-0"
17'-0"
This drawing reflects the Addendum 2 changes m3a'd-0e "in phases 1, 1D and 2
Simultaneous Heating and Cooling (typ)
Primary Heating/Cooling HSC (3)
High Temp HW Boosting HSC (3)
OPTION 3B

## Slide 29: Heating Electrification Proposed
Heat Pumps use electricity from the grid

## Slide 30: Existing
Page 1 of 6
04/24/2024
[4 x Existing]
[Existing]

## Slide 31: 2026-2030: Heat Shift Chillers (Recovery)
[Existing]
[New]
[3 x Existing]
[New]

## Slide 32: 2026-2030 Heat Shift Chillers (Seawater) & Phase out Boilers
[2 x Existing]
[X x New]

## Slide 33: 2036-2050 Convert Campus to Low Temp. Heating Hot Water
[1 x Remaining]

## Slide 34: Liberal Arts & Sciences Building Restoration
GeoConnect Study
University of Massachusetts Dartmouth May 11, 2025

## Slide 35: LARTS Building Restoration Project
The LARTS building is an iconic 1966 work of Brutalist architecture by Paul Rudolph
With 34 classrooms, 173 offices, several student-support centers, academic departments, and common space, the 125,000-sf building is the academic workhorse of the campus
This project will improve the student experience and longevity of the building while protecting its architectural integrity

## Slide 36: Project Scope
GROUND-LOOP HEAT EXCHANGER
Dry and comfortable
New, insulated windows; new window coverings
Fresh feel
More inclusive, welcoming, and user-friendly
Safer and code-compliant
Executive Order 594: Shift to clean energy for public buildings and campuses
LARTS is an important part of UMass Dartmouth’s strategy

## Slide 37: Modernizing an Icon
The design sensitively integrates new systems into the existing historic building.
The existing building has an energy use intensity (EUI) of 132 kBTU/sf/year
Current modeling is tracking 40 kBTU/year, a 70% reduction in energy use intensity

## Slide 38: Geothermal Borefield
Geothermal borefield in progress
LARTS BUILDING
GEOTHERMAL BOREFIELD
QUAD
TO AUDITORIUM + ADMISSIONS
NEW OUTDOOR EQUIPMENT ENCLOSURE
Ground-source heat pumps circulate water in 650’-deep wells. The natural temperature of the earth warms the water in the winter and cools it in the summer. This water is circulated through the heating & cooling systems in the building.
50 bores at 650’ deep
No visible elements at the surface
Location selected to support future expansion of campus geo capacity AND future building sites

## Slide 39: Outdoor equipment enclosure
Air-cooled chiller and geothermal equipment will be contained in a new, freestanding outbuilding and enclosure
The design will complement the existing architecture while remaining distinct
Materials include custom fluted concrete block and preweathered wood screening

## Slide 40: GeoConnect Study
Is it possible for the new geothermal system to support additional campus buildings during non-peak load periods?
Is it possible to use the LARTS systems to provide redundancy?
The study is exploring whether the geothermal piping can be routed to the existing systems serving nearby building(s).
LARTS
GEOTHERMAL BOREFIELD
QUAD
AUDITORIUM + ADMISSIONS
CAMPUS CENTER
LIBRARY
SENG

## Slide 41: MA DOER LBE Council Meeting May 12, 2026

## Slide 42: Electrification of Central Heating Plant
Steam generation from electricity
  Direct-to-steam heat pump
  Use of residual heat in condensate return
  Can be adapted to other sources (e.g., wastewater)
System design in progress
  Reduction of scope 1 emissions by ~10,000 MTCO2E (~12% of campus)
  Estimated cost: $18.5M
  Eversource Incentive
  MA DOER DIG Grant Request: $7.35M

## Slide 43: Industrial Heat Pump
Superior Efficiency – COP 3 – 4 times more heat energy than electricity consumed
Decarbonization & Sustainability – by electrifying heat can eliminate fossil fuel
Waste Heat Recovery – upgrade waste heat from industrial processes to useable high temperature process heat
Lower Operating Cost High - high efficiency leads to lower energy bills
Reduce Maintenance and Risk – as compared to fossil fuel boilers.

## Slide 44: Highly Efficient
1 kWh
Heat Pump
Transition grid losses
Driver Motor
“Coefficient of Performance”
2-4 kWh Usable Heat
0,95 kWh
Electricity

## Slide 45: Recover Process Heat

## Slide 46: Site Location

## Slide 47: Parking Lot #28 Photo Voltaic Parking Canopies

## Slide 48: Great Location For Expansion
Surface water and sewage water as heat source
Kompressor
Motor
Ambient Heat
District heating grid
Historically grown networks need temperatures up to 130°C
High performance heat pumps can be seamlessly integrated in existing networks
Important: Optimize networks as far as possible (lower temperatures, storage)
Heat Source:
Sewage 15°C
River 5°C
Warmer Source and/or colder return:
Better efficiency (C.O.P.)!

## Slide 49: Project Summary
Reduce University’s onsite GHG emissions by 15%
Cost Effective
Highly Efficient
Eligible for Eversource Incentive
Modular Unit – can be moved in the future
Ability to be converted to water-to-water heat pump in the future
Great site location – next to Waste Water Treatment Plant – for future heat recovery
Being coupled with near by solar photo voltaic and battery storage projects. On same electrical feeder.

## Slide 50: DCAMM

## Slide 51: Q&A
Any questions for our speakers?
Raise your hand in Zoom or type your questions in the chat.

## Slide 52: In the News…

## Slide 53: Norway hits record EV shares
Norway had 98.6% new EVs registered in April 2026
Biggest contributors were VW, Toyota, BMW, Skoda, and Volvo
Of the 11,103 new passenger cars registered in April:
  10,985 were electric (BEV, PHEV, HEV)
  Of those, 10,952 were fully battery electric
  118 ran on fossil fuels
Over one-third of Norway’s vehicles are electric
Source: Norway hits record 98.6 pct EV share in April, led by VW and Toyota

## Slide 54: Used EV Sales Surge
After the end of federal tax credits in September, used EVs fare better than new
Americans bought nearly 43,000 used EVs in March, marking new monthly record
In March, used EV sales rose by 28% year-over-year
At the same time, roughly 83,000 new EVs were sold, but experienced a nearly 25% year-over-year decline
Source: What EV Slowdown? Used Electric Car Sales Hit A Record High In March

## Slide 55: Clean power met all new electricity demand in 2025
A historic year for solar and other renewable energy sources
Solar grows at highest rate in eight years as exponential rise continues
Fossil generation falls in China and India in historic reversal
Renewables overtake coal for the first time in modern era
Source: Global Electricity Review 2026 | Ember

## Slide 56: Vineyard Wind Contracts Activate
806-MW project ensures stable, affordable prices for the next 20 years
Will save Massachusetts customers a projected $1.4 billion on electricity bills (an average of 1.4 cents/kWh in direct bill savings)
Reduces carbon emissions by more than 1.6 million metric tons per year – equivalent of taking 325,000 cars off the road annually or burning more than 3.7 million barrels of oil
Source: Vineyard Wind Contracts Lower Electricity Prices for Massachusetts Customers | Mass.gov

## Slide 57: Healey-Driscoll Administration Invests $13.4M into Community Colleges
Heat Pump & HVAC Training Network aims to help community colleges establish or upgrade training centers, expand capacity, and provide students with resources they need to enter the workforce
13 community colleges received grants of between $555,000 and $1,250,000
Expected to support at least 500 additional learners
Funded primarily by DOER and managed by Mass CEC

## Slide 58: April Drought Conditions Worsen
Connecticut River Valley, Central, and Northeast Regions and Nantucket County now in Significant Drought
In April, precipitation was well below normal
Nantucket continues to experience the most significant scarcities
Even with March snowmelt, recent rainfall has not been enough to make up for precipitation and groundwater deficits from the past two years
Source: EEA

## Slide 59: LBE Updates & Reminders

## Slide 60: Drive Electric MA Symposium: June 10th
See LBE staff present!
When: Wednesday, June 10th
Symposium – 9:00AM
EVICC Meeting – 1:00PM
Where: AC Hotel, Worcester
Attendees will see presentations and panel discussions focused on EV programs, charging infrastructure expansion, and fleet electrification.
Register for the event via Recharge America.

## Slide 61: 2026 Show & Mow
Join us for this year’s Show & Mow in Northampton!
This event is hosted by City of Northampton and co-hosted by LBE and OSD. Attendees will learn more about battery-powered landscaping equipment (BPLE) and try out equipment offered by FAC116 vendors! Representatives from MassSave and DOER will also be on hand to discuss purchasing incentives.*
*This event is funded partially by National Grid.
When: June 24th, 2026, 9:30AM – 1:00PM
Where: Smith Vocational and Agricultural High School
Register for the event on OSD’s Landing Page.

## Slide 62: Large Building Energy Reporting (LBER) due June 30th
Massachusetts' Large Building Energy Reporting (LBER) is a law that requires DOER to publicly disclose the Energy Usage of Buildings 20,000 square feet or greater.
Reporting on calendar year 2025 data is approaching soon:
Energy reporting for most building types is due June 30th
Buildings that have requested and been approved for campus reporting receive a reporting extension until July 30th
For general questions related to the LBER process for state buildings, email Arianna Zrzavy on the LBE team (Arianna.Zrzavy@mass.gov)

## Slide 63: Digital Accessibility Updates
All public entities are required by federal law and state policy to make digital content accessible.
What does this mean for LBE?
We are improving and updating our web pages.
We are working through documents on our pages and making them accessible.
In the future, when we ask for slides, we will ask for them to be already accessible when sent to us.
We understand this is a learning process, so we are happy to direct you to state accessibility services to learn more! Contact Arianna (Arianna.Zrzavy@mass.gov) with LBE-specific questions.

## Slide 64: Thank You!