# Background/Introduction

**INDOOR AIR QUALITY ASSESSMENT**

**McCloskey Middle School**

**62 Capron Street**

**Uxbridge, Massachusetts**



Prepared by:

Massachusetts Department of Public Health

Bureau of Environmental Health

Indoor Air Quality Program

March 2014

At the request of a parent, the Massachusetts Department of Public Health (MDPH), Bureau of Environmental Health (BEH) provided assistance and consultation regarding indoor air quality (IAQ) at the McCloskey Middle School (MMS) located at 62 Capron Street, Uxbridge, Massachusetts. On November 26, 2013, Cory Holmes, Environmental Analyst/Regional Inspector in BEH’s IAQ Program visited the school to perform an assessment. The assessment was coordinated through the Uxbridge Public Schools Facilities Department and Uxbridge Board of Health.

The MMS is a two-story brick structure with basement built in the 1930s that formerly served as the Uxbridge High School. Additions were built in 1954, 1989 and 1998. The school contains general classrooms, science rooms, art room, gymnasium, auditorium, music rooms, media center, cafeteria, and office space. Windows are openable throughout the building.

# Methods

Air tests for carbon monoxide, carbon dioxide, temperature and relative humidity were conducted with the TSI, Q-Trak, IAQ Monitor, Model 7565. Air tests for airborne particle matter with a diameter less than 2.5 micrometers were taken with the TSI, DUSTTRAK™ Aerosol Monitor Model 8520. BEH/IAQ staff also performed visual inspection of building materials for water damage and/or microbial growth.

# Results

The school houses approximately 470 students in grades 6 through 8 with a staff of approximately 40. Tests were taken during normal operations at the school. Results appear in Table 1.

# Discussion

## Ventilation

It can be seen from Table 1 that carbon dioxide levels were below 800 parts per million (ppm) in 35 of 43 areas, indicating adequate air exchange in the majority of areas examined. It is important to note, however, that several areas had open windows or were empty/sparsely populated, which can greatly reduce carbon dioxide levels. Carbon dioxide levels would be expected to increase with higher occupancy and windows closed.

Fresh air in the majority of classrooms is supplied by unit ventilators (univents) (Picture 1). A univent is designed to draw air from outdoors through a fresh air intake located on the exterior wall of the building (Picture 2). Return air is drawn through an air intake located at the base of each unit where fresh and return air are mixed, filtered, heated or cooled and provided to classrooms through an air diffuser located in the top of the unit ([Figure 1](http://www.mass.gov/eohhs/docs/dph/environmental/iaq/appendices/univent.doc)). Univents were found deactivated in a number of areas (Table 1). In order for univents to provide fresh air as designed, these units must remain on and be allowed to operate while rooms are occupied.

Some classrooms, offices, and common areas (e.g., locker room, gym) are ventilated by air handling units (AHUs) located in mechanical rooms (Picture 3) or mounted on the ceiling. Supply air in these areas is provided via wall/ceiling-mounted diffusers and air is ducted back to the AHUs by wall/ceiling-mounted return vents. The unit in the boys’ locker room/gym office was not operating during the assessment. In addition, exhaust vents in restroom/shower areas in the girls’ locker room gym office were not operating. Exhaust vents in locker rooms and restroom/shower areas should be activated/repaired to remove odors, excess heat and moisture. Strong tire/rubber odors were detected in the gym equipment room, which was not equipped with any means of exhaust ventilation.

Exhaust ventilation for classrooms in the original portion of the building is provided by floor level cubby holes. Air is drawn into these cubby holes and ducted to rooftop motors. The design of these exhausts makes them prone to blockage by classroom items (Picture 4). Exhaust ventilation in the remainder of the building is provided by wall-mounted vents, which were also found obstructed in several areas at the time of the assessment (Picture 5). Both wall and cubby hole exhausts were found not drawing or weakly drawing air in a number of areas (Table 1). In some rooms exhaust vents are located near hallway doors, which reportedly are generally left open. With the hallway doors open, the exhaust vent will tend to draw air from the hallway *into* the classroom, instead of drawing stale air *from* the classroom. Therefore it is recommended that classroom doors remain shut while exhaust vents are operating.

To maximize air exchange, the MDPH recommends that both supply and exhaust ventilation operate continuously during periods of occupancy. In order to have proper ventilation with a mechanical supply and exhaust system, the systems must be balanced to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room. It is recommended that heating, ventilating and air conditioning (HVAC) systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994). The date of the last balancing of these systems was not available at the time of assessment.

Minimum design ventilation rates are mandated by the Massachusetts State Building Code (MSBC). Until 2011, the minimum ventilation rate in Massachusetts was higher for both occupied office spaces and general classrooms, with similar requirements for other occupied spaces (BOCA, 1993). The current version of the MSBC, promulgated in 2011 by the State Board of Building Regulations and Standards (SBBRS), adopted the 2009 International Mechanical Code (IMC) to set minimum ventilation rates. **Please note that the MSBC is a minimum standard that is not health-based**. At lower rates of cubic feet per minute (cfm) per occupant of fresh air, carbon dioxide levels would be expected to rise significantly. A ventilation rate of 20 cfm per occupant of fresh air provides optimal air exchange resulting in carbon dioxide levels at or below 800 ppm in the indoor environment in each area measured. MDPH recommends that carbon dioxide levels be maintained at 800 ppm or below. This is because most environmental and occupational health scientists involved with research on IAQ and health effects have documented significant increases in indoor air quality complaints and/or health effects when carbon dioxide levels rise above the MDPH guidelines of 800 ppm for schools, office buildings and other occupied spaces (Sundell et al., 2011). The ventilation must be on at all times that the room is occupied. Providing adequate fresh air ventilation with open windows and maintaining the temperature in the comfort range during the cold weather season is impractical. Mechanical ventilation is usually required to provide adequate fresh air ventilation.

Carbon dioxide is not a problem in and of itself. It is used as an indicator of the adequacy of the fresh air ventilation. As carbon dioxide levels rise, it indicates that the ventilating system is malfunctioning or the design occupancy of the room is being exceeded. When this happens, a buildup of common indoor air pollutants can occur, leading to discomfort or health complaints. The Occupational Safety and Health Administration (OSHA) standard for carbon dioxide is 5,000 parts per million parts of air (ppm). Workers may be exposed to this level for 40 hours/week, based on a time-weighted average (OSHA, 1997).

The MDPH uses a guideline of 800 ppm for publicly occupied buildings. A guideline of 600 ppm or less is preferred in schools due to the fact that the majority of occupants are young and considered to be a more sensitive population in the evaluation of environmental health status. Inadequate ventilation and/or elevated temperatures are major causes of complaints such as respiratory, eye, nose and throat irritation, lethargy and headaches. For more information concerning carbon dioxide, consult [Appendix A](http://www.mass.gov/eohhs/docs/dph/environmental/iaq/appendices/carbon-dioxide.doc).

Indoor temperature measurements ranged from 68°F to 83°F (Table 1), which were within the MDPH recommended comfort range in most areas on the day of assessment. The MDPH recommends that indoor air temperatures be maintained in a range of 70°F to 78°F in order to provide for the comfort of building occupants. In many cases concerning indoor air quality, fluctuations of temperature in occupied spaces are typically experienced, even in a building with an adequate fresh air supply. In addition, it is difficult to control temperature and maintain comfort without operating the ventilation equipment as designed (e.g., univents/exhaust vents deactivated/obstructed). Of note was the elevated temperature of 83°F in classroom 224, which may indicate a problem with the thermostat/univent heating controls.

The relative humidity measured in the building ranged from 11 to 24 percent, which was below the MDPH recommended comfort range in all areas surveyed (Table 1). The MDPH recommends a comfort range of 40 to 60 percent for indoor air relative humidity. The sensation of dryness and irritation is common in a low relative humidity environment. Low relative humidity is a very common problem during the heating season in the northeast part of the United States.

## Microbial/Moisture Concerns

Water-damaged ceiling tiles were observed in several areas (Table 1; Pictures 6 and 7), which can indicate active/historic leaks from either the roof/building envelope or plumbing system. Water-damaged ceiling tiles can provide a source of mold and should be replaced after a water leak is discovered and repaired.

At the time of assessment, water-damaged gypsum wallboard and ceiling tiles were observed in the cafeteria. In subsequent correspondence with the school Principal, Dr. Rich Drolet, it was reported that work to replace these materials was scheduled to occur over the February 2014 school break. In the interim BEH/IAQ staff recommended covering/sealing the damaged wallboard with plastic sheeting.

The US Environmental Protection Agency (US EPA) and the American Conference of Governmental Industrial Hygienists (ACGIH) recommend that porous materials (e.g., carpeting, gypsum wallboard) be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2001; ACGIH, 1989). If not dried within this time frame, mold growth may occur. Once mold has colonized porous materials, they are difficult to clean and should be removed/discarded.

Dehumidifiers are employed as needed in some areas during hot, humid weather. Dehumidifiers should be cleaned/maintained as per the manufacturer’s instructions to prevent mold/odors associated with standing water.

Plants were noted in some classrooms (Table 1). Plants can be a source of pollen and mold which can be respiratory irritants to some individuals. Plants should be properly maintained and equipped with drip pans and should be located away from univents to prevent the aerosolization of dirt, pollen and mold.

## Other IAQ Evaluations

Indoor air quality can be negatively influenced by the presence of respiratory irritants, such as products of combustion. The process of combustion produces a number of pollutants. Common combustion emissions include carbon monoxide, carbon dioxide, water vapor and smoke (fine airborne particle material). Of these materials, exposure to carbon monoxide and particulate matter with a diameter of 2.5 micrometers (μm) or less (PM2.5) can produce immediate, acute health effects upon exposure. To determine whether combustion products were present in the indoor environment, BEH/IAQ staff obtained measurements for carbon monoxide and PM2.5.

### Carbon Monoxide

Carbon monoxide is a by-product of incomplete combustion of organic matter (e.g., gasoline, wood and tobacco). Exposure to carbon monoxide can produce immediate and acute health effects. Several air quality standards have been established to address carbon monoxide and prevent symptoms from exposure to these substances. The MDPH established a corrective action level concerning carbon monoxide in ice skating rinks that use fossil-fueled ice resurfacing equipment. If an operator of an indoor ice rink measures a carbon monoxide level over 30 ppm, taken 20 minutes after resurfacing within a rink, that operator must take actions to reduce carbon monoxide levels (MDPH, 1997).

The American Society of Heating Refrigeration and Air-Conditioning Engineers (ASHRAE) has adopted the National Ambient Air Quality Standards (NAAQS) as one set of criteria for assessing indoor air quality and monitoring of fresh air introduced by HVAC systems (ASHRAE, 1989). The NAAQS are standards established by the US EPA to protect the public health from six criteria pollutants, including carbon monoxide and particulate matter (US EPA, 2006). As recommended by ASHRAE, pollutant levels of fresh air introduced to a building should not exceed the NAAQS levels (ASHRAE, 1989). The NAAQS were adopted by reference in the Building Officials & Code Administrators (BOCA) National Mechanical Code of 1993 (BOCA, 1993), which is now an HVAC standard included in the Massachusetts State Building Code (SBBRS, 2011). According to the NAAQS, carbon monoxide levels in outdoor air should not exceed 9 ppm in an eight-hour average (US EPA, 2006).

*Carbon monoxide should not be present in a typical, indoor environment*. If it *is* present, indoor carbon monoxide levels should be less than or equal to outdoor levels. On the day of assessment, outdoor carbon monoxide concentrations were non-detect (ND) (Table 1). No measurable levels of carbon monoxide were detected inside the building (Table 1).

### Particulate Matter

The US EPA has established NAAQS limits for exposure to particulate matter. Particulate matter includes airborne solids that can be irritating to the eyes, nose and throat. The NAAQS originally established exposure limits to PM with a diameter of 10 μm or less (PM10). In 1997, US EPA established a more protective standard for fine airborne particulate matter with a diameter of 2.5 μm or less (PM2.5). This more stringent PM2.5 standard requires outdoor air particle levels be maintained below 35 μg/m3 over a 24-hour average (US EPA, 2006). Although both the ASHRAE standard and BOCA Code adopted the PM10 standard for evaluating air quality, MDPH uses the more protective PM2.5 standard for evaluating airborne PM concentrations in the indoor environment.

Outdoor PM2.5 concentrations were measured at 5 to 10 μg/m3 (Table 1). PM2.5 levels measured in the school were between 1 to 12 μg/m3 (Table 1), which were below the NAAQS PM2.5 level of 35 μg/m3. Frequently, indoor air levels of particulates (including PM2.5) can be at higher levels than those measured outdoors. A number of activities that occur indoors and/or mechanical devices can generate particulate during normal operations. Sources of indoor airborne particulates may include but are not limited to particles generated during the operation of fan belts in the HVAC system, use of stoves and/or microwave ovens in kitchen areas; use of photocopiers, fax machines and computer printing devices; operation of an ordinary vacuum cleaner and heavy foot traffic indoors.

### Volatile Organic Compounds

Indoor air concentrations can be greatly impacted by the use of products containing volatile organic compounds (VOCs). VOCs are carbon-containing substances that have the ability to evaporate at room temperature. Frequently, exposure to low levels of total VOCs (TVOCs) may produce eye, nose, throat and/or respiratory irritation in some sensitive individuals. For example, chemicals evaporating from a paint can stored at room temperature would most likely contain VOCs. In an effort to identify materials that can potentially increase indoor VOC concentrations, BEH/IAQ staff examined rooms for products containing these respiratory irritants.

Classrooms contained dry erase boards and related materials. Materials such as dry erase markers and dry erase board cleaners may contain VOCs, such as methyl isobutyl ketone, n-butyl acetate and butyl-cellusolve (Sanford, 1999), which can be irritating to the eyes, nose and throat.

Plug-in air deodorizers (Picture 8) and air fresheners were found in several areas (Table 1). Air deodorizers contain chemicals that can be irritating to the eyes, nose and throat of sensitive individuals. Many air deodorizers contain 1,4-dichlorobenzene, a VOC which may cause reductions in lung function (NIH, 2006). In addition, air deodorizers do not remove materials causing odors, but rather, mask odors which may be present in the area.

## Other Conditions

Other conditions that can affect IAQ were observed during the assessment. In many classrooms, a large number of items were on floors, windowsills, tabletops, counters, bookcases and desks, which provide a source for dusts to accumulate. These items (e.g., papers, folders, boxes) make it difficult for custodial staff to clean. Items should be relocated and/or be cleaned periodically to avoid excessive dust build up. In addition, dust and debris can accumulate on flat surfaces (e.g., desktops, shelving and carpets) in occupied areas and subsequently be re-aerosolized causing further irritation.

Carpeting in a number of areas was found soiled and in disrepair (in some cases loose/wrinkled, which could be a tripping hazard (Pictures 9 and 10)). The Institute of Inspection, Cleaning and Restoration Certification (IICRC), recommends that carpeting be cleaned annually (or semi-annually in soiled high traffic areas) (IICRC, 2005). Since the average service time of carpeting in a school environment is approximately eleven years (Bishop, 2002), consideration should be given to planning for the replacement of carpeting with new flooring.

A number of univents, air diffusers, exhaust/return vents and personal fans were found to have accumulated dust/debris (Picture 11). If exhaust vents are not functioning, backdrafting can occur, which can re-aerosolize accumulated dust particles. Re-activated supply, exhaust/return vents and fans can also aerosolize dust accumulated on vents/fan blades.

Several classrooms contain portable air purifiers to help improve IAQ (Picture 12). It is important to note that these units contain filters that should be cleaned/changed as per the manufactures’ instructions. In addition, the units should be elevated off the floor (e.g., on a stool or table) to prevent draw of accumulated dust/debris located at floor level.

Bowed ceiling tiles were observed in a number of areas (Picture 13; Table 1). If the ceiling tile systems are not intact/installed properly, they can create pathways for accumulated dust/debris in the ceiling plenum to enter occupied areas where they can serve as a source of eye and respiratory irritation. Finally, exposed fiberglass insulation around pipes was seen in several areas (Picture 14; Table 1). Fiberglass can be a source of irritation to the eyes, skin and respiratory system.

# Conclusions/Recommendations

In view of the findings at the time of the visit, the following recommendations are made:

1. Operate all ventilation systems throughout the building (e.g., gym, cafeteria, classrooms) continuously during periods of occupancy to maximize air exchange. If increased airflow is desired, operate univents in fan “high” mode.
2. Examine thermostat/heat controls in classroom 224 to reduce heat and improve thermal comfort for occupants; make repairs as needed.
3. Ensure that mechanical ventilation is activated in the locker rooms, gym offices, shower and restroom areas; make repairs as needed.
4. Install local exhaust vent in gym equipment/football rooms to remove moisture/odors. Please note, a passive vent in the door or undercut may be required to provide “make-up” air.
5. Ensure univents remain clear of blockages/items from the surface of air diffusers (top) and return vents (along front/bottom).
6. Remove blockages/items from wall and cubby hole exhausts to ensure adequate airflow.
7. Close classroom doors for proper operation of mechanical ventilation system/air exchange.
8. Consider adopting a balancing schedule of every 5 years for all mechanical ventilation systems, as recommended by ventilation industrial standards (SMACNA, 1994).
9. Use openable windows in conjunction with classroom exhaust vents to facilitate air exchange. Care should be taken to ensure windows are properly closed at night and weekends to avoid the freezing of pipes and potential flooding.
10. For buildings in New England, periods of low relative humidity during the winter are often unavoidable. Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low. To control dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended. Avoid the use of feather dusters. Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritations).
11. Continue with plans to remove/replace water-damaged wallboard in cafeteria over the February break.
    * In the interim, cover/seal the damaged wallboard with plastic sheeting.
    * During removal, the damaged wallboard should be contained in plastic bags for transport out of the building.
    * Once removed, clean non porous surfaces with an antimicrobial agent and vacuum surfaces with a HEPA-filtered vacuum cleaner and/or wet wiping techniques.
12. Ensure roof/plumbing leaks are repaired and replace any remaining water-damaged ceiling tiles. Examine the area above these tiles for mold growth. Disinfect areas of water leaks with an appropriate antimicrobial, as needed.
13. Use dehumidifiers as needed in areas of excessive moisture (e.g., >70% for extended periods of time) during hot, humid weather. Clean/maintain dehumidifiers as per the manufacturer’s instructions to prevent mold/odors associated with standing water in units.
14. Ensure indoor plants are equipped with drip pans. Examine drip pans periodically for mold growth and disinfect with an appropriate antimicrobial, as needed. Move plants away from the air stream of mechanical ventilation equipment.
15. Clean and maintain filters for portable air purifiers as per the manufacturer’s instructions; elevate units off the floor.
16. Rewrap damaged fiberglass pipe insulation where needed to prevent exposure to fiberglass in occupied areas.
17. Ensure ceiling tiles are installed correctly to prevent bowing/spaces into the ceiling plenum.
18. Relocate or consider reducing the amount of materials stored in classrooms to allow for more thorough cleaning of classrooms. Clean items regularly with a wet cloth or sponge to prevent excessive dust build-up.
19. Refrain from using air fresheners and deodorizers to prevent exposure to VOCs.
20. Continue to clean carpeting annually or semi-annually in soiled high traffic areas as per the recommendations of the Institute of Inspection, Cleaning and Restoration Certification (IICRC). Copies of the IICRC fact sheet can be downloaded at: <http://www.cleancareseminars.com/carpet_cleaning_faq4.htm> (IICRC, 2005).
21. Consider a long-term plan to replace old/soiled/damaged carpeting as funds become available. Consider replacing carpeting with a non-porous surface such as vinyl tile.
22. Clean personal fans, air diffusers and return vents periodically of accumulated dust.
23. Vacuum interior of univents regularly (e.g., during regular filter changes).
24. Consider adopting the US EPA (2000) document, “Tools for Schools”, as an instrument for maintaining a good indoor air quality environment in the building. This document is available at: <http://www.epa.gov/iaq/schools/index.html>.
25. Refer to resource manual and other related indoor air quality documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings. These documents are available at: <http://mass.gov/dph/iaq>.

# References

ACGIH. 1989. Guidelines for the Assessment of Bioaerosols in the Indoor Environment. American Conference of Governmental Industrial Hygienists, Cincinnati, OH.

ASHRAE. 1989. Ventilation for Acceptable Indoor Air Quality. American Society of Heating, Refrigeration and Air Conditioning Engineers. ANSI/ASHRAE 62-1989.

Bishop. 2002. Bishop, J. & Institute of Inspection, Cleaning and Restoration Certification. A Life Cycle Cost Analysis for Floor Coverings in School Facilities.

BOCA. 1993. The BOCA National Mechanical Code/1993. 8th ed. Building Officials and Code Administrators International, Inc., Country Club Hill, IL.

IICRC. 2005. Carpet Cleaning FAQ 4 Institute of Inspection, Cleaning and Restoration Certification. Institute of Inspection Cleaning and Restoration, Vancouver, WA.

MDPH. 1997. Requirements to Maintain Air Quality in Indoor Skating Rinks (State Sanitary Code, Chapter XI). 105 CMR 675.000. Massachusetts Department of Public Health, Boston, MA.

NIH. 2006. Chemical in Many Air Fresheners May Reduce Lung Function. *NIH News*. National Institute of Health. July 27, 2006. <http://www.nih.gov/news/pr/jul2006/niehs-27.htm>.

OSHA. 1997. Limits for Air Contaminants. Occupational Safety and Health Administration. Code of Federal Regulations. 29 C.F.R 1910.1000 Table Z-1-A.

Sanford. 1999. Material Safety Data Sheet (MSDS No: 198-17). Expo® Dry Erase Markers Bullet, Chisel, and Ultra Fine Tip. Sanford Corporation. Bellwood, IL.

SBBRS. 2011. Mechanical Ventilation. State Board of Building Regulations and Standards. Code of Massachusetts Regulations, 8th edition. 780 CMR 1209.0

SMACNA. 1994. HVAC Systems Commissioning Manual. 1st ed. Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

Sundell. 2011. Sundell, J., H. Levin, W. W. Nazaroff, W. S. Cain, W. J. Fisk, D. T. Grimsrud, F. Gyntelberg, Y. Li, A. K. Persily, A. C. Pickering, J. M. Samet, J. D. Spengler, S. T. Taylor, and C. J. Weschler. 2011. Ventilation rates and health: multidisciplinary review of the scientific literature. *Indoor Air*, Volume 21: pp 191–204.

US EPA. 2000. Tools for Schools. Office of Air and Radiation, Office of Radiation and Indoor Air, Indoor Environments Division (6609J). EPA 402-K-95-001, Second Edition. <http://www.epa.gov/iaq/schools/actionkit.html>.

US EPA. 2001. Mold Remediation in Schools and Commercial Buildings. US Environmental Protection Agency, Office of Air and Radiation, Indoor Environments Division, Washington, D.C. EPA 402-K-01-001. March 2001.

US EPA. 2006. National Ambient Air Quality Standards (NAAQS). US Environmental Protection Agency, Office of Air Quality Planning and Standards, Washington, DC. <http://www.epa.gov/air/criteria.html>.

**Picture 1**

****

**Classroom unit ventilator (univent)**

**Picture 2**

****

**Univent fresh air intake**

**Picture 3**

****

**Air handling unit (AHU) in mechanical room**

**Picture 4**

****

**Cubby hole exhaust prone to obstruction by stored items**

**Picture 5**

****

**Classroom exhaust vent obstructed by furniture and other items**

**Picture 6**

****

**Water-damaged ceiling tiles**

**Picture 7**

****

**Water-damaged ceiling tile**

**Picture 8**

****

**Plug-in deodorizer**

**Picture 9**

****

**Worn/damaged carpeting**

**Picture 10**

****

**Worn/damaged, soiled carpeting**

**Picture 11**

****

**Accumulated dust/debris on exhaust/return vent**

**Picture 12**

****

**Air purifier on floor of classroom**

**Picture 13**

****

**Bowed ceiling tile in classroom**

**Picture 14**

****

**Exposed fiberglass insulation around pipes in classroom**

| **Location** | **Carbon**  **Dioxide**  **(\*ppm)** | **Carbon Monoxide**  **(ppm)** | **Temp**  **(°F)** | **Relative**  **Humidity**  **(%)** | **PM2.5**  **(ug/m3)** | **Occupants**  **in Room** | **Windows**  **Openable** | **Ventilation** | | **Remarks** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Intake** | **Exhaust** |
| Background | 422 | ND | 40 | 22 | 5-10 |  |  |  |  | Cold and cloudy |
| 003 Band Room | 679 | ND | 68 | 20 | 9 | 0 | Y | Y | Y | Exposed fiberglass-pipes |
| 004 | 830 | ND | 72 | 22 | 5 | 0 | Y | Y | Y | UV off, space heater near papers, exhaust vent obstructed-desk |
| 006 Teacher’s Lounge | 688 | ND | 73 | 19 | 4 | 6 | Y | Y | Y | Old/damaged carpeting |
| Art Room | 561 | ND | 70 | 19 | 4 | 0 | Y | Y | Y | Ducted kiln, ducted paint booth |
| Music Room | 674 | ND | 70 | 18 | 6 | 0 | Y | Y | Y | UV and exhaust off, old carpeting, exposed fiberglass-pipes |
| Guidance Office | 705 | ND | 73 | 18 | 2 | 4 | N | Y | Y | Old/damaged carpeting |
| Mr. Flanagan Office | 658 | ND | 74 | 18 | 2 | 1 | Y | Y | Y |  |
| Nurse’s Suite | 684 | ND | 74 | 17 | 3 | 1 | Y | Y | Y | 1 WD CT, rust on supports |
| 115 | 503 | ND | 72 | 11 | 4 | 0 | N | Y | Y | 1 WD CT |
| 116 | 759 | ND | 75 | 16 | 8 | 24 | N | Y | Y | Bowed CTs |
| 125 | 638 | ND | 75 | 15 | 2 | 4 | N | Y | Y | Old/soiled carpeting, 2 WD CT |
| 126 | 560 | ND | 75 | 14 | 12 | 10 | Y | Y | N | Plants, 2-plug in AD, old/damaged carpeting |
| 127 | 450 | ND | 74 | 12 | 6 | 0 | Y | Y | Y | PF-dusty, old carpeting, plug-in AD |
| 128 | 540 | ND | 74 | 13 | 4 | 4 | Y | Y | Y | Old/soiled carpeting, DO |
| 129 | 522 | ND | 75 | 16 | 4 | 0 | Y | Y | Y | 6 WD CT, AD, bowed CTs |
| 130 | 498 | ND | 74 | 15 | 4 | 0 | Y | Y | Y |  |
| 131 | 582 | ND | 75 | 18 | 7 | 1 | Y | Y | Y | Exhaust obstructed, DO, plants, old/soiled carpeting |
| 205 | 540 | ND | 71 | 18 | 3 | 0 | Y | Y | Y | No draw from exhaust, carpeting |
| 206 | 492 | ND | 73 | 16 | 4 | 1 | Y | Y | Y | Exhaust off, AP |
| 209 | 627 | ND | 71 | 18 | 4 | 0 | Y | Y | Y | Exhaust near hallway door, occupants at lunch, 2 WD CT, bowed CTs, dust/debris accumulation on exhaust vent |
| 210 | 972 | ND | 72 | 23 | 3 | 29 | Y | Y | Y | Dust/debris accumulation on exhaust vent, AP-floor, 6 WD CTs |
| 211 | 588 | ND | 72 | 17 | 3 | 1 | Y | Y | Y | 1 WD CT, PF |
| 212 | 715 | ND | 69 | 24 | 2 | 3 | Y | N | N |  |
| 213 | 655 | ND | 69 | 21 | 1 | 0 | Y | Y | Y |  |
| 214 | 688 | ND | 70 | 20 | 2 | 7 | Y | Y | Y | 7 WD CT, bowed CTs, exhaust near hallway door, PF |
| 220 | 705 | ND | 73 | 17 | 4 | 1 | Y | Y | N | Old/stained carpeting |
| 221 | 1253 | ND | 77 | 19 | 3 | 25 | Y | Y | Y | Plants, DO |
| 222 | 1650 | ND | 73 | 22 | 3 | 1 | Y | Y | Y | Exhaust off, 23 occupants gone ~30 mins, DO, PF-dusty |
| 223 | 999 | ND | 74 | 20 | 2 | 0 | Y | Y | Y |  |
| 224 | 1053 | ND | 83 | 22 | 9 | 24 | Y | Y | Y | DO, AP |
| 225 | 1163 | ND | 74 | 24 | 3 | 24 | Y | Y | N | AP (2) |
| 226 | 1170 | ND | 72 | 24 | 10 | 11 | Y | N | Y | DO, plants |
| 233 | 509 | ND | 71 | 15 | 3 | 0 | N | Y | Y | DO |
| 234 | 678 | ND | 72 | 18 | 4 | 6 | N | Y | Y |  |
| 237 | 757 | ND | 72 | 19 | 9 | 20 | Y | Y | Y | Window open, bowed CTs, 4 WD CT |
| 238 | 736 | ND | 72 | 18 | 6 | 0 | Y | Y | Y |  |
| Boys Locker Room | 700 | ND | 68 | 22 | 4 | 15 | N | Y | Y | Supply and exhaust off |
| Gym Office | 666 | ND | 68 | 23 | 4 | 1 | N | N | Y | Exhaust off |
| Library | 511 | ND | 72 | 15 | 8 | 10 | Y | Y | Y |  |
| Cafeteria | 492 | ND | 76 | 13 | 5 | 0 | Y | Y | Y | WD gypsum wallboard and CTs, will be replaced over February 2014 vacation |
| Gym Equipment Room |  |  |  |  |  |  | N | Y | N | Tire/rubber odors, recommend installing duct to remove odors |
| Gym | 661 | ND | 68 | 22 | 8 | ~45 | N | Y | Y |  |
| Girls Locker Room | 673 | ND | 68 | 22 | 9 | 0 | N | Y | Y | RR exhaust off (2) |
| Girls Gym Office | 686 | ND | 70 | 22 | 5 | 0 | N | Y | Y |  |