The Commonwealth of Massachusetts

Executive Office of Health and Human Services

Department of Public Health

Bureau of Environmental Health

Community Sanitation Program

5 Randolph Street

Canton, MA 02021

Telephone: (781)828-7910

Facsimile: (781)828-7703

lauren.thomas@state.ma.us

DEVAL L. PATRICK GOVERNOR TIMOTHY P. MURRAY LIEUTENANT GOVERNOR JUDYANN BIGBY, MD SECRETARY JOHN AUERBACH COMMISSIONER

January 26, 2010

Lynn M. Bissonette, Superintendent

MCI Framingham

P.O. Box 9007

99 Loring Drive

Framingham, MA 01704

Re: Facility Inspection

Dear Superintendent Bissonette:

In accordance with M.G.L. c. 111, §§ 5, 20, and 21, and Department of Public Health Regulations 105 CMR 451.000: Minimum Health and Sanitation Standards and Inspection Procedures for Correctional Facilities; 105 CMR 480.000: Storage and Disposal of Infectious or Physically Dangerous Medical or Biological Waste (State Sanitary Code, Chapter VIII); 105 CMR 590.000: Minimum Sanitation Standards for Food Establishments (State Sanitary Code Chapter X); the 1999 Food Code; and 105 CMR 205.000 Minimum Standards Governing Medical Records and the Conduct of Physical Examinations in Correctional Facilities; I conducted an inspection of MCI Framingham on January 22 and 25, 2010 accompanied by Brad Cowen, Director of Security, Pamela Britt, Fire Safety and Environmental Health Officer and Chris Lanoue, Director of Engineering. Violations noted are listed below (* indicates conditions documented on previous inspection reports).

Smith Building

Lobby Area

No Violations Noted

Women’s Bathroom C133A

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.126	Hot Water: Hot water temperature 1050F

Men’s Bathroom C141A

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, sink fixture leaking

Officer’s Area

Training Rooms

No Violations Noted

Break Room

No Violations Noted

Weight Room 122A

No Violations Noted

Men’s Locker Room

105 CMR 451.123	Maintenance: Floor dirty

105 CMR 451.126	Hot Water: Hot water temperature 1040F

Women’s Locker Room

No Violations Noted

Inside Control

Control

No Violations Noted

P Trap

No Violations Noted

Inmate Bathroom 103A

105 CMR 451.123	Maintenance: Water fountain loose

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, facet leaking on sink fixture

Office C106A

105 CMR 451.353	Interior Maintenance: Light shield loose

Staff Bathroom 106A

105 CMR 451.123	Maintenance: Ceiling vent dirty

105 CMR 451.124*	Water Supply: Insufficient water supply in quantity and pressure at water fountain

Storage Room C104A

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, one light 	fixture not working properly

105 CMR 451.353	Interior Maintenance: Light shields loose

Inmate Break Room 105A

FC 4-601.11(c)	Cleaning of Equipment and Utensils, Objective: Non-food contact surface dirty, 	refrigerator gasket dirty

FC 4-903.11(A)(2)	Protection of Clean Items, Storing: Single-service items not protected from 	contamination, items left uncovered

Storage Room 107A

No Violations Noted

Transportation Office 108A

No Violations Noted

Medical Room 109A

No Violations Noted

Inmate Shower 110A

No Violations Noted

Imamate Shower 111A

105 CMR 451.123*	Maintenance: Wall and floor paint damaged

Control Room 112A

FC 3-501.16(B)*	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 450F

Mechanical/Laundry Room

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, floor drain clogged

105 CMR 451.353	Interior Maintenance: Kick plate missing from washer machine

105 CMR 451.353	Interior Maintenance: Floor dirty

Search Room 115A & 116A

No Violations Noted

Holding Cell 117A-120A

No Violations Noted

Officers Room C108A

No Violations Noted

Visiting Area

105 CMR 451.344	Illumination in Habitable Areas: Several light fixtures not working properly in visiting 	area

105 CMR 451.353*	Interior Maintenance: Carpet not placed properly under vending machines

105 CMR 451.353	Interior Maintenance: Carpet dirty under vending machine

FC 4-601.11(c)	Cleaning of Equipment and Utensils, Objective: Vending machine draws dirty

Inmate Bathroom C138A

105 CMR 451.124	Water Supply: Insufficient water supply in quantity and pressure at handwash sink

105 CMR 451.126	Hot Water: Hot water temperature 930F

Women’s Bathroom

No Violations Noted

Men’s Bathroom

No Violations Noted

Visitation Play Area

105 CMR 451.353	Interior Maintenance: Ceiling vent dirty

Smith Food Service

Kitchen

FC 4-501.11(B)	Maintenance and Operation, Equipment: Equipment components not maintained in a 	state of good repair, kick plate missing from refrigerator unit

FC 4-903.11(B)(1)	Protection of Clean Items, Storing: Trays not stored in the inverted position

FC 3-304.14(B)(2)	Preventing Contamination from Linens: Wet cloth not stored in sanitizer bucket

FC 6-202.11(A)	Design, Construction, and Installation; Functionality: Glass light shields not shatter-	resistant or protected by metal cage shields

FC 4-903.11(A)(3)	Protection of Clean Items, Storing: Empty juice containers not stored 6 inches off the 	floor

FC 5-202.12(A)	Plumbing System, Design: No hot water provided to handwash sink

FC 4-501.112(A)(2)	Maintenance and Operation, Equipment: Inadequate water temperature in the	mechanical warewashing machine

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, vent cover missing 	inside hood

Dinning Room

No Violations Noted

Smith Hallway

105 CMR 451.353	Interior Maintenance: Ceiling vent dirty

Smith Clinic

No Violations Noted

Janitor’s Closet C102

105 CMR 451.353	Interior Maintenance: Ceiling vent dirty

Staff Bathroom C131

No Violations Noted

Staff Bathroom C154

No Violations Noted

Multi-Purpose Room

No Violations Noted

Smith Galleries	Closed-Area no longer utilized

ATU East

Common Area

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, light out 	outside shower units

105 CMR 451.350	Structural Maintenance: Roof leak causing damaged to ceiling and walls near cell # 	220, 221, 217, and 218

Storage Room C129

No Violations Noted

Day Room C130

105 CMR 451.353*	Interior Maintenance: Damaged table top surface not longer easily cleanable

Break Room C124

No FC 4-204.112(A)		Design and Construction, Functionality: No functioning thermometer in refrigerator

Office C136

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, handle missing from refrigerator unit

Lower Level Janitor’s Closet C119

105 CMR 451.353	Interior Maintenance: Ceiling vent dirty

Lower Level Showers

105 CMR 451.123	Maintenance: Wall paint damaged in handicap equipped shower unit

Upper Level Showers

105 CMR 451.123	Maintenance: Flying insects observed in shower area

105 CMR 451.130	Hot Water: Shower water temperature 900F

Upper Level Janitor’s Closet

No Violations Noted

Cells

105 CMR 451.101	Blankets: Blanket damaged in cell # 119-B2

105 CMR 451.102	Pillows and Linens: Pillow damaged in cell # 130-B2

105 CMR 451.321*	Cell Size: Inadequate floor space, cells double bunked

ATU West

Common Area

No Violations Noted

Day Room

No Violations Noted

Lower Level Janitor’s Closet

No Violations Noted

Lower Level Showers

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, handicap equipped shower unit 	out of order

Upper Level Showers

105 CMR 451.123	Maintenance: Vent damaged in left and middle shower units

105 CMR 451.123	Maintenance: Ceiling vent dirty in right shower unit

Upper Level Janitor’s Closet

No Violations Noted

Office C141

No Violations Noted

Cells

No Violations Noted

New Line

Day Room C153

105 CMR 451.353	Interior Maintenance: Vent dirty

105 CMR 451.353	Interior Maintenance: Damaged table top surface no longer easily cleanable

Storage Room C155

No Violations Noted

Office C161

No Violations Noted

Lower Level Janitor’s Closet

No Violations Noted

Lower Level Shower Unit

No Violations Noted

Upper Level Showers

105 CMR 451.123	Maintenance: Vent damaged in left and middle shower units

105 CMR 451.123	Maintenance: Ceiling vent dirty in right shower unit

Upper Level Janitor’s Closet	Under Renovation at the Time of Inspection

Cells

105 CMR 451.103	Mattresses: Mattress damage in cell # 251-B1

105 CMR 451.350	Structural Maintenance: Ceiling damaged in cell # 149 and 159

CCU

Common Area

No Violations Noted

Storage Room

No Violations Noted

Medical Room

105 CMR 451.124	Water Supply: Insufficient hot water supply in quantity and pressure at handwash sink

105 CMR 451.350	Structural Maintenance: Ceiling damaged

Lower Level Showers

105 CMR 451.123	Maintenance: Wall paint damaged in shower unit # C112 and C113

105 CMR 451.123	Maintenance: Shower walls dirty in shower unit # C112, C113, and C114

Lower Level Janitor’s Closet

No Violations Noted

Upper Level Showers

105 CMR 451.123	Maintenance: Shower walls dirty in shower unit # C206, C207, and C208

Cells

No Violations Noted

Second Floor Office Area

Bathroom C210A

105 CMR 451.124	Water Supply: Insufficient water supply in quantity and pressure at water fountain

Bathroom C211A

No Violations Noted

Break Room C218A

105 CMR 451.113	Toilet and Handwashing Sink in Locked Cells: No toilet in locked cell

Room 237A

105 CMR 451.353	Interior Maintenance: Vent dirty

HSU

Second Floor

Medical Room 2

No Violations Noted

Optometry Room

105 CMR 451.344	Illumination in Habitable Areas: Two light fixtures not working properly

Residential Treatment Unit

No Violations Noted

Ob-Gyn Exam Room

105 CMR 451.353	Interior Maintenance: Vent dirty

Project Catch the Hope

No Violations Noted

Barton Housing Unit

Housing Unit Hallway

No Violations Noted

Janitor’s Closet

105 CMR 451.353	Interior Maintenance: No light shield in maintenance area

Library

No Violations Noted

Day Room

105 CMR 451.353*	Interior Maintenance: Damaged table top surface no longer easily cleanable

105 CMR 451.353	Interior Maintenance: Vent dusty

Activity Room

No Violations Noted

Shower Rooms

105 CMR 451.126	Hot Water: Hot water temperature 1150F

Kitchenette

No Violations Noted

Cells

No Violations Noted

First Floor

Medical Records Room

No Violations Noted

Medical Records Break Room

No Violations Noted

HSU Unit

Office

No Violations Noted

Office Bathroom

105 CMR 451.123	Maintenance: Window damaged

Nurse’s Station

No Violations Noted

Detox Room 114

105 CMR 451.322	Cell Size: Inadequate floor space in dorm room

Medical Cell

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, hot water faucet leaking in cell # 	106

105 CMR 451.322	Cell Size: Inadequate floor space in dorm room # 101-109

Doctor’s Office 110

105 CMR 451.110(B)	Hygiene Supplies at Toilet and Handwash Sink: No waste receptacle at handwash sink

105 CMR 451.123	Maintenance: Hot water control missing from handwash sink

Search and Interview Room

No Violations Noted

Shower Room

No Violations Noted

Biohazard Room

105 CMR 451.353	Interior Maintenance: Unfinished wooden surface not easily cleanable

Laundry Room

No Violations Noted

Clinical Area

Nurses Bathroom

105 CMR 451.123*	Maintenance: Radiator paint blistering

Inmate Bathroom

105 CMR 451.123	Maintenance: Unfinished wooden surface in bathroom not easily cleanable

Dental Room# 2

No Violations Noted

X-Ray Room #1

105 CMR 451.110(A)	Hygiene Supplies at Toilet and Handwash Sink: No paper towels at handwash sink

Nurse’s Break Room

105 CMR 451.353	Interior Maintenance: Heater unit rusted

Trauma Room # 4

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, sink leaking

Trauma Room # 6	Occupied at the time of inspection

Lab # 7

No Violations Noted

Treatment Room # 8

No Violations Noted

Treatment Room # 9

No Violations Noted

Treatment Room #10

No Violations Noted

Cottages

Laurel Building

Common Area

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, windows 	covered with plastic to reduce the draft

Officer’s Room

No Violations Noted

Kitchenette

No Violations Noted

Refrigerator Room

No Violations Noted

Slop Sink Room (A)

No Violations Noted

Storage Rooms (A)

No Violations Noted

Interview Room (A)

No Violations Noted

Caustic Room (C)

No Violations Noted

Shower Room A&B

105 CMR 451.130*	Hot Water: Shower water temperature 1450F

Shower Room B&C

105 CMR 451.130*	Hot Water: Shower water temperature 1450F

Hallway A-Cells

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, most 	windows covered with plastic to reduce the draft

105 CMR 451.353	Interior Maintenance: Ceiling vents dirty in cells

Hallway B-Cells

105 CMR 451.344	Illumination in Habitable Areas: Light fixture not working properly, night light not 	working properly in cell # 19

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, most 	windows covered with plastic to reduce the draft

105 CMR 451.353	Interior Maintenance: Ceiling vents dirty in cells

Hallway C-Cells

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, most 	windows covered with plastic to reduce the draft

105 CMR 451.353	Interior Maintenance: Ceiling vents dirty in cells

Algon Building

Common Area

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, most 	windows covered with plastic to reduce the draft

Officer’s Room

No Violations Noted

Kitchenette

FC 4-501.114(C)(2)	Maintenance and Operation; Equipment: Quaternary ammonium solution greater than 	the manufacturers recommended concentration

Refrigerator Room

No Violations Noted

Slop Sink Room (A)

105 CMR 451.353	Interior Maintenance: Wet mops left in buckets

Storage Room (A)

No Violations Noted

Kaivac Machine Storage Room (A)

No Violations Noted

Interview Room (A)

No Violations Noted

Caustic Room (C)

No Violations Noted

Shower Room A&B

105 CMR 451.123*	Maintenance: Soap scum observed in shower unit # 1, 2, and 3

105 CMR 451.130	Hot Water: Shower water temperature 1450F

Shower Room B&C

105 CMR 451.123	Maintenance: Soap scum observed in shower unit # 1, 2, and 3

105 CMR 451.130	Hot Water: Shower water temperature 1450F

Hallway A-Cells

105 CMR 451.344	Illumination in Habitable Areas: Light fixture not working properly, night light not 	working properly in cell # 10

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, windows 	covered with plastic to reduce the draft

105 CMR 451.353	Interior Maintenance: Ceiling vents dirty in cells

Hallway B-Cells

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, windows 	covered with plastic to reduce the draft

105 CMR 451.353	Interior Maintenance: Ceiling vents dirty in cells

Hallway C-Cells

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, windows 	covered with plastic to reduce the draft

105 CMR 451.353	Interior Maintenance: Ceiling vents dirty in cells

Town Line Building

Common Area

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, most 	windows covered with plastic to reduce the draft

105 CMR 451.350	Structural Maintenance: Floor tiles damaged near entrance

Officer’s Room

No Violations Noted

Kitchenette

FC 4-501.114(C)(2)	Maintenance and Operation; Equipment: Quaternary ammonium solution greater than 	the manufacturers recommended concentration

Refrigerator Room

No Violations Noted

Slop Sink Room (A)

No Violations Noted

Storage Rooms (A)

No Violations Noted

Interview Room (A)

No Violations Noted

Caustic Room (C)

No Violations Noted

Shower Room A&B

105 CMR 451.123	Maintenance: Soap scum observed in shower unit # 1, 2, and 3

Shower Room B&C

No Violations Noted

Hallway A-Cells

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, most 	windows covered with plastic to reduce the draft

105 CMR 451.353	Interior Maintenance: Ceiling vents dirty in cells

Hallway B-Cells

105 CMR 451.344	Illumination in Habitable Areas: Light fixture not working properly, night light not 	working properly in cell # 23

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, most 	windows covered with plastic to reduce the draft

105 CMR 451.350	Structural Maintenance: Ceiling tiles damaged in cell # 34

105 CMR 451.353	Interior Maintenance: Ceiling vents dirty in cells

Hallway C-Cells

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, most 	windows covered with plastic to reduce the draft

105 CMR 451.353	Interior Maintenance: Ceiling vents dirty in cells

Pioneer Building

Common Area

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, most 	windows covered with plastic to reduce the draft

105 CMR 451.350	Structural Maintenance: Ceiling leaking outside the kitchenette

Officer’s Room

No Violations Noted

Kitchenette

FC 4-501.114(C)(2)	Maintenance and Operation; Equipment: Quaternary ammonium solution greater than 	the manufacturers recommended concentration

Refrigerator Room

105 CMR 451.353	Interior Maintenance: Ceiling rusted

Slop Sink Room (A)

105 CMR 451.353	Interior Maintenance: Ceiling tiles missing

Storage Rooms (A)

105 CMR 451.353	Interior Maintenance: Ceiling tiles missing

Interview Room (A)

No Violations Noted

Caustic Room (C)

105 CMR 451.353	Interior Maintenance: Ceiling tiles missing

Shower Room A&B

105 CMR 451.123	Maintenance: Ceiling paint peeling in shower # 1, 2, and 3

105 CMR 451.123	Maintenance: Floor finish not easily cleanable in shower room

105 CMR 451.130*	Hot Water: Shower water temperature 1200F

Shower Room B&C

105 CMR 451.123	Maintenance: Floor finish not easily cleanable in shower room

105 CMR 451.130*	Hot Water: Shower water temperature 1200F

Hallway A-Cells

105 CMR 451.344	Illumination in Habitable Areas: Light fixture not working properly, night light not 	working properly in cell # 1

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, most 	windows covered with plastic to reduce the draft

105 CMR 451.353	Interior Maintenance: Ceiling vents dirty in cells

Hallway B-Cells

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, most 	windows covered with plastic to reduce the draft

105 CMR 451.353	Interior Maintenance: Ceiling vents dirty in cells

105 CMR 451.353	Interior Maintenance: Ceiling rusted in cell # 21

Hallway C-Cells

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight, most 	windows covered with plastic to reduce the draft

105 CMR 451.353	Interior Maintenance: Ceiling vents dirty in cells

Modular Building-Overflow

Dorm Area

No Violations Noted

Shower Room

105 CMR 451.130	Hot Water: Shower water temperature 1160F

Bathroom

No Violations Noted

Brewster Building

Brewster 1

Common Area

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, several lights 	out

Control Room

No Violations Noted

Control Bathroom

105 CMR 451.110(A)	Hygiene Supplies at Toilet and Handwash Sink: No paper towels at handwash sink

105 CMR 451.123	Maintenance: Light shield missing

Storage Room

105 CMR 451.353	Interior Maintenance: Vent cover not properly secured

105 CMR 451.353	Interior Maintenance: Wet mop left in buckets

Bathroom

105 CMR 451.123	Maintenance: Vent and light fixture dirty

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, handicap equipped toilet leaking

Shower Room

105 CMR 451.123*	Maintenance: Unfinished wood on ceiling vents

105 CMR 451.123	Maintenance: Walls and floors damaged in shower stall # 4, 5, 6, and 7

105 CMR 451.123	Maintenance: Vent fan out of order

105 CMR 451.123	Maintenance: Ceiling vent dirty

Kitchenette Area

105 CMR 451.126	Hot Water: Hot water temperature 1350F

FC 4-602.12(B)	Cleaning of Equipment and Utensils; Frequency: Interior of microwave oven dirty

FC 6-301.11	Numbers and Capacity; Handwashing Facilities: No soap at handwash sink

Wash Basin Room

No Violations Noted

Room 1	Not in use at the time of inspection

Room 2

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Floor damaged

Room 3

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Floor damaged

Room 4

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Floor damaged

Room 5

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350	Structural Maintenance: Floor damaged

Room 6

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Floor damaged

Room 7

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Floor damaged

Room 8

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Floor damaged

Room 9

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Floor damaged

Room 10	Not in use at the time of inspection

Brewster 2

Common Area

105 CMR 451.345	Illumination in Common Passage Ways and Areas: Inadequate lighting, several lights 	outs

105 CMR 451.353	Interior Maintenance: Several light shields missing

Control Room

No Violations Noted

Control Bathroom

105 CMR 451.123	Maintenance: Light shield missing

Storage Room

105 CMR 451.350	Structural Maintenance: Floor tiles damaged and missing

Bathroom

105 CMR 451.130*	Plumbing: Plumbing not maintained in good repair, no hot water provided to 	handwash sink # 3

105 CMR 451.123	Maintenance: Electric hand dryer not functioning properly

Shower Room

105 CMR 451.123	Maintenance: Vent dirty

105 CMR 451.123	Maintenance: Soap scum observed in shower units # 4 and 7

105 CMR 451.123	Maintenance: Flies observed in shower room

Kitchenette Area

FC 4-501.114(C)(2)	Maintenance and Operation; Equipment: Quaternary ammonium solution greater than 	the manufacturers recommended concentration

Wash Basin Room

No Violations Noted

Room 1

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.101	Blankets: Blanket damaged on bed # 8

Room 2

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Floor damaged

105 CMR 451.141	Screens: Screen damaged

Room 3

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.353	Interior Maintenance: Vent dirty

Room 4

105 CMR 451.103	Mattresses: Mattress damage on bed # 6

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Floor damaged

105 CMR 451.353	Interior Maintenance: Vent dirty

Room 5

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Floor damaged

105 CMR 451.353	Interior Maintenance: Vent dirty

Room 6

105 CMR 451.101	Blankets: Blanket damaged on bed # 1 and 6

105 CMR 451.141	Screens: Screen damaged

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Floor damaged

Room 7

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.344	Illumination in Habitable Areas: Light fixture not working properly

105 CMR 451.350*	Structural Maintenance: Floor damaged

Room 8

105 CMR 451.141	Screens: Screen damaged

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.350*	Structural Maintenance: Floor damaged

Room 9

105 CMR 451.141	Screens: Screen damaged

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.344	Illumination in Habitable Areas: Light fixture not working properly

105 CMR 451.350*	Structural Maintenance: Floor damaged

Room 10

105 CMR 451.103	Mattresses: Mattress damage on bed # 2

105 CMR 451.141	Screens: Screen damaged

105 CMR 451.322*	Cell Size: Inadequate floor space in dorm room

105 CMR 451.344	Illumination in Habitable Areas: Light fixture not working properly

105 CMR 451.350*	Structural Maintenance: Floor damaged

Old Administration Building

First Floor

Rec Room 115B

No Violations Noted

Bathroom 117A

105 CMR 451.123	Maintenance: Light shield missing

105 CMR 451.126	Hot Water: Hot water temperature recorded at 600F at handwash sink

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, faucet leaking

Cosmetology Classroom 130

105 CMR 451.126*	Hot Water: Hot water temperature recorded at 930F at hair washing and handwash 	sinks

105 CMR 451.350*	Structural Maintenance: Ceiling damaged

105 CMR 451.353	Interior Maintenance: Ceiling paint damaged

Prep-Release

No Violations Noted

Weight Room 118

105 CMR 451.344	Illumination in Habitable Areas: Several light fixtures not working properly

105 CMR 451.353	Interior Maintenance: Light shield missing

Fire Equipment Room/Bathroom 119

105 CMR 451.126	Hot Water: Hot water temperature recorded at 800F at handwash sink

Officer’s Room 121

No Violations Noted

Closet 122-2	Locked-Room not accessible at the time of inspection

Closet 122-3	Locked-Room not accessible at the time of inspection

Janitor’s Closet 122-6

No Violations Noted

Closet 122-7

No Violations Noted

Work Assignment 114

No Violations Noted

Staff Bathroom 114

105 CMR 451.126	Hot Water: Hot water temperature recorded at 870F at handwash sink

Classroom 131D

105 CMR 451.141	Screens: Screen damaged

Director of Treatments Office

No Violations Noted

D Hallway

105 CMR 451.331	Radiators and Heating Pipes: Pipes not properly insulated

D Board Bathroom

No Violations Noted

D Board Office 113

No Violations Noted

Room 111

105 CMR 451.350	Structural Maintenance: Window not weather tight, damaged window no repaired 	properly

Gym 112

No Violations Noted

Operations near the Gym

105 CMR 451.350	Structural Maintenance: Several floor tiles missing

105 CMR 451.350	Structural Maintenance: Several ceiling tiles missing

Operation Bathroom

105 CMR 451.126	Hot Water: Hot water temperature recorded at 910F at handwash sink

105 CMR 451.123	Maintenance: Cabinet doors missing

Protestant Chaplin’s Office 137

No Violations Noted

Catholic Chaplin’s Office 139

No Violations Noted

Program Supervisors Office 141

No Violations Noted

Physiological Office 146

No Violations Noted

Staff Bathroom 147

105 CMR 451.123	Maintenance: Wall tiles damaged near doorway

Inmate Waiting Room 148

105 CMR 451.331	Radiators and Heating Pipes: Pipes not insulated properly, insulation damaged

Office 149

No Violations Noted

Second Floor

Old Max Unit	Undergoing renovations at the time of inspection

IPS

105 CMR 451.330	Room Temperature: Room temperature 800F

105 CMR 451.350	Structural Maintenance: Floor damaged

105 CMR 451.353	Interior Maintenance: Light shield missing

IPS Bathroom

105 CMR 451.123	Maintenance: Floor damaged and no longer easily cleanable

105 CMR 451.123*	Maintenance: Handwash sink water worn and no longer easily cleanable

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1070F at handwash sink

Psychology Corridor

Office # 1

105 CMR 451.344	Illumination in Habitable Areas: Light fixture not working properly, one light out

Office # 2

No Violations Noted

Office # 3

No Violations Noted

Office # 4

No Violations Noted

Office # 5

No Violations Noted

Office # 6

No Violations Noted

Office # 7

105 CMR 451.344	Illumination in Habitable Areas: Light fixture not working properly, one light out

Office # 8

No Violations Noted

Office # 9

No Violations Noted

Office # 10

No Violations Noted

Office # 11

No Violations Noted

Bathroom

105 CMR 451.123	Maintenance: Floor tiles damaged

105 CMR 451.123	Maintenance: Light fixture dirty

105 CMR 451.123	Maintenance: Light fixture not working properly

File Room # 13

105 CMR 451.353	Interior Maintenance: Wall paint damaged

Office # 14

No Violations Noted

Office # 15

No Violations Noted

Office # 16

No Violations Noted

Room # 17

No Violations Noted

Office # 18

No Violations Noted

Office # 19

No Violations Noted

Office # 20

No Violations Noted

Education 212

Bathroom

105 CMR 451.110(A)	Hygiene Supplies at Toilet and Handwash Sink: No toilet paper in stall # 2

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, excess water pressure at 	handwash sink

Classrooms

No Violations Noted

Office

No Violations Noted

Industries 213

105 CMR 451.350	Structural Maintenance: Window pane damaged

Office

105 CMR 451.350	Structural Maintenance: Window not weather tight, damaged window no repaired 	properly

Staff Bathroom

105 CMR 451.123	Maintenance: Wall damaged

Inmate Bathroom

105 CMR 451.123	Maintenance: Wall damaged

Building and Trades 214	Program closed

Education Area Staff Bathroom

105 CMR 451.123	Maintenance: Vent cover missing

105 CMR 451.126	Hot Water: Hot water temperature recoded at 1010F at handwash sink

Classroom 215-2

No Violations Noted

Classroom 215-4

105 CMR 451.353	Interior Maintenance: Ceiling tiles not installed properly

Janitors Closet 216

No Violations Noted

Parole Hallway 218

105 CMR 451.350	Structural Maintenance: Ceiling paint damaged in several offices

Parole Bathroom

105 CMR 451.123	Maintenance: Unfinished wooden surfaces not easily cleanable

Parole Kitchenette

FC 3-501.16(B)*	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 440F

Storage Area

No Violations Noted

Law Library 211

No Violations Noted

Office 207

No Violations Noted

Classroom 201

No Violations Noted

Principles Bathroom

105 CMR 451.123	Maintenance: Vent dirty

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1000F at handwash sink

Basement

Laundry Area

105 CMR 451.350*	Structural Maintenance: Windows not structurally sound and weather tight

Inmate Bathroom

105 CMR 451.110(A)	Hygiene Supplies at Toilet and Handwash Sink: No soap at handwash sink

105 CMR 451.123	Maintenance: Standing water on floor outside bathroom

105 CMR 451.126	Hot Water: Hot water temperature recorded at 1000F at handwash sink

Food Service Area

Hallway

FC 6-202.15(D)(1)	Design, Construction, and Installation; Functionality: Screens not installed in exterior 	windows

Inmate Dinning Room

FC 6-501.12(A)	Maintenance and Operation; Cleaning: Facility not properly cleaned, vent dirty

Serving Line

FC 6-101.11(A)(1)	Materials for Construction and Repairs: Surface not easily cleanable, red tabletop 	damaged

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, cover missing from ice cooler

FC 6-501.12(A)*	Maintenance and Operation; Cleaning: Facility not properly cleaned, debris observed 	between the half wall and the serve line

Mechanical Warewashing Room

FC 3-304.14(B)(2)	Preventing Contamination from Linens: Wet cloth not stored in sanitizer bucket

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, floor tiles 	damaged

FC 4-901.11(A)	Protection of Clean Items, Drying: Clean and sanitized trays not allowed to air dry 	fully

Culinary Arts Kitchen

FC 6-202.11(A)	Design, Construction, and Installation; Functionality: Glass light shield not shatter-	resistant or protected by metal cage in grease hood

FC 3-304.12(A)	Preventing Contamination from Utensils: Service utensils stored below the food and 	container line in the pasta in refrigerator unit

FC 3-302.11(A)(1)(b)	Preventing Food and Ingredient Contamination: Preventing cross contamination,	ready-to-eat foods not appropriately separated from raw foods, raw eggs stored above 	ready to eat food

FC 6-101.11(A)(1)	Materials for Construction and Repairs: Surface not easily cleanable, unfinished 	wooden surface on window

Staff Dinning Room

FC 6-101.11(A)(1)	Materials for Construction and Repairs: Surface not easily cleanable, cardboard 	utensil holder

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, ice machine not working properly

Main Kitchen

Hallway

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, windows and 	screens damaged

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, ceiling tiles water 	stained and one damaged

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, one light fixture 	not working properly

Paper Goods Storage Room

FC 4-903.11(A)(2)	Protection of Clean Items, Storing: Single-service items not protected from 	contamination, forks left uncovered

FC 6-202.11(A)	Design, Construction, and Installation; Functionality: Light bulbs not shatter-resistant 	or protected by light shields

Dry Storage Room

FC 6-404.11	Location and Placement; Distressed Merchandise: Dented cans not properly 	segregated

Freezer

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, ice buildup observed in light shield

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, one cooler fan not working properly

Refrigerator

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, floor plate loose

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, light fixture not working properly

Staff Office

No Violations Noted

Back Pots and Pans Area

FC 6-202.15(A)(3)*	Design, Construction, and Installation; Functionality: Outer door not weather and 	vermin tight

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, refrigerator overfilled and preventing door from shutting properly

Bakery Area

FC 4-501.16	Maintenance and Operation, Equipment: Handwashing sink used for warewashing

Refrigerator # 5

No Violations Noted

Freezer # 6

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, light fixture not working properly

Inmate Dinning Area

No Violations Noted

Dry Goods Storage Room

FC 4-903.11(B)(2)	Protection of Clean Items, Storing: Uncovered equipment not protected from 	contaminations, meat cover left uncovered

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, vent cover missing

Broom Area

FC 3-304.14(B)(2)	Preventing Contamination from Linens: Wet cloth not stored in sanitizer bucket

Prep-Table Handwash Sink Near Can Opener

FC 5-202.12(A)	Plumbing System, Design: No hot water provided at handwash sink

Prep-Table Handwash Sink Near 3-Compartment Sink

FC 6-501.11	Maintenance and Operation; Repairing: Facility not in good repair, paper towel holder 	damaged

3-Compartment Sink

FC 4-501.114(C)(2)	Maintenance and Operation; Equipment: Quaternary ammonium compound (QAC)	solution below manufacturer’s recommended concentration in sanitizer bucket

FC 4-501.114(C)(2)	Maintenance and Operation; Equipment: Quaternary ammonium compound (QAC)	solution greater than manufacturer’s recommended concentration in 3-compartment 	sink

Warmers

FC 4-501.11(A)	Maintenance and Operation, Equipment: Equipment not maintained in a state of good 	repair, lock damaged on warmer unit

Back Area-Officer’s Area

FC 6-202.15(A)(3)*	Design, Construction, and Installation; Functionality: Outer door not weather and 	vermin tight

Inmate Bathroom

No Violations Noted

Staff Bathroom

FC 6-101.11(A)(1)*	Materials for Construction and Repairs: Surface not easily cleanable, handwash sink 	water worn

FC 6-501.11*	Maintenance and Operation; Repairing: Facility not in good repair, heating pipes not 	insulated properly

Maintenance Building 4

Tool Crib

No Violations Noted

Paint Room

No Violations Noted

Bathroom in Office

No Violations Noted

Inmate Bathroom

105 CMR 451.331	Radiators and Heating Pipes: Pipes not properly insulated

Staff Bathroom

105 CMR 451.110(B)	Hygiene Supplies at Toilet and Handwash Sink: No waste receptacle at handwash sink

105 CMR 451.123	Maintenance: Vent fan dirty

Break Room

FC 4-501.11(B)	Maintenance and Operation, Equipment: Equipment components not maintained in a 	state of good repair, kick plate missing from refrigerator unit

FC 3-501.16(B)	Limitation of Growth of Organisms, Temperature and Time Control: Refrigerator 	temperature recorded at 450F

Power Plant 3

Bathroom

105 CMR 451.110(B)	Hygiene Supplies at Toilet and Handwash Sink: No waste receptacle at handwash sink

105 CMR 451.130	Hot Water: Shower water temperature recorded at 1160F

Break Room

105 CMR 451.130	Plumbing: Plumbing not maintained in good repair, faucet leaking

Vehicle Trap	The trap was not inspected at the time of inspection due to inclimate weather

Observations and Recommendations

- Although there is still damage to the ceilings in the cottages, overall they look much improved from the pervious inspections

- Violations in the refrigerator in the Culinary Arts Kitchen were addressed at the time of inspection

- Please provided documentation confirming that all blankets supplied to inmates are fire retardant in accordance with 105 CMR 451.101

This facility does not comply with the Department’s Regulations cited above. In accordance with 105 CMR 451.404, please indicate next to each entry on the inspection report a plan of correction. Said plan of correction must be submitted within ten working days of receiving this report and should detail the specific steps that will be taken and the date of expected compliance. The plan of correction should be submitted to my attention, at the address listed above.

To review the specific regulatory requirements please visit our website at www.mass.gov/dph/dcs and click on "Community Sanitation Regulations" (available in both PDF and RTF formats).

To review the Food Establishment regulations please visit the Food Protection website at www.mass.gov/dph/fpp and click on “Food Protection Regulations”. Then under “Retail” click “105 CMR 590.000 - State Sanitary Code Chapter X – Minimum Sanitation Standards for Food Establishments” and “1999 Food Code”.

This inspection report is signed and certified under the pains and penalties of perjury.

Sincerely,

Lauren Thomas

Environmental Health Inspector, CSP, BEH

cc:	Suzanne K. Condon, Associate Commissioner, Director, BEH

Steven Hughes, Director, CSP, BEH

JudyAnn Bigby, MD, Secretary, Executive Office of Health and Human Services

Harold W. Clarke, Commissioner, DOC

Pamela Britt, EHSO

Framingham Board of Health

Clerk, Massachusetts House of Representatives

Clerk, Massachusetts Senate

Kevin M. Burke, EOPS