INDOOR AIR QUALITY WALKTHROUGH

Michael E. Smith Middle School

100 Mosier Street

South Hadley

May 2026

Prepared by:

Massachusetts Department of Public Health

Bureau of Climate and Environmental Health

Division of Environmental Health Regulations and Standards

Contents

EXECUTIVE SUMMARY	3

BACKGROUND	5

RESULTS AND DISCUSSION	5

Ventilation	5

Water Damage and Moisture Concerns	8

Sources of Respiratory Irritants/Possible Asthma Triggers	10

Other IAQ Issues	12

CONCLUSIONS AND RECOMMENDATIONS	13

REFERENCES	18

FIGURES	20

PICTURES	21

Table 1	39

Table 2A	44

Table 2B	45

Table 2C	46

Table 3	47

Table 4	49

# EXECUTIVE SUMMARY

The Massachusetts Department of Public Health’s (MDPH), Division of Environmental Health Regulations and Standards (EHRS) conducted an Indoor Air Quality (IAQ) walkthrough of the Michael E. Smith Middle School located at 100 Mosier Street, South Hadley, on May 8, 2026. This walkthrough was in conjunction with the “Asthma in Schools: Data to Action Project” - a collaboration between Massachusetts Department of Public Health programs, local health departments, and local school health and administration officials to support asthma prevention and intervention efforts in school settings, see https://www.mass.gov/asthma-in-schools-data-to-action-project.

Any building can have IAQ issues. These issues can be made worse through conditions common to marginalized communities (Environmental Justice communities or EJ) such as inequitable exposure to outdoor air pollution and a greater likelihood of poor building conditions leading to deterioration of IAQ resulting in higher asthma rates. The Smith Middle School is not located within an EJ community, but there are EJ census blocks in South Hadley that this school draws from. Note that the pediatric asthma rate for this school as of 2024-2025 is 21%, which is statistically significantly higher than the statewide pediatric prevalence rate of 9.6% (MAEPHT, 2026).

The assessment was conducted by evaluating several key elements within the school; a visual inspection of the heating, cooling, and ventilating (HVAC) systems, water/microbial damage, exterior building envelope evaluation, cleanliness, and point sources of respiratory irritants such as chemicals. Data is collected in this manner to identify potential asthma triggers, allergens, and other environmental factors that can cause indoor air quality symptoms.

As a result of this walkthrough, there are several findings: at approximately 60 years old with additions added around 26 years ago, this school is generally in good condition. As building systems age, appropriate preventive and regular maintenance will help to keep school systems operating well into the future. Note that some water-stained/bowing ceiling tiles were found, and there are occupant-induced issues including storage/clutter, partially blocked unit ventilators and items placed in front of or near exhaust vents. (Results and Discussion), (Conclusions)

Based on the results of the assessment, the following primary recommendations are made:

- Operate supply and exhaust ventilation continuously when the building is occupied. Check unit ventilators air handling units, and exhaust vents during occupied periods to ensure they are on and operating to their full capacity.

- Educate teachers and staff on the operation of unit ventilators and exhaust vents so they can avoid blocking units and can report off or inoperable units to facility staff. If not already in use, consider using a tracking program to collect and administer work orders for mechanical systems.

- Address building envelope issues leading to water infiltration and damaged building materials in the building. Replace water-damaged ceiling tiles and clean/repair any other water-damaged materials.

- Reduce clutter and sort stored materials regularly to remove items that are outdated or no longer needed. Store items neatly and off the floor.

- Cut grass, flowers, and tree branches near uninvent fresh air intakes on the exterior of the building.

Note that this building was visited by the IAQ unit in 2017. The report from that visit can be found at https://www.mass.gov/info-details/indoor-air-quality-reports-cities-and-towns-s#south-hadley along with other IAQ reports. Also note that this report contains a series of recommendations that should serve as Best Practices that apply to most public-school buildings across the Commonwealth and should be shared amongst other buildings in the school district.

# BACKGROUND

| Building: | Michael E. Smith Middle School (MESMS) |
| --- | --- |
| Address: | 100 Mosier Street, South Hadley, MA |
| Coordinated Via: | Melissa Bednarski, Director of Health Services, South Hadley Public Schools |
| Reason for Request: | Pediatric Asthma Project and General IAQ |
| Date of Assessment: | May 8, 2026 |
| Massachusetts Department of Public Health/Bureau of Climate and Environmental Health/Division of Environmental Health Regulations and Standards (MDPH/BCEH/EHRS) staff | Ruth Alfasso and Thomas Murphy, IAQ Outreach and Education Unit, EHRS |
| Building Description: | The MESMS is a two-story, red-brick building originally built in the 1960s. Additions were built in 1999-2000. The school originally had an indoor swimming pool, but this facility has been drained and is no longer used. |
| Windows: | Most windows in the school are openable. |

# RESULTS AND DISCUSSION

A summary of conditions observed during the indoor air quality walkthrough can be found in (Table 1).

## Ventilation

Ventilation refers to both the supply of fresh air and the removal of stale air from a room. The introduction of fresh air into an occupied space will dilute normally occurring pollutants that are generated by occupancy and other activities. In addition, an HVAC system will remove pollutants from a building if operating appropriately. All ventilation systems throughout the building should operate continuously during periods of occupancy.

Fresh air ventilation for the MESMS comes from a combination of unit ventilators (univents) in classrooms (Picture 1), and air handling units (AHUs) located on the roof (Picture 2) and in mechanical areas. Air from AHUs is filtered and heated/cooled and supplied to rooms via ceiling-mounted vents (Pictures 3 and 4). Only some of the AHUs provide air cooling/conditioning.

Univents draw air in from a vent on the exterior of the building (Picture 5), filter it, heat it, and provide it to the classroom through a vent on the top (Figure 1). Air is returned to the univent through a vent at the bottom. Note that some univents are located on the ceiling of rooms.

Classrooms and other rooms are also equipped with exhaust vents located on walls or the ceiling that remove stale air from rooms via rooftop exhaust motors (Pictures 6 and 7).

The HVAC equipment in the building is controlled by a centralized energy management system. There are sensors in each room which feed into this system. The IAQ Outreach and Education unit recommends that occupied rooms be supplied with continuous fresh air.

The various types of ventilation components as well as devices that can move/redirect airflow are listed in Table 2A, Table 2B and Table 2C.

### HVAC System Maintenance

- According to the American Society of Heating, Refrigeration, and Air-Conditioning Engineering (ASHRAE), the service life of the types of HVAC equipment present in the school is 15-20 years, assuming routine maintenance of the equipment (ASHRAE, 1991). Equipment in the school installed during the 2000-era renovations is just past its service life. Routine maintenance and sourcing compatible parts will become increasingly difficult as the systems age.

Balancing

To have proper ventilation with a mechanical supply and exhaust system, a system must be balanced to provide an adequate amount of fresh air to the interior of a room while also removing stale air from the room.

It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).

At the time of the visit, maintenance and upgrades were being performed on building management systems, therefore some of the ventilation equipment, such as univents and exhaust vents in some rooms, were observed to be off (Table 1).

### HVAC Types and Specific Conditions

Fresh Air Ventilation:

- Some univents were blocked by furniture or items (Picture 8). This can restrict the flow of fresh air and air circulation in the building. The vents on top and the bottom need to be kept clear of obstructions.

- The IAQ Outreach and Education Unit recommends that filters of at least a minimum efficiency reporting value (MERV) 8 or better be used, if an HVAC engineer confirms the system can be so equipped without adversely affecting function, as these are adequate to filter out pollen, mold, and similar particulates (ASHRAE, 2012).

  - AHUs were equipped with filters that were rated MERV 10 (Picture 9)

  - Univents were equipped with filters that were rated MERV 8 (Picture 10)

Exhaust vents:

- Most of the wall-mounted exhaust vents that were tested were on and operated strongly. A few, however, were not drawing (Table 1). This is most likely due to the upgrades being made to building management systems.

  - Many exhaust vents were dusty (Table 1; Pictures 6 and 11). This is a sign that they are operational, since dust accumulates through the action of the vent drawing air. However, dust should be cleaned periodically because it can become aerosolized and lead to irritation, or, if moistened, could become moldy,

  - Some wall exhaust vents were noted to be blocked by items or furniture (Picture 12; Table 1). It is important to keep exhaust vents as clear as possible for stale air to be ejected out of the classroom.

Additional HVAC Conditions:

- Most classrooms have openable windows (Table 1). Windows can potentially be used for additional fresh air during temperate weather.

  - Windows should be kept closed during wet weather to prevent water infiltration.

  - They should also be kept closed when air conditioning is operating to prevent condensation and mold growth during periods of elevated relative humidity.

  - Occupants should be aware of outdoor air quality and avoid opening windows during days with poor air quality, high pollen, outdoor noise, or when gas-fired equipment is operating near the windows.

  - When not in use, windows should be closed tightly and locked.

- Mini-split (also called ductless) air conditioners were present in a few rooms, including a former computer learning room (Picture 13). These units circulate cool air (sometimes they also provide heat), but do not supply fresh air. These units produce condensation which needs to be drained. Mini-splits need to be cleaned regularly to prevent odors.

- Window air conditioners were present in some classrooms (Table 1; Picture 14). These units may provide a small amount of fresh air when used. They have a filter that needs to be cleaned periodically.

- Specialized exhaust vents were found in the Home Ec kitchen, for the art room kiln, and in a few other areas. These task-based exhaust vents need to be used every time the associated equipment is used to remove odors, excess heat, and fumes.

- No supply or exhaust ventilation was noted in the maintenance shop room. While this room has an overhead and regular door to the outside, doors cannot be used during inclement weather, and staff are discouraged from opening these doors due to security concerns. Activities performed in this area may include spraying products such as lubricants and cutting various materials. These activities may produce odors and irritating or harmful fumes. Exhaust ventilation, with an appropriate amount of make-up air, is needed to ensure a healthy environment for maintenance personnel using this room.

- Air purifiers were noted in some classrooms and offices (Picture 15). It was reported some staff no longer use their air purifiers which were provided to them during the height of the COVID-19 pandemic. Air purifiers with HEPA filters are good choices to remove particulates from the air that may include dust, pollen, mold spores, and microbes. Air purifiers that may produce ozone should not be used. Air purifiers should be maintained in accordance with manufacturers’ instructions, including cleaning and filter changes.

- The pool room has a specialized ventilation system that is still in use despite the pool being empty and closed. The pool system is designed to move large amounts of air and also control humidity.

## Water Damage and Moisture Concerns

Molds are found naturally in our environment both indoors and outdoors. Inside, mold growth may occur when items, particularly porous products such as paper or gypsum wallboard, are exposed to moisture. Typical water sources include leaks, floods, and condensation. To avoid mold growth, dry all water-damaged items and affected areas within 24-48 hours and reduce indoor humidity. Some people with chronic respiratory conditions, such as asthma, are more likely to experience health symptoms associated with molds, including allergic reactions and respiratory irritation. Controlling moisture is the key to preventing mold growth and potential health symptoms.

Mold Growth

Porous materials (e.g., gypsum wallboard, ceiling tiles and carpeting) can be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2008).

If porous materials are not dried within this time frame, mold growth may occur.

Hot humid summers are becoming more frequent due to climate change. Massachusetts has experienced hot, humid, and rainy summers in 2018, 2021, and 2023. July of 2021 was the wettest ever recorded in Massachusetts, and the three-month period from June through August, known as the meteorological summer, was the fourth wettest on record, according to the National Oceanic and Atmospheric Administration’s (NOAA) Centers for Environmental Information (NOAA, 2021). The summer of 2023 was measured as the second rainiest on record (WBUR, 2023). The summers of 2024 and 2025 also had significant stretches of hot, humid weather. These conditions are challenging for buildings, even those with central air conditioning.

Please note that the IAQ Outreach and Education Unit does not recommend conducting mold testing in a typical water damage remediation. For details, please consult Guidance Regarding Testing for Mold in Water-Damaged Public Buildings | Mass.gov

The application of a mildewcide to moldy porous materials is not recommended.

During these hot and wet summers, extended periods of outdoor relative humidity above 70% occurred. Public buildings experienced extended periods of water vapor exposure from high relative humidity. When exposed to these conditions, porous materials such as gypsum wallboard, cardboard, and other materials may become mold colonized, particularly if located in areas that are prone to developing condensation (e.g., floors and walls in below grade space).

Water-damaged ceiling tiles were found in a few locations (Pictures 16 and 17; Table 1), which can indicate plumbing, HVAC, or building envelope leaks. Water-damaged ceiling tiles can provide a source of mold and should be replaced after a water leak is discovered and repaired. Staff are encouraged to report any active leaks to the Facilities Department for prompt remediation. None of the water-damaged tiles had the characteristic dark or fuzzy staining indicating mold growth.

- Plants and cut flowers were noted in some classrooms and offices (Pictures 18 and 19; Table 1). Plants can be a source of pollen or mold especially if overwatered or not well maintained. Plants without drip pans can damage porous surfaces they are placed on. Plants should also not be located in the airstream of ventilation equipment (e.g., Picture 19) to prevent the spread of pollen or mold.

- There are sinks in classrooms, offices, and other areas (Table 1).

  - Some sinks may not be used often, Sinks and floor drains (e.g., for eye wash stations) that are not used often can have the plumbing trap dry out, which allows sewer gases into occupied areas. Pouring water down seldom-used sinks every few weeks will keep the trap seal intact.

  - Some sinks in the Home Ec kitchen had gaps between the sink cabinet and the backsplash (Picture 20). This can allow water to penetrate and further damage material and will be difficult to keep clean. Some backsplashes had already been repaired with caulking.

  - The cabinet under the sink is a damp area. Porous items or an excess of items should not be stored in there.

- Eyewashes and emergency showers were present in some science classrooms. These need to be inspected periodically to prevent leaks. No items should be stored near these units in case they need to be activated. Care should be taken during testing that water is contained and cleaned up.

- Damaged, loose coving was noted in a science classroom in a corner near an exterior wall (Picture 21). This is a sign that water damage has occurred here in the past. Maintenance should peel the coving up to check for additional water damage underneath, and seal it back on once the wall is clean and dry.

- A few dehumidifiers were noted in the building (Picture 22). Dehumidifiers are helpful to remove excess humidity before it can lead to comfort issues or condensation.

  - Dehumidifiers need to be emptied regularly or drained into a sink/floor drain and cleaned periodically to remove stagnant water and any build-up that can lead to odors.

  - One unit had a display that read 35, indicating 35% relative humidity. The guidance used by the IAQ unit is that relative humidity between 40% and 60% is most likely to be comfortable. Reducing humidity too low can cause discomfort due to dry air.

- In some classrooms and hallways, ceiling tiles were found to be bowed or sagging slightly in the ceiling tile grid (Table 1). Bowed ceiling tiles are a sign of long-term water vapor exposure, which causes sagging due to the weight of water in the ceiling tile and its effect on binders that hold the tile intact. This is a sign of exposure to high humidity over a long period of time. While bowed ceiling tiles are not themselves an air quality issue, so long as the tiles are still secure in the ceiling, it is an indication that humidity issues may continue to occur. Particular care regarding porous items during humid weather should be taken in rooms with bowed ceiling tiles.

- This school had previously had issues with floor damage including floor tile mastic coming up between tiles. This was traced to a problem with a lack of vapor barrier beneath the floor and has since been repaired. This was also an issue addressed in the 2017 DPH IAQ report.

- Window condensation was noted between windowpanes in a few areas (Picture 23). This is a sign that the insulating seal between panes has failed and these windows will not insulate as well as those in which the seals are intact.

- The Guidance Preventing Mold Growth in Hot Humid Weather and Remediation and prevention of mold growth and water damage in public schools and buildings to maintain air quality can be used for help with excess humidity.

An exterior evaluation was also conducted to identify potential pathways for water penetration and pest entry. The following issues were found:

- Some exterior doors had light visible beneath them (Picture 24), indicating gaps which can allow unconditioned air, moisture, odors, or pests inside.

- Plants and trees were close to the building, including in courtyards, some of which were overgrown (Pictures 25 through 27). Plants next to the building can hold moisture against the exterior, encourage pests, and be a source of pollen and odors through open windows and uninvent fresh air intakes.

- Bird houses were also noted. Bird waste can be a source of odors, bacteria and mold, and birds may carry mites that can enter occupied spaces. Bird houses should be moved away from the building, and nests on building materials should be removed.

- A small amount of efflorescence (mineral salts from brick) and damage to exterior brickwork was noted (Picture 28), however most of the building exterior was in good condition.

A list of water damage issues identified and included as Table 3.

## Sources of Respiratory Irritants/Possible Asthma Triggers

Asthma is a lung disease that can make breathing difficult. Without careful management of asthma, some individuals can have symptoms, like a tight feeling in the chest, shortness of breath, coughing, or wheezing. Although there is no cure for asthma, individuals with asthma can live healthy, active lives. A safe and healthy environment helps to reduce asthma symptoms.

Comparison of Local and State-wide Asthma Rates (2024-2025 school year/MAEPHT, 2026)

17.6% of children have asthma

South Hadley

9.6% of children

have asthma

Massachusetts

21% of children

have asthma

M. E. Smith School

- Sometimes, learning tools and personal items in a classroom can be a source of irritation. For example, a bird or insect nest is a great learning tool for students but may harbor microbes and allergens. Similarly, food-based projects can attract pests that carry disease or trigger allergies.

- Personal products, particularly those with volatile organic compounds (VOCs) including scents, can also be a source of respiratory irritation. VOCs are carbon-containing substances that have the ability to evaporate at room temperature. Frequently, exposure to low levels of total VOCs (TVOCs) may produce eye, nose, throat and/or respiratory irritation in some sensitive individuals. Products noted were dry erase markers, hand sanitizers, other cleaning/sanitizing products, and air fresheners (Picture 29; Table 1). Consult “Clean Air Is Odor Free” for more information on fragrances in schools and other buildings.

- Dust, a common respiratory and eye irritant, can collect on surfaces and items. Although janitorial and maintenance staff perform routine cleaning in classrooms, they may not be able to clean as effectively if classroom items are not picked up or surfaces are cluttered.

- At least one broom and a fan in a classroom had accumulated a significant amount of dust (Pictures 30 and 31; Table 1). Brooms and fans should be cleaned on a consistent basis, and the use of a HEPA vacuum and wet wiping is preferred to minimize the reaerosolization of dust. This dust can also be a medium for mold growth.

For guidance on maintaining an asthma-friendly healthy school environment, please consult the MDPH Asthma Prevention and Control Program’s Clearing the Air: An Asthma Toolkit for Healthy Schools.

Possible asthma triggers and/or airborne pollutants exist in the building. These are listed below as well as in (Table 4).

- A few classrooms and storage areas had an excess of items such as books, craft materials, papers, boxes, and miscellaneous materials (Picture 32 and 33). Excess items can accumulate dust and make it difficult for custodial staff to clean. Items should be relocated and/or be cleaned periodically to avoid excessive dust build up. In addition, dust and debris can accumulate on flat surfaces (e.g., desktops, shelving and carpets) in occupied areas and subsequently be re-aerosolized causing further irritation.

- Break rooms around the school and some classrooms and offices have food storage and preparation equipment such as refrigerators, microwaves, and toasters. Some of this equipment was dirty (Picture 34; Table 1). Food spills and crumbs can be a source of odors, especially when heated, and can attract pests.

  - While these refrigerators are not covered by the food code, it is good practice to have a thermometer in each refrigerator that is visible to ensure refrigerated food temperatures are kept at 5ºC (41ºF) or less (US FDA, 2022).

  - All food should be stored in closed, pest-proof containers (e.g., glass or hard plastic) when not in use.

- Some classrooms had area rugs, pillows/cushions, upholstered furniture, and wall hangings (Table 1). These need to be cleaned regularly to remove dust, debris, and odors. Area rugs should be stored off the floor in a climate-controlled area during the summer to prevent moistening by condensation. Used area rugs should not be brought into the school as they may harbor allergens such as pet dander.

- Cloth was covering lights in some areas (Picture 35). These coverings should be made of fire-retardant materials made for this purpose. Any cloth coverings should be laundered periodically and removed during summer break.

- The Home Ec kitchen has many stoves, two of which are gas-fired. Although the room has exhaust ventilation, no vent hoods are present over the stoves. All cooking may create odors, particulates, and other fumes. Use of gas stoves is more likely to create carbon monoxide and nitrogen dioxide. Cooking should be done with good ventilation. Using only the electric stoves will reduce products of combustion present with burning natural gas.

- Natural gas lab valves are present in some science classrooms. These are reportedly turned off at the room source and not used. Piping for these units should be checked periodically to avoid any gas leaks.

- Laminators were observed in at least one location. Laminators melt plastic and produce fumes and odors. They should be used with good ventilation.

- Tennis balls were used as chair glides in a few areas (Table 1). Tennis balls are made of materials that may be a source of respiratory irritants. Constant wearing of tennis balls can produce fibers and off-gas VOCs. Tennis balls are made with a natural rubber latex bladder, which becomes abraded when used as a chair leg pad. Use of tennis balls in this manner may introduce latex dust into the school environment. Some individuals are highly allergic to latex (e.g., spina bifida patients) (SBAA, 2001). It is recommended that the use of materials containing latex be limited to reduce the potential for symptoms in sensitive individuals (NIOSH, 1997). Latex-free glides should be used for this purpose.

- An anti-idling sign was posted in the front of the school (Picture 36). Vehicle exhaust is an asthma triggering pollutant and anti-idling should be strongly enforced. Refer to idling-faq for more information.

## Other IAQ Issues

Radon

Radon is a naturally occurring radioactive gas that seeps into buildings from the surrounding soil and can increase the risk of lung cancer at elevated levels.

The Environmental Protection Agency (EPA) conducted a National School Radon Survey “in which it discovered nearly one in five schools has at least one schoolroom with a short-term radon level above the action level of 4pCi/L (picocuries per liter) – the level at which the EPA recommends that schools take action to reduce the level” (US EPA, 1993).

The MDPH therefore recommends that every school be tested for radon, and that this testing be conducted during the heating season while school is in session in a manner consistent with US EPA radon testing guidelines. Radon measurement specialists and other information can be found at www.nrsb.org and http://aarst-nrpp.com/wp, with additional information at: https://www.mass.gov/radon and fact sheet on radon in schools and child care programs.

# CONCLUSIONS AND RECOMMENDATIONS

Please note: this report contains a series of recommendations that should serve as Best Practices that apply to most public-school buildings across the Commonwealth and should be shared amongst other buildings in the School District.

Short-term recommendations can be implemented as soon as practicable, however long-term measures are more complex and will require planning and resources to adequately address overall indoor air quality issues within the building.

Short-term Recommendations

HVAC System					       Helpful Links

| - 1. | Ensure proper operation of all AHUs, univents, and other HVAC systems. |  |
| --- | --- | --- |
| - 2. | Remove blockages from the top/front of univents, exhaust vents, and radiators. including furniture and items. |  |
| - 3. | Periodically check the function of all classroom and restroom exhaust vents. Repair as needed. |  |
| - 5. | Continue with regular filter changes for HVAC equipment using a minimum efficiency rating value (MERV) 8 or the best quality/highest MERV-rated filter that can be used without effecting airflow. Ensure filters fit flush within their racks to prevent filter bypass. | ANSI/ASHRAE Standard 52.2-2017 |
| - 6. | During filter changes, clean dust and debris from the inside of univent and AHU cabinets. |  |
| - 7. | Develop and communicate a policy on when openable windows can be used. Tightly close windows at the end of the day and avoid opening windows during extreme cold to prevent freezing of pipes. Keep windows closed when it is hot and humid, outdoor air quality unhealthy, during heavy traffic conditions, or when the generator is operating. | https://www.airnow.gov/ |
|  | Clean and maintain mini-split air conditioners including ensuring condensation is draining properly in accordance with manufacturers’ instructions. |  |
|  | Clean filters on window air conditioners regularly. Ensure they are sealed into windows with water-resistant material. |  |
|  | Ensure task-based exhaust is used for Home Ec kitchens, the kiln, and other uses, whenever the associated equipment is in use. |  |
|  | Consider adding exhaust ventilation and fresh make-up air to the maintenance shop to reduce odors, particulates, and fumes from activities in this area. |  |
|  | Portable air purifiers may also be used to supplement mechanical ventilation filtration. | https://ww2.arb.ca.gov/list-carb-certified-air-cleaning-devices https://www.epa.gov/indoor-air-quality-iaq/ozone-generators-are-sold-air-cleaners |
|  | Continue to operate the pool ventilation system until more permanent plans for the pool have been determined. |  |
| Water Damage Sources |  |  |
| - 9. | Replace water-damaged ceiling tiles. Repeated water damage to ceiling tiles indicates leaks from the roof or plumbing/HVAC system which should be repaired. | http://www.epa.gov/mold/mold-remediation-schools-and-commercial-buildings-guide |
| - 10. | Properly maintain plants to avoid mold and odors. Keep plants away from airflow of HVAC equipment. |  |
|  | Pour water periodically (every week or two) down sinks and floor drains that are not often used to maintain the trap seal and prevent sewer gases from entering occupied areas. |  |
|  | Repair sink backsplashes in the Home Ec kitchen. |  |
|  | Avoid storing porous materials or large amounts of materials under sink cabinets. |  |
|  | Inspect eyewash stations and safety showers periodically and avoid storing any porous materials near them. |  |
|  | Repair damaged coving shown in Picture 21. |  |
|  | Continue to use dehumidifiers when indoor humidity is high. Clean and maintain the units to prevent stagnant water and odors. Ensure units do not reduce humidity too far, especially during cold weather. |  |
|  | Use information from the new building maintenance system to monitor humidity levels in the school and to help manage the potential for condensation during humid weather. | https://www.mass.gov/info-details/preventing-mold-growth-in-massachusetts-schools-during-hot-humid-weather and Remediation and prevention of mold growth and water damage in public schools and buildings to maintain air quality |
| - 20. | During summer months, pull furniture away (1 to 2 inches) from walls to prevent mold growth due to lack of airflow and remove impermeable wall coverings that can trap moisture such as laminated posters. |  |
|  | Ensure exterior doors fit tightly with no gaps. Repair or replace weatherstripping where needed. |  |
|  | Trim plants and trees from the building exterior including the courtyards and near uninvent fresh air intakes. |  |
| Respiratory Irritants/Possible Asthma Triggers |  |  |
| - 23. | Reduce use of products and equipment that create irritating volatile organic compounds (VOCs) and only use in well-ventilated areas. Minimize the use of air fresheners (e.g., plug-ins), deodorizers and scented products. | https://www.mass.gov/cleaner-greener-healthier-schools and Clean Air Is Odor Free |
| - 33. | Use only District-approved cleaning products. Keep spray bottles properly labeled and out of the reach of children. |  |
| - 34. | Provide exhaust ventilation or move copiers and laminators to a well-ventilated area with an exhaust vent. |  |
| - 26. | Clean area carpets, upholstered furniture, cushions/pillows frequently using a HEPA-equipped vacuum cleaner. Avoid bringing used area rugs into the school. |  |
|  | Clean carpeting regularly in accordance with IICRC recommendations (IICRC, 2012). |  |
| - 27. | Periodically, sort classroom and other storage areas for removal of unwanted items. Store the remaining items neatly and off the floor. |  |
| - 28. | Clean personal fans, supply, and exhaust/return vents periodically to remove dust and debris. |  |
| - 31. | Ensure the principles of integrated pest management (IPM) are followed in accordance with state regulations. | https://massnrc.org/ipm/docs/ipmkitforbuildingmanagers.pdf |
|  | Ensure food preparation equipment is kept clean to prevent smoke, odors, and pests |  |
|  | Keep all food in tightly-closed pest-proof containers. |  |
|  | Clean upholstered furniture, plush items, and wall hangings regularly to remove dust and odors. |  |
|  | Replace tennis balls with latex free glides. |  |
|  | Continue to enforce no idling next to the building. |  |

Other Recommendations to Improve Air Quality Conditions

| - 35. | Test the school for radon by a certified radon measurement specialist during the heating season when school is in session. | Radon measurement specialists and other information can be found at: www.nrsb.org, and http://aarst-nrpp.com/wp |
| --- | --- | --- |
| - 36. | To learn more about radon, review the MDPH’s Radon in Schools and Child Care Programs factsheet. | https://www.mass.gov/info-details/radon-in-schools. |
| - 37. | Utilize the US EPA’s (2000), “Tools for Schools” as an instrument for maintaining a good IAQ environment in the building. | https://www.epa.gov/iaq-schools. |
| - 38. | For guidance on maintaining an asthma-friendly healthy school environment, please consult the MDPH Asthma Prevention and Control Program’s Clearing the Air: An Asthma Toolkit for Healthy Schools. | https://www.maasthma.org/schooltoolkit |
| - 39. | Include an IAQ component in the school’s Wellness Advisory Committee program. An IAQ plan should have an IAQ liaison/teacher representative, a member of maintenance/facilities and administration that conduct regular walk-throughs to identify on-going and/or potential environmental issues. |  |

Long-term recommendations

|  | Consider options for decommissioning or reusing the pool section of the building. |  |
| --- | --- | --- |
|  | Consider installing sensor technology in classrooms to provide continuous monitoring of the following indoor air parameters (particularly temperature and relative humidity). Sensors should be re-calibrated quarterly or according to manufacturers’ specifications and building management software updated as per manufacturers’ instructions, industrial standards, and/or change in operating systems. As an example, the link to the right illustrates how this technology is serving Boston Public Schools to improve air quality (i.e., carbon dioxide, temperature, relative humidity, carbon monoxide, and particulate matter). | COVID-19 Health & Safety Information / Indoor Air Quality Sensor Dashboard (bostonpublicschools.org) |
|  | Consider replacing gas stoves in the Home Ec kitchen with electric stoves and installing exhaust hoods over stoves. |  |

# REFERENCES

ASHRAE. 1991. ASHRAE Applications Handbook, Chapter 33 “Owning and Operating Costs”. American Society of Heating, Refrigeration and Air Conditioning Engineers, Atlanta, GA.

ASHRAE. 2012. American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) Standard 52.2-2012 -- Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size (ANSI Approved).

IICRC. 2012. Institute of Inspection, Cleaning and Restoration Certification. Carpet Cleaning: FAQ.

MAEPHT. 2026. Massachusetts Environmental Public Health Tracking. Massachusetts Department of Public Health – Bureau of Climate and Environmental Health. https://matracking.ehs.state.ma.us/

NIOSH. 1997. NIOSH Alert Preventing Allergic Reactions to Natural Rubber latex in the Workplace. National Institute for Occupational Safety and Health, Atlanta, GA.

NOAA. 2021. Summer 2021 neck and neck with Dust Bowl summer for hottest on record. National Oceanic and Atmospheric Administration, 1401 Constitution Avenue NW, Room 5128, Washington, DC 20230 https://www.noaa.gov/news/summer-2021-neck-and-neck-with-dust-bowl-summer-for-hottest-on-record

SBAA. 2001. Latex In the Home And Community Updated Spring 2001. Spina Bifida Association of America, Washington, DC.

SMACNA. 1994. HVAC Systems Commissioning Manual. 1st ed. Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

US EPA. 1993. Radon Measurement in Schools, Revised Edition. Office of Air and Radiation, Office of Radiation and Indoor Air, Indoor Environments Division (6609J). EPA 402-R-92-014.

US EPA. 2000. Tools for Schools. Office of Air and Radiation, Office of Radiation and Indoor Air, Indoor Environments Division (6609J). EPA 402-K-95-001, Second Edition. https://www.epa.gov/iaq-schools.

US EPA. 2008. Mold Remediation in Schools and Commercial Buildings. US Environmental Protection Agency, Office of Air and Radiation, Indoor Environments Division, Washington, D.C. EPA 402-K-01-001. http://www.epa.gov/mold/mold-remediation-schools-and-commercial-buildings-guide.

US FDA. 2022. 2022 Food Code. U.S. Department of Health and Human Services. U.S. Food and Drug Administration. College Park, MD January 18, 2023 Version. https://www.fda.gov/media/164194/download

WBUR. 2023. “It's been a summer of rain and flooding misery in Mass.” WBUR local news. September 12, 2023. https://www.wbur.org/news/2023/09/12/summer-flooding-rain-massachusetts.

# FIGURES

Figure 1

Unit Ventilator (Univent)

Mixed Air

Air Diffuser

Outdoors								Indoors

Fan

Heating/Cooling Coil

Air Mixing Plenum

Filter

Outdoor										Return

Air										Air

Air

Flow

Control

Louvers

# Air Flow

=  Fresh Air/Return Air

=  Mixed Air

# PICTURES

## Ventilation Pictures

Picture 1

Typical classroom univent

Picture 2

Rooftop air handling unit, seen from window

Picture 3

Ceiling-mounted supply vent

Picture 4

Ceiling-mounted supply vent in the library

Picture 5

Exterior fresh air vent for univent

Picture 6

Wall-mounted exhaust vent, note dust

Picture 7

Ceiling-mounted exhaust vent

Picture 8

Items on top of univent in a classroom

Picture 9

MERV 10 air handling unit filter

Picture 10

Univent filter

Picture 11

Dusty exhaust vent

Picture 12

Exhaust vent blocked by shelf unit

Picture 13

Mini-split (ductless) air conditioning unit

Picture 14

Window air conditioner

Picture 15

Air purifier

## Water Damage Pictures

Picture 16

Water-damaged ceiling tile

Picture 17

Water-damaged ceiling tile

Picture 18

Plants in a classroom

Picture 19

Plants on a univent

Picture 20

Gap between sink and backsplash

Picture 21

Damaged loose coving

Picture 22

Dehumidifier in a classroom

Picture 23

Condensation between window panes

Picture 24

Light visible beneath exterior door

Picture 25

Plants and trees overgrown in a courtyard

Picture 26

Large trees near the building

Picture 27

Plants and flowers near univent air intake

Picture 28

Efflorescence and slight damage to bricks

## Sources of Respiratory Irritation Pictures

Picture 29

Liquid air freshener

Picture 30

Dusty broom in a classroom

Picture 31

Dusty personal fan in a classroom

Picture 32

Items in a classroom

Picture 33

Cluttered science storage area

Picture 34

Dirty microwave interior

Picture 35

Cloth over fluorescent light

Picture 36

No idling sign

# Table 1

| Room | Openable Windows | HVAC | Ventilation |  | Ceiling Tiles/Staining (Y or N) B = Bowed | Comments |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Supply | Exhaust |  |  |
| IT and staff workroom | N | Y | Y | Y |  | Fridge, NC |
| Nurse’s office | Y | Y | Y | Y |  | Restroom, sanitizers in attached restroom, sinks, fridge, NC |
| Main office | N | Y | Y | Y |  | Carpet, plants |
| Principal’s office | Y | Y | Y | Y |  | Carpet, DEM |
| Office within main office area | Y | Y | Y | Y | Y |  |
| 139 | N | Y | Y | Y | Y | NC, bean bags, fridge |
| School group | N | Y | N | Y |  | NC |
| Courtyards |  |  |  |  |  | Trees, plants, flowers, birdhouse, some trees/bushes close to walls |
| Band | Y | Y | Y | Y | B | NC, gap under door |
| Practice room | N | N | N | N |  | NC, items |
| Practice room | N | N | N | N |  | NC, floor dirty, DEM, instruments |
| Practice room | N | Y | N | Y |  | NC |
| Pool (empty) | N | Y | Y | Y |  | Pool is drained and unused, special pool HVAC system still used |
| Locker room | N | Y | Y | Y |  | Water shut off to this area unless needed for cleaning or drain filling |
| Greenhouse | Y | Y | N | Y |  | Big exhaust vents in wall with switch, soil and plants, sink |
| Stage | N | N | N | N | Y |  |
| Home Ec. Kitchen 113 | N, door | Y | Y | Y |  | Stoves, including 2 gas-fired ones, fridges, other cooking equipment, dishwashers, laundry, NC, some sink backsplashes have gaps, food |
| 111 | Y | Y | Y | Y | N | Plants |
| 112 | Y | Y | Y | Y |  | Cloth on lights, exhaust off |
| 106 | Y | Y | Y | Y |  | area mat, DEM, AP with cover off, food |
| 107 Art Room | Y | Y | Y | Y | N | Kilns |
| 104 sensory area | Y | N | N | N | Y | Area rug, seating balls, AC, radiator |
| 103 staff room | Y | Y | Y | Y | N | Window air conditioner, coffee maker, dirty microwave, laminator |
| 102 | N | Y | Y | Y |  | Carpet, DEM, PF |
| 100 library | Y | Y | Y | Y | Y | Old carpet, items on floor |
| Library office | N | Y | Y | Y | Y | AP, items on floor |
| 132 | Y | Y | Y | Y | Y | DEM, ductless AC, AF odor (no AF seen), the WD CT may be recent, temperature control issues |
| IT, and pH control | Y | Y | Y | Y |  | Missing ceiling tile, NC |
| 108 | Y | Y | Y | Y |  | NC, DEM |
| 122 | Y |  |  |  |  | Storage, sinks, pH tank, sand on floor |
| 115 | Y | Y | Y | Y |  | Sink, gas valves – all turned off at source, DEM, dehumidifier, eyewash |
| 123 | Y | Y | Y | Y |  | DEM, AP, NC, tennis balls on chair legs, exhaust vent dusty |
| 120 | Y | Y | Y | Y |  | DEM, NC, chalk |
| 121 | Y | Y | Y off | Y | Y | Univent off, hand sanitizer, cleaning wipes |
| 114 | Y | Y | Y | Y | Y | DEM, area rug, cloth on lights |
| 116 | Y | Y | Y | Y | N | Univent partially blocked, dusty personal fan, exhaust vent on wall partially blocked by shelf |
| 117 | Y | Y | Y | Y |  | NC, PFs, items, supply vent dusty |
| 118 | Y | Y | Y | Y |  | Dehumidifier “empty” light blinking |
| 119 | Y | Y | Y off | Y | N | Univent off, dusty broom |
| 125 | Y | Y | Y off | Y | N | Univent off, cleaning wipes |
| 127 | Y | Y | Y off | Y | Y | Univent off, uninvent partially blocked |
| 129 | Y | Y | Y | Y | N | Exhaust vent partially blocked by recycling container |
| 131 | Y | Y | Y | Y | N | Window air conditioner |
| 133 | Y | Y | Y | Y | Y | Cleaning wipes, Storage closet close to exhaust vent |
| 135 | Y | Y | Y | Y | Y | Partially blocked univent |
| 219 | Y | Y | Y | Y | B | Plants, DEM, NC, floor fan |
| 218 | N | N | N | N |  | Storage |
| 217 | Y | Y | Y | Y |  | NC, items, DEM |
| 215 | Y | Y | Y | Y | B | DEM, NC, chalk |
| 213 | Y | Y | Y | Y |  | DEM |
| 200 | Y | Y | Y | Y | N |  |
| 202 | Y | Y | Y | Y | N | Area carpet, air purifier, hand sanitizer |
| 204 | Y | Y | Y | Y | N | Air purifier, personal fan, cleaning wipes, exhaust vent partially blocked |
| 206 | Y | Y | Y | Y | N | Hole in ceiling tile |
| 212 | Y | Y | Y | Y | N | Window air conditioner |
| 214 | Y | Y | Y | Y | N |  |
| 216 | Y | Y | Y | Y | N | Personal fan, uninvent partially blocked |
| 2nd floor women’s restroom | N | Y | N | Y |  |  |
| 209 | N | N | N | N |  | Janitor’s storage, mop sink |
| 205 | Y | Y | Y | Y |  | Science sinks, gascocks (off at source), eyewash, WD coving exterior wall |
| 203 science storage | N | Y | N | Y | Y | Musty smell, items |
| 201 | Y | Y | Y | Y |  | Plants, eyewash, science sinks, bean bag chairs, DEM |
| 208 | Y | Y | Y | Y | Y (5) | Tennis balls on chair legs, NC, plant, PF |
| Women’s restroom | N | Y | N | Y |  | Chemical or air freshener odor |
| 224 | Y | Y | Y | Y |  | Chalk, plants, DEM, microwave |
| 222 | Y | Y | Y | Y |  | Conference/copy room, microwave dirty, window AC, small fridge – dirty, NC |
| 225 | Y | Y | Y | Y |  | Plants, DEM, NC |
| 223 | Y | Y | Y | Y |  | Reading resource - books |
| 221 | Y | Y | Y | Y | Y (2) | NC, plants, DEM, PF |
| 227 | Y | Y | Y | Y |  | NC, books, DEM, plush furniture/items |
| 229 | Y | Y | Y | Y |  | PF, dirty floor, chalk, DEM |
| 231 | Y | Y | Y | Y |  | NC, DEM, HS |
| 233 | Y | Y | Y off | Y | N | Univent off, cleaning wipes, plants on uninvent, exhaust vent partially blocked by storage closet |
| 232 | Y | Y | Y off | Y | N | Univent off, plants, air purifier, timer for exhaust vent |
| Room connecting 232 and 234 | N | Y | Y | Y | N | Accumulation of items/paperwork on/around sinks/counter, refrigerator |
| 234 | Y | Y | Y | Y | N | Plants, personal fan |
| 235 | Y | Y | Y off | Y | N | Univent off, personal fan |
| 236 | Y | Y | Y | Y | N | Dehumidifier, HVAC room |
| 220 | Y | Y | Y | Y |  | DEM, NC, dusty PF, plants |
| Gym | N | Y | Y | Y |  |  |
| Weight/exercise room | Y, Door | Y | Y | Y |  | Matting, concrete floor |
| Cafeteria | Y | Y | Y | Y |  | NC |
| Facilities shop room | N, doors | N | N | N |  | NC, concrete floor, overhead and other exterior doors, use of chemicals, cutting equipment, no HVAC or means to provide air conditioning or fresh air, difficult to keep doors open to provide fresh air due to potential safety concerns |

# Table 2A

| Equipment Present in Building (X = Yes) | Type of Heating/Cooling Ventilation Equipment | Fresh Air Supply (X = Yes) | Type of Location(s) | Air Filters Installed MERV Rating (1-15, U*) (X = Yes) | Comments |
| --- | --- | --- | --- | --- | --- |
| X | Univents | X | classrooms | 8 |  |
| X | Rooftop Air Handling Units | X | Common areas | 10 |  |
|  | Outdoor, Ground-Installed Air Handling Units |  |  |  |  |
|  | Attic/Crawlspace Air Handling Units |  |  |  |  |
|  | Ceiling-Mounted Air Handling Units (including inside plenum) |  |  |  |  |
|  | Basement/Crawlspace-Installed Air Handling Units |  |  |  |  |
| X | Mechanical Room-installed Air Handling Units | X | Some common areas | 10 |  |
|  | Fan Coil Units |  |  |  |  |
| X | Window-Mounted Air Conditioners | X | Various areas |  |  |
|  | Wall Louver-Controlled Gravity Air Supply |  |  |  |  |
| X | Windows |  | Classrooms, offices |  |  |
|  | Fan in window (blowing in) |  |  |  |  |
|  | Built in wall fan (switched) |  |  |  |  |
|  | Heat recovery ventilator unit |  |  |  |  |
|  | Energy recovery ventilator unit |  |  |  |  |
|  | Chilled Beam |  |  |  |  |
|  | Passive combustion supply vent in basement/boiler room |  |  |  |  |

*U = Filter Rating underdetermined due to inaccessibility during building visit

# Table 2B

| Equipment Present in Building (X = Yes) | Type of Exhaust Ventilation Equipment | Ducted To Outdoors (X = Yes) | Type of Location(s) | Comments |
| --- | --- | --- | --- | --- |
| X | Rooftop Motors/Fans | X | Classrooms and offices |  |
|  | Unit Exhaust |  |  |  |
| X | Ceiling Return Vent | X | Some rooms |  |
|  | Ceiling Return Vent, Plenum |  |  |  |
| X | Wall Return Vent | X | Some rooms |  |
|  | Kitchen Stove Hood |  |  |  |
| X | Restroom Exhaust Vent | X |  |  |
|  | Photocopier Exhaust Vent |  |  |  |
|  | Garage |  |  |  |
|  | Chemical Hood(s) |  |  |  |
|  | Locker Rooms |  |  |  |
|  | Showers |  |  |  |
|  | Clothes Dryers |  |  |  |
|  | Gas Water Heaters |  |  |  |
|  | Furnace-Flue to Chimney |  |  |  |
|  | Furnace/Boiler direct vent or power vent (no combustion air supply) |  |  |  |
| X | Kiln, Pottery | X | Art room |  |
|  | Dark Room |  |  |  |
|  | Generator Room |  |  |  |
|  | Wood Shop Dust Collector |  |  |  |
|  | Spray Paint Booths |  |  |  |
|  | Fan in window (blowing out) |  |  |  |

# Table 2C

| Equipment Present in Building (X = Yes) | Type of Equipment | Type of Location(s) | Comments |
| --- | --- | --- | --- |
| X | Floor Fans, pedestal | Classrooms |  |
| X | Floor Fans, portable | Classrooms |  |
| X | Air Purifier (HEPA, other) | Classrooms and offices |  |
|  | Floor heaters, portable |  |  |
| X | Refrigerators, Cold Beverage Vending Machines |  |  |
|  | Radiator, wall-mounted |  |  |
|  | Radiator, floor-mounted |  |  |
|  | Passive Vents (Wall/Door) |  |  |

# Table 3

| Found in Building X = Yes | Water-Damaged Materials, Building Components or Stored Materials | Location | Visible Microbial Growth? X = Yes | Musty odor detected? X = Yes | Comments |
| --- | --- | --- | --- | --- | --- |
|  | Books-other bound materials |  |  |  |  |
|  | Brick walls – broken, missing mortar |  |  |  |  |
|  | Brick walls – blocked weep holes |  |  |  |  |
|  | Cardboard boxes |  |  |  |  |
|  | Carpet tiles |  |  |  |  |
|  | Carpet - Area rugs |  |  |  |  |
|  | Carpet wall-to-wall |  |  |  |  |
|  | Ceiling tiles - affixed directly to ceiling surface |  |  |  |  |
| X | Ceiling tiles - bowing-in suspended ceiling | Some classrooms |  |  |  |
|  | Ceiling tiles - water-stained in splined ceiling |  |  |  |  |
| X | Ceiling tiles - water-stained in suspended ceiling | Classrooms, offices, common areas |  |  |  |
|  | Chairs - laminated |  |  |  |  |
|  | Cloth |  |  |  |  |
|  | Countertops (around sinks) |  |  |  |  |
|  | Curtains |  |  |  |  |
|  | Dust/debris within AHU, uninvent, HVAC, chilled beam units, etc. (WD through condensation, humidity, or leaks) |  |  |  |  |
|  | Efflorescence (i.e., mineral deposits) |  |  |  |  |
|  | Engineered woods - particleboard, plywood, Masonite |  |  |  |  |
|  | Flooring – loosened tiles |  |  |  |  |
|  | Flooring - wooden |  |  |  |  |
|  | Furniture - laminated |  |  |  |  |
|  | Furniture - upholstered |  |  |  |  |
|  | Gypsum wallboard - ceiling |  |  |  |  |
|  | Gypsum wallboard - restroom wall |  |  |  |  |
|  | Gypsum wallboard - interior wall |  |  |  |  |
|  | Gypsum wallboard – located on exterior wall |  |  |  |  |
|  | HVAC drain pan – lack of draining |  |  |  |  |
|  | HVAC filters |  |  |  |  |
|  | Insulation- attic (paper-backed) |  |  |  |  |
|  | Insulation - inside air handling unit |  |  |  |  |
|  | Insulation - on pipe(s) fiberglass |  |  |  |  |
|  | Insulation - on pipe(s) other/plaster-like material |  |  |  |  |
|  | Insulation - wall cavity |  |  |  |  |
|  | Insulation – ceiling plenum |  |  |  |  |
|  | Modular furniture – walls/cloth partitions |  |  |  |  |
|  | Musical instrument cases |  |  |  |  |
|  | Plaster ceilings |  |  |  |  |
|  | Records/files |  |  |  |  |
|  | Refrigerator - door gasket |  |  |  |  |
|  | Refrigerator - drip pan |  |  |  |  |
|  | Refrigerator - Interior surfaces |  |  |  |  |
|  | Room divider - ceiling-mounted, sliding |  |  |  |  |
| X | Sink backsplash | Home Ec kitchen |  |  |  |
|  | Sink under cabinet |  |  |  |  |
|  | Tables – laminated |  |  |  |  |
|  | Wallpaper |  |  |  |  |
|  | Wood - attic/roof materials |  |  |  |  |
|  | Wood - floor joists in basement ceiling |  |  |  |  |
|  | Wood - wall framing |  |  |  |  |
|  | Wood – windowsills |  |  |  |  |
|  | Wood - window-mounted air conditioner framing |  |  |  |  |
|  | OTHER |  |  |  |  |

WHAT ARE ENVIRONMENTAL ASTHMA TRIGGERS?

Asthma triggers are any chemical, pollutant, or allergen that can make your asthma worse. Asthma triggers can also be strong chemical smells, dust, or pets. Your asthma triggers may be different from those of other people. Not all asthma triggers affect people the same way. Environmental asthma triggers are found both indoors and outdoors. MDPH link: Asthma and Your Environment (mass.gov)

# Table 4

| Condition Present X = Yes | Possible asthma symptom-inducing environmental pollutant | Recommendation to reduce or eliminate the pollutant |
| --- | --- | --- |
| X | Water Damage and/or Mold (allergen) | Identify water source and repair to eliminate. Clean non-porous materials. Remove and replace porous materials susceptible to mold growth. Perform regular water damage assessments as a tool to ensure timely mitigation as needed. Use NIOSH water damage assessment protocol as a guide: NIOSH water damage assessment guideline. |
| X | Moistening of building components during hot, humid weather (>2 days in length) (mold, allergen) | Remove materials not dried in <2 days in a manner consistent with US EPA Mold Removal in Commercial Buildings guideline. Use dehumidification in occupied basement areas and other areas with chronic dampness. |
| X | Vegetation against exterior of building (water damage-mold) | Remove all vegetation preventing building exterior drying. Remove all vegetation capable of falling onto a building or depositing debris onto the roof. |
|  | Personal humidifiers (lack of proper maintenance) (pollutant and allergen) | Clean and maintain properly. Use distilled water to eliminate metal and water treatment odors. Maintain hydration by increasing water consumption. |
| X | Drains: Floor drains, Sink drains (abandoned use) Water bubblers (abandoned use) | If in use, pour water into drain at least twice a week. If not in use, seal the drain with an appropriate material in accordance with Massachusetts Plumbing Code (248 CMR 10.00). |
|  | Live Animals (turtles, gerbils, birds, rabbits, etc.) | Ensure cleanliness or remove animals from the location. |
|  | Improperly maintained aquariums and terrariums (allergen) | Maintain such equipment properly to eliminate odor. Discontinue use. |
| X | Plants and flowers (allergen and mold) | Keep indoor plants well maintained and not overwatered. Monitor for signs of mold and pests. Ensure water for cut flowers does not become stagnant. Ensure dried plant material is free of odors, mold, and pests and handled carefully If asthma risks are high, eliminate plants and flowers. |
|  | HVAC system moisture issues (mold, allergen) | Consult ASHRAE’s minimum standards for HVAC maintenance and inspection of commercial HVAC systems (https://www.ashrae.org/technical-resources/bookstore/standards-180-and-211). |
|  | HVAC system contaminant issues (allergen) | Consult ASHRAE’s minimum standards for HVAC maintenance and inspection of commercial HVAC systems (https://www.ashrae.org/technical-resources/bookstore/standards-180-and-211). |
|  | Indoor swimming pool odors outside of swimming pool (mold, chemical) | Maintain and operate pool HVAC systems to vent odors from building. Ensure locker room exhaust vents are operating during building hours. All doors leading to pool should be rendered airtight and be closed. |
| X | Pollen (allergen) | Recommend installation of MERV 8 or better filters if HVAC engineer confirms HVAC system can be so equipped without adversely affecting function. Cut grass after hours. Cut grass in a pattern to direct clippings away from exterior wall. Remove trees and shrubs from in front of windows and air intakes. |
|  | Dry air | Maintain hydration. Avoid overheating of air. |
|  | Dust mites (allergen) | Recommendation to remove non-official upholstered furniture, area rugs, pillows, cushions, etc. Cleaning with use of HEPA-filtered vacuum cleaner. Eliminating clutter, storing items in dust and moisture-proof containers, and regularly removing dust through wet wiping. |
|  | Pests, including rodents and cockroaches (allergen) | Use of integrated pest management guidelines, including: - Proper disposal of food containers - Proper storage of food products in airtight containers - Elimination of use of food as art projects - Remove pest harborages/clutter - Regular monitoring for pests EPA IPM guideline link |
| X | Latex-containing materials | Remove tennis balls from furniture legs or replace with latex free ones. |
| X | Fragrances (chemical) | Eliminate point sources, such as: - Plug-in air fresheners - Aroma/oil reed diffusers - Scented sprays - Discontinue use of other scented materials - Consult MDPH fragrance guideline: Clean air is odor-free |
|  | Strong smells from /use of Chemicals (such as cleaning products) (chemical) | Use building-issued cleaning products. Use products in accordance with manufacturer’s instructions including dilution, application, and ventilation. Avoid using products that are stronger than needed for the situation. |
|  | Strong odors from new building materials (carpeting/furniture) (chemical) | Use low VOC-emitting materials. Air out materials (outside or in unoccupied area) prior to installation. |
|  | Tobacco smoke Secondhand Smoke (pollutant) | Eliminate tobacco smoking. Seal all shared wall penetrations. |
| X | Products with strong odor such as paint, perfume, hairspray, air fresheners, bug-spray, laminators, candles, wax melters, dry erase markers and other VOC-containing products (chemical) | If essential: - Provide proper exhaust ventilation to eject aerosolized product directly outdoors. - Avoid/reduce use during occupied hours. If not necessary, remove and eliminate. |
| X | Vehicle exhaust (pollutant) | Enforce anti-idling regulations and post signs to give notice. Relocate vehicles away from fresh air intakes. Require cars to park face-in at building walls. idling-faq |
| X | Vapors and or fumes from gas, oil, or kerosene stoves (pollutant) | Operate stove hood when stove in use. Install stove hood if not present. Ensure equipment is in good working order. |
|  | Ozone (pollutant) | Eliminate use of ozone generating equipment. |
| X | Window Air Conditioners (if not properly maintained) (allergen) | Equip with proper filter and clean periodically. Clean drip pans. Install in window with weathertight, non-mold-growth sustaining material. |
| X | Pottery (pollutant) | Do not operate kiln during occupied hours. Operate kiln with exhaust system activated. Seal all seams and holes in kiln vent. Ensure kiln exhaust discharge terminates outdoors. |
| X | Carpeting (allergen) | Clean carpeting in a manner consistent with IICRC standards, including regular vacuuming with a high efficiency particulate air (HEPA) filtered vacuum in combination with annual cleaning or semi-annual cleaning in soiled high traffic areas. |
| X | Sweeping/dusting vs HEPA vacuuming/wet wiping (allergen or pollutant) | Refrain from using feather dusters or brooms. Utilize HEPA vacuums and wet wiping to minimize aerosolizing particulate matter. |
| X | Lack of adequate air exchange/mechanical ventilation | Make repairs as necessary and ensure all HVAC system components are operating continuously when building is occupied. |
| X | Lack of local exhaust at source of pollution (vocational shop activities, kitchen exhaust hood) (all) | Recommend installation of exhaust ventilation to direct pollutants directly outdoors. |
|  | Renovating buildings while occupied (chemical) | Use all SMACNA guidelines for Renovation While Buildings Are Occupied. For information, visit https://www.mass.gov/service-details/construction-and-renovation-generated-pollutants-in-occupied-buildings. |
|  | Chemistry program chemical storage (chemical) | Repair (if needed) and operate chemical storeroom vents appropriately. Reduce or eliminate unneeded or overstocked chemicals. Store all chemicals in a manner to separate incompatible chemicals. Keep chemical storerooms clean. |
| X | Photocopiers/duplicating machines | All machines should have dedicated exhaust vents. |