## Sheet1
APPLICANT:
FACILITY ADDRESS:
SYSTEM DESIGN FLOW: gpd
FACILITY AGGREGATE DESIGN FLOW: gpd
□ NEW CONSTRUCTION □ UPGRADE/REPAIR
REVIEWED BY:
DATE:
| N/A | OK | NO
SOIL TESTING
Performed by a currently approved Soil Evaluator [310 CMR 15.018(1)]
Witnessed by the Approving Authority [310 CMR 15.101(1)]
Soil testing complete and prepared on MassDEP-approved form [310 CMR 15.103(1), (2) and (4)]
Percolation testing witnessed by the Approving Authority [310 CMR 15.104(1)]
Soil logs and percolation testing results submitted to the Approving Authority within 60 days of testing including the certification statement [310 CMR 15.018(2)]
Four feet of naturally occurring pervious material beneath the proposed SAS. Required for new construction; I/A may solve the issue for an upgrade [310 CMR 15.415(1) and (2)]
If LUA for depth to groundwater, Approving Authority witness is also an approved Soil Evaluator [310 CMR 15.405(1)(h)1 - if not, variance
GENERAL
Legal boundaries denoted [310 CMR 15.220(4)(a)]
Street, Lot, tax parcel number and lot number noted on plan [310 CMR 15.220(4)(u)]
Locus provided [310 CMR 15.2204(t)]
Plan proper scale? (1"=40' for plot plans, 1"= 20' or fewer for components) [310 CMR 15.220(4)]
Easements shown [310 CMR 15.220(4)(b)]
System located totally on lot served
If upgrade and any component is to be placed on abutting property, recorded easement [310 CMR 15.404(3)(d)] and PLS stamp [310 CMR 15.405(1)(a)]
If property line variance is required for upgrade or new construction [310 CMR 15.220(3)] or LUA for an upgrade within 5 feet of a property line [310 CMR 15.405(1)(a)], PLS stamp
Location of impervious surfaces (driveways, parking areas etc.) [310 CMR 15.220(4)(d)]
Location all propsoed and all existing buildings [310 CMR 15.220(4)(c)]
Location and dimensions of system components and reserve area(s) [310 CMR 15.220(4)(e)]
System calculations shown [310 CMR 15.220(4)(f)]
daily flow (310 CMR 15.203) or MassDEP approval
septic tank capacity (required and provided)
soil absorption system (required and provided)
whether system is designed for garbage grinder
North arrow [310 CMR 15.220(4)(g)]
Existing and proposed contours [310 CMR 15.220(4)(g)]
Location and log of deep observation holes (existing grade elevation on each test) [310 CMR 15.220(4)(h)]
Name(s) of Approving Authority who witnessed soil and percolation testing [310 CMR 15.220(4)(h) and (i)]
Name(s) and approval date(s) of soil evaluator(s) who conducted soil and percolation testing [310 CMR 15.220(4)(h), (i) and (j)]
Location and date of percolation tests [310 CMR 15.220(4)(i)]
Percolation test results match loading rate? [310 CMR 15.242]
Certification statement by Soil Evaluator [310 CMR 15.220(4)(j)]
Observed and adjusted groundwater (method for adjustment given or indicated) [310 CMR 15.103(3) and 310 CMR 15.220(4)(n)]
Mounding analysis provided as a supplemental document for systems with total design flow ≥ 2,000 gpd (includes individual systems part of a larger system) [310 CMR 15.212(2)]
Location of every water supply, public and private, [310 CMR 15.220(4)(k)]
within 400 feet of the proposed system location in the case of surface water supplies and gravel packed public water supply wells
within 250 feet of the proposed system location in the case of tubular public water supply wells
within 150 feet of the proposed system location in the case of private water supply wells
Location of all surface waters and wetlands located up to 100 ft. beyond setbacks listed in 310 CMR 15.211 and any catch basins located within 50 ft. [310 CMR 15.220(4)(l)]
NOTE: If tanks and/or SAS are located within certain setbacks of surface water supplies and tributaries thereto, LUA does not apply to repairs and variance is required [310 CMR 15.405(1)(g)]. In addition, MassDEP approval of certain setback variance may be required [310 CMR15.411(5)].
Location of all irrigation wells within 50 feet of the proposed system [310 CMR 15.211(1)]
Water lines and other subsurface utilities located [310 CMR 15.220(4)(m)] (if water line cross see 310 CMR 15.211(1)[1])
Profile of system showing invert elevations of all system components and the bottom of the SAS [310 CMR15.220(4)(o)]
Stamp of designer [310 CMR 15.220(1) and 310 CMR 15.220(2)]
Stamp of Registered Land Surveyor (if required) [310 CMR 15.220(3) and 310 CMR 15.405(1)(a)]
Number and location of test holes adequate (two in each of the primary and reserve unless trenches as permitted in 310 CMR 15.102(2) or as approved for an upgrade under LUA at 310 CMR 15.405(1)(k)
Test holes adequate to demonstrate four feet of suitable material beneath entire SAS [310 CMR 15.103(4)]
Test holes adequate to confirm adequate groundwater separation [310 CMR 15.103(3)]
Benchmark within 50-75' of system [310 CMR 15.220(4)(q)]
Materials specifications noted? [various sections of 310 CMR 15.000]
System components ≤ 36" deep (unless Local Upgrade Approval requested) [310 CMR 15.221(7) and 310 CMR 15.405(1(b)]
GREASE TRAP
If required by T5, must be external [310 CMR 15.230(12)]
Adequate size: minimum capacity of 1,000 gallons or 24-hr kitchen flow (25 gpd/seat) capacity whichever is greater [310 CMR 15.230(3)]
Minimum depth of 4 feet [310 CMR 15.230(3)]
Separate building sewer from kitchen [310 CMR 15.230(2)]
Watertight construction and constructed of materials specified in 310 CMR 15.221 and 15.226(1) and (2) [310 CMR 15.230(4)]
Inlet tee extends to mid-depth of the tank [310 CMR 15.230(5)]
Outlet tee extends to within 12" of the bottom [310 CMR 15.230(5)]
Note regarding installation on stable compacted base [310 CMR 15.230(6)]
20" minimum diameter access covers over both the inlet and outlet tees [310 CMR 15.330(7)]
Drop between inlet and outlet elevations is at least 2 inches (0.17 ft) [310 CMR15.230(9)]
Inlet and outlet elevations at least 12" above high groundwater (except as described 310 CMR 15.227(5)) or permitted for upgrades under LUA [310 CMR 15.405(1)(j)]
Accesssibility must be maintained [310 CMR 15.230(8)]
> 10 ft from building foundation [310 CMR 15.211(1)]
Buoyancy calculation Required/Done [310 CMR 15.221(8)]
H-20 where appropriate [310 CMR 15.226(3)]
Setbacks from resources [310 CMR 15.211]
Does Approving Authority want to require alarms and/or remote monitoring? If yes, has it been provided? [310 CR15.230(13)]
BUILDING SEWER
At least ten feet from any water line [310 CMR 15.222(2)]; LUA for repairs/upgrades [310 CMR 15.405(1)(g)]
4 inch minimum diameter for building sewer [310 CMR 15.222(1)]
Sewer piping at least 18" below water line (when water and sewer cross) [310 CMR 15.211(1)[1]]
Cleanouts required/provided ? [310 CMR 15.222(8)]
Thrust blocks specified in force mains? 310 CMR 15.221(6)(c)]
Slope of sewer line not less than 0.01 (1/8"/ft) 0.02 preferable [310 CMR 15.222(6)]
Proper pitch on all runs? (0.005 within gravity-distributed trenches and beds) [310 CMR 15.251(9) and 310 CMR 15.252(2)(c)]
PUMPING PRIOR TO SEPTIC TANK
If < 25% design flow of the system for a single-family dwelling only, pump discharge pipe is connected to builing sewer [310 CMR 15.229(1)] and
If non-grinder pump,
discharge flow rate is less than 60 gpm at design total dynamic head [310 CMR 15.229(1)(a)]
capable of passing a 2-inch solid [310 CMR 15.229(1)(a)]
discharges to a septic tank with a mimimum volume of 1,500 gal [310 CMR 15.229(1)(a)]
If grinder pump,
discharge flow rate shall comply with State Pumpng Code [310 CMR 15.229(1)(b)]
discharges to a multi-compartment septic tank or two tanks in series [310 CMR 15.229(1)(b)]
If > 25% design flow of the system for a single-family dwelling only, pump discharge pipe is connected to builing sewer [310 CMR 15.229(2)] and
If non-grinder pump,
discharge flow rate is less than 60 gpm at design total dynamic head [310 CMR 15.229(1)(a) and 310 CMR 15.229(2)(a)]
capable of passing a 2-inch solid [310 CMR 15.229(1)(a) and 310 CMR 15.229(2)(a)]
discharges to a multi-compartment septic tank or two tanks in series [310 CMR 15.229(1)(b) and 310 CMR 15.229(2)(a)]
stand-by power, a hookup for standby power or at least one-day of storage capcaty is provided [310CMR 15.229(2)(c)]
If grinder pump,
discharge flow rate shall comply with State Pumpng Code [310 CMR 15.229(1)(b) and 310 CMR 15.229(2)(a)]
discharges to a multi-compartment septic tank or two tanks in series [310 CMR 15.229(1)(b) and 310 CMR 15.229(2)(a)]
stand-by power, a hookup for standby power or at least one-day of storage capcaty is provided [310CMR 15.229(2)(c)]
If other than a single-family dweliing, all other uses of pumps prior to sepic tanks must received prior written Approving Authority approval [310 CMR 15.229(3)]
SEPTIC TANK
Adequate size [310 CMR 15.223(1)]
Inlet tee located ten inches below flow line [310 CMR 15.227(6)]
Outlet tee 14" or 14" + 5" per foot for increase ft depth [310 CMR 15.227(6)]
Outlet tee with gas baffle or approved filter [310 CMR 15.227(4)]
Drop between inlet and outlet elevations is at least 2 inches (0.17 ft) but no more than 3 inches (0.25 ft) [310 CMR15.227(4)]
Note regarding installation on stable compacted base [310 CMR 15.228(1)]
Horizontal separation between inlet and outlet tees (no less than liquid depth) [310 CMR 15.227(2)]
Inlet/Outlet elevations at least 12" above high groundwater (except as described 310 CMR 15.227(5)) or permitted for upgrades under LUA [310 CMR 15.405(1)(j)]
Minimum cover 9" (Tanks buried more than 9" must have risers on all openings and on the d-box) [310 CMR 15.2228(1) and 310 CMR 15.232(3)(f)]
Three access covers (inlet and outlet must be 20" or greater) - middle access at least 8" [310 CMR 15.228(2)] - all to grade
All at-grade covers secured to unauthorized access? [310 CMR 15.228(2)]
> 10 ft from building foundation or slab [310 CMR 15.211(1)]
Buoyancy calculation Required/Done [310 CMR 15.221(8)]
H-20 Where appropriate? [310 CMR 15.226(3)]
Setbacks from resources [310 CMR 15.211]
MULTI-COMPARTMENT SEPTIC TANK OR TANKS IN SERIES
Required when other than single-family dwelling or when flow >1,000 gpd [310 CMR 15.223(1)(b)]
First compartment 200% daily flow; second compartment 100% daily flow [310 CMR 15.224(2) and (3)]
"U" pipe through or over baffle, outlet of each compartment with gas baffle or approved filter [310 CMR 15.224(4)]
DISTRIBUTION BOX
Stable compacted base [310 CMR 15.221(2) and 310 CMR 15.232(2)(a)]
Splash plate or baffle tee required on inlet? Provided? (when pressure sewer to d-box or steep pitch of gravity sewer) [310 CMR 15.323(3)(a)]
Riser if deeper than 9" [310 CMR 15.232(3)(f)]
2-inch minimum drop from inlet to outlets [310 CMR 15.232(3)(b)]
Inside minimum dimension 12" [310 CMR 15.232(2)(b)]
Minimum sump 6" [310 CMR15.232(3)(e)]
Watertight cover if <2000gpd); waterproof manhole if >2000gpd [310 CMR 15.232(3)(d)]
PUMP CHAMBER AND FORCE MAIN
Emergency storage above working level (pump on elev) ≥ design flow? [310 CMR 15.231(2)]; If not, standby power
Proper setbacks [310 CMR 15.211 (same as septic tanks)]
Watertight 20-in minimum diameter manhole [310 CMR 15.231(5)]
Manhole to grade [310 CMR 15.231(5)]
Service components accessible (not too deep with piping, disconnects accessible)
Alarm floats - alarm on circuit separate from pumps [310 CMR 15.230(9)]
Pump operation: pumps off/lead pump on; lag pump on and alarm on; pumps may alternate [310 CMR 15.230(8)]
If serving more than two residential units, must have two pumps operating in lead-lag mode. [310 CMR 15.231(6) and (8)]
Stable Compacted Base [310 CMR 15.221(2)]
Buoyancy calculations needed ? Provided? [310 CMR 15.221(8)]
Siphon problem? (leachfield below pump chamber)
Materials specified [310 CMR 15.251(5) specifies various pipe types allowed]
PRESSURE DOSED OR PRESSURE DISTRIBUTED SYSTEM
Pump and piping calculations as required [310 CMR 15.220(4)(r)]
Pressure distribution required on all systems ≥ 2,000 gpd [310 CMR 15.254(2)]
If used in gravelless system - make sure jet is directed as not to scour soil interface [Guidance Document]
Inspections once per year (< 2,000 gpd) or quarterly (≥ 2,000 gpd) good to note on plan [310 CMR 15.254(2)(d)]
SOIL ABSORPTION SYSTEMS (SAS) GENERAL
Calculations shown and correct
4 feet of naturally occurring material [310 CMR 15.240(1)]
Required separation to groundwater? [310 CMR 15.212)]
Aggregate specified as double washed [310 CMR 15.247(2)]
System Venting required/provided (system under driveway or >36" deep) [310 CMR 15.241]
Inspection ports specified and within 3" of final grade? [310 CMR 15.240(13)]
If ≥ 2,000 gpd (overall system in the aggregate), mounding analysis required [310 CMR 15.240(12)]
Correct LTAR selected for gravity distribution or pressure distribution without higher LTAR [310 CMR 1.242(1)(a)]
Correct LTAR selected for pressure distribution - higher LTAR [310 CMR 1.242(1)(b)]
Correct LTAR selected and pressure distribution provided if appropriate for LUA for upgrades with sieve analysis [310 CMR 15.405(1)(i) and associated guidance]
TRENCHES
100 feet - maximum length [310 CMR 15.251(1)(a)]
Width - 2-ft min and 3-ft max [310CMR 15.251(1)(b)
Effective depth - 2-ft max [310 CMR 15.251(1)(c)]
Minimum separation 2x effective depth or width whichever greater (3x if reserve between trenches) [310 CMR 251(1)(d)]
Situated along contours [310 CMR 15.251(2)]
Breakout OK? [310 CMR 15.211(1)[4] and Guidance Document]
Minimum pipe diameter of 3-inches [310 CMR 15.251(7)]
Gravity distribution line slope of 0.005 feet per foot [310 CMR 15.251(9)]
Lines exceeding 50 feet in length shall be connected and vented [310 CMR 15.251(11)]
Endcaps or vent manifold specified?
Size and orientation of discharge holes specified? (not smaller than 3/8" not larger than 5/8") [310 CMR 15.251(8) and 310 CMR 15.252(2)(h)]
Materials specified [310 CMR 15.251(5)]
BED OF FIELD SAS
Maximum size of bed or field = 5,000 gpd [310 CMR 15.252(1)]
Minimum 2 distribution lines [310 CMR 15.252(2)(a)]
Maximum separation between lines 6' [310 CMR 15.252(2)(d)]
Maximum separation between lines and outside of bed 4' [310 CMR 15.252(2)(e)]
Gravity distribution line slope of 0.005 feet per foot [310 CMR 15.252(2)(c)]
Aggregate depth below discharge pipes 6" minimum, 12" maximum. [310 CMR 15.252(2)(g)]
Separation between beds 10' minimum. [310 CMR 15.252(2)(f)]
Bottom area used in calculations only [310 CMR 15.252(2)(i)]
Endcaps or vent manifold specified?
Size and orientation of discharge holes specified? (not smaller than 3/8" not larger than 5/8") [310 CMR 15.251(8) and 310 CMR 15.252(2)(h)]
Materials specified [10 CMR 15.251(5)]
GALLERIES, PITS AND CHAMBERS
NOTE: If the SAS is an alternative SAS with treatment or an altenative SAS approved under the I/A program, please use the appropriate alternative technology checklist.
Chambers and galleries in trench configuration supplied with inlet every 20 ft. [310 CMR 15.253(6)]
Each structure with one inspection manhole (if >2000 gpd must be to grade) [310 CMR 15.253(2)]
Aggregate 1' minimum to 4' maximum. [310 CMR 15.253(1)(b)]
2' sidewall credit maximum [310 CMR 15.253(1)(a)]
In bed configuration, inlet every 40 sq. ft. [310 CMR 15.253(6)]
If two or more pits, parallel operation [310 CMR 15.253(4)]
Pits, chambers and galleries in bed or field configuration, effective leaching area includes only the bottom area, not the sidewalls [310 CMR 15.253(7)]
Endcaps or vent manifold specified?
Size and orientation of discharge holes specified? (not smaller than 3/8" not larger than 5/8") [310 CMR 15.251(8) and 310 CMR 15.252(2)(h)]
Materials specified [310 CMR 15.251(5)]
CONSTRUCTION IN FILL
Plan specifies that the fill shall meet the specification of 310 CMR 15.255(3)
Impervious barrier and/or retaining wall required [Guidance Document]
Installation must be supervised by designer [310 CMR 15.255(2)(b)]
Retaining wall designed by Registered Professional Engineer [310 CMR 15.255(2)(a)]
Side slope does not exceed 3:1 [310 CMR 15.255(2)]
Breakout requirements met [310 CMR 15.252(2) and Guidance Document]
≥ 5 ft. from impervious barrier to edge of SAS (10 ft. recommended) [310 CMR 15.255(2)(e)]
TIGHT TANK
Upgrade of a failed system with no alternative [310 CMR 15.260(1)]
New construction permitted only for: boat pump-out facility; buildings related to public water supply; or publicly owned and operated seasonal structures (all with no other feasuible alternative) [310 CMR 15.260(1)]
Upgrade of failed system serving an existing seasonal (< 6 mo/yr) residential facility [310 CMR 15.260(8)]
Capacity ≥ 500% design flow in accorance with 310 CMR 15.203 but no less than 2,000 gpd [310 CMR 15.260(2)(a)]
Audio and visual alarms set at 3/5 capacity [310 CMR 15.260(2)(c)]
Waterproof and watertight and not located in groundwater without extensive testing [310 CMR 15.260(2)(j)]
Meets 310 CMR 15.226(1) through (4) [310 CMR 15.260(2)(l)]
Method, frequency and location for disposal of contents [310 CMR 15.260(2)(e) and (f)]
At least one 24-inch diamter cast iron manhole at finished grade [310 CMR 15.260(2)(f)]
Year-round access [310 CMR 15.260(2)(g)]
O&M plan [310 CMR 15.260(2)(i)]
Deed notice re: tight tank [310 CMR 15.260(6)]
Deed notice re: seasonal dwelling [310 CMR 15.260(8)]
AREAS WITH NITROGEN LOADING RESTRICTIONS
If new construction in a Zone II, IWPA or private well area, meets 440 gpd [310 CMR 15.214(1) and (2)]
If not, credit land provided [310 CMR 15.216, esp. (5), and Guidelines for Title 5 Aggregation of Flows and Nitrogen Loading]
If credit land provided, easements and deed restrictions provided [310 CMR 15.216(5)(b) and Guidelines for Title 5 Aggregation of Flows and Nitrogen Loading]
If not, nitrogen-reducing I/A provided {Refer to I/A approvals}
If new construction in a Zone II, IWPA or private well area, and does not meet 440 gpd, MFC should be pursued [Title 5 Program's Guidance on System Upgrades in Areas Subject to Nitrogen Loading Limitations, Policy No. BRP/DWM/PeP-P99-5]
SHARED SYSTEM
If new construction, approved cluster development? [310 CMR 15.290(1)(b)]
If yes, no demonstration plan required [310 CMR 15.290(1)(b)]
If no, demonstration plan required [310 CMR 15.290(1)(b)]
Proposed O&M plan [310 CMR 15.290(2)(b)]
Easement showing shared components [310 CMR 15.290(2(c)]
Form of ownership of the shared components [310 CMR 15.290(2(c)]
Financial assurance mechanism [310 CMR 15.290(2)(d)]
Proposed Covenant and Easement Documents [310 CMR 15.290(2)(e)]
Division of facility resulting in shared system {Refer to 310 CMR 15.291}