COMPLIANCE CHECKLIST

OP1_General & Specialty Medical Services Facilities

The following checklist is intended to be used in plan review applications for health care facilities submitted to Massachusetts Department of Public Health  This checklist summarizes & references applicable requirements from Licensure Regulations & 2022 Edition of FGI Guidelines for Design & Construction of Outpatient Facilities  Applicants must verify compliance of plans submitted to Department with all referenced requirements from Licensure Regulations & FGI Guidelines when completing this Checklist  separate Checklist must be completed for each nursing unit hospital or clinic department or clinical suite.

Other jurisdictions regulations & codes may have additional requirements which are not included in this checklist such as:

- NFPA 101 Life Safety Code (2012) & applicable related standards contained in appendices of Code

- State Building Code (780 CMR)

- Accreditation requirements of Joint Commission

- CDC Guidelines for Preventing Transmission of Mycobacterium Tuberculosis in Health Care Facilities

- USP 797 & Regulations of Massachusetts Board of Registration in Pharmacy

- Occupational Safety & Health Standards (OSHA)

- Accessibility Guidelines of Americans with Disabilities Act (ADA)

- Architectural Access Board Regulations (521 CMR)

- Local Authorities having jurisdiction

Instructions:

- All requirement lines must be completed according to following instructions & included in plan submissions for Self-Certification Process or Abbreviated Review Process.

- This checklist must be completed by project architect or engineer based on design actually reflected in plans at time of completion of checklist.

- Each requirement line (___) of this Checklist must be completed exclusively with one of following marks unless otherwise directed in checklist  If functional space is not affected by renovation project mark “E” may be indicated on requirement line (___) before name of functional space (associated requirements on indented lines below that name or associated MEP requirements do not have to be completed in this case)  If more than one functional space serves given required function (e.g. patient room or exam room) that clarification should be provided in Project Narrative & requirement lines are understood to only address functional spaces that are involved in project.

| X = Requirement is met for new space for renovated space or for existing direct support space for expanded service. | = Check box under section titles or individual requirements lines for optional services or functions that are not included in project area. |
| --- | --- |
| E = Requirement relative to existing suite or area that has been licensed for its designated function is not affected by construction project & does not pertain to required direct support space for specific service affected by project “E” must not be used for existing required support space associated with new patient care room or area. | W = Waiver requested for specific section of Regulations or FGI Guidelines where hardship in meeting requirement can be demonstrated (a Physical Plant Waiver Form must be completed for each waiver request) explicit floor plan or plan detail must be attached to each waiver request. |

- All room functions marked with "X" must be shown on plans with same name labels as in this checklist.

- Mechanical electrical & plumbing requirements are only partially mentioned in this checklist.  Relevant section of FGI Guidelines must be used for project compliance with all MEP requirements & for waiver references.

- Oxygen, vacuum, medical air waste, anesthesia gas disposal & instrument air outlets (if required) are identified respectively by abbreviations "OX" "VAC" "MA" “WAGD” & “IA”.

- Any requirements referenced with “FI” result from formal interpretations from FGI Interpretations Task Group.

- The location requirements including asterisks (*) refer to definitions of Glossary in beginning section of FGI Guidelines & reproduced in this checklist.

| Facility Name: |  | DoN Project Number: (if applicable) |
| --- | --- | --- |
| Facility Address: |  |  |
| Satellite Name: (if applicable) |  | Building/Floor Location: |
| Satellite Address: (if applicable) |  | Submission Dates: |
| Project Description: |  | Initial Date: Revision Date: |

|  | Architectural Requirements | Building Systems Requirements |  |
| --- | --- | --- | --- |
| 2.2 | GENERAL & SPECIALTY MEDICAL SERVICES FACILITIES |  |  |
| 2.2-2 2.1-2.1.1.2 | ACCOMMODATIONS FOR CARE OF INDIVIDUALS OF SIZE ☐ check if not included in project (only if Patient Handling & Movement Assessment that determines that outpatient service does not have need for expanded-capacity lifts & architectural details that support movement of individuals of size in patient areas is attached to Project Narrative) |  |  |
| 2.1-2.1.2 | Location: |  |  |
|  | ___ spaces designated for care of or use by individuals of size are provided in locations to accommodate population expected to be served by facility |  |  |
| 2.1-2.5 | ___ Handwashing stations |  |  |
| 2.1-2.5.2 | ___ downward static force required for handwashing stations designated for individuals of size accommodates maximum patient weight of patient population |  |  |
| 2.1-2.6 | ___ Patient toilet room |  |  |
| 2.1-2.6.1.1 | ___ expanded-capacity toilet ___ mounted Min. 36” from finished wall to centerline of toilet on both sides (for caregiver assistance and/or use of floor-based lift) or | Ventilation: ___ Min. 4 air changes per hour ___ Exhaust ___ Negative pressure ___ No recirculating room units | Table 8-2 |
| 2.1-2.6.1.2 | ___ regular toilet ___ mounted Min. 44” from centerline of toilet on both sides to finished walls to allow for positioning of expanded-capacity commode over toilet |  |  |
| 2.1-2.6.1.3 | ___ rectangular clear floor area Min. 46” wide extends 72” from front of toilet |  |  |
| 2.1-2.6.2.1 | ___ grab bars in toilet rooms intended for use by individuals of size are anchored to sustain concentrated load of 800 pounds |  |  |
| 2.1-2.6.2.2 | ___ adjustable/foldable grab bar mounted on horizontally movable track is provided |  |  |
| 2.1-2.7 | ___ Single-patient exam/observation room |  |  |
| 2.1-2.7.1 | Space Requirements: |  |  |
| 2.1-2.7.1.1(1) | ___ Min. 5'-0" clearance at foot of expanded-capacity exam table | Ventilation: ___ Min. 2 air changes per hour | Table 8-2 |
| (2) | ___ Min. 3'-0" clearance on non-transfer side of expanded- capacity exam table | Lighting: ___ Portable or fixed exam light | 2.1-8.3.4.2(1) |
| (3)(a) | ___ Min. 5’-0” on transfer side of expanded-capacity exam table with ceiling- or wall-mounted lift or | Power: ___ Each exam table is served by at least one duplex receptacle | 2.2-8.3.6.2 |
| (3)(b) | ___ Min. 7’-0” on transfer side of expanded-capacity exam table in rooms without ceiling- or wall-mounted lift |  |  |
| 2.1-2.8 | ___ Equipment & supply storage |  |  |
| 2.1-2.9 | ___ Waiting areas |  |  |
| 2.1-2.9.1 | ___ seating for persons of size be provided in waiting areas in outpatient facilities |  |  |
| 2.1-2.9.2 | ___ waiting areas be sized to accommodate expanded-capacity furniture required for patients & visitors of size |  |  |
| 2.1-2.10.1 | ___ All plumbing fixtures handrails grab bars patient lift equipment built-in furniture & other furnishings designed to accommodate maximum patient weight |  |  |
| 2.1-2.10.2 | Door Openings: |  |  |
| 2.1-2.10.2.1 | ___ all door openings used for path of travel to public areas & areas where care will be provided for individuals of size have Min. clear width of 45.5” to provide access for expanded-capacity wheelchairs |  |  |
| 2.1-2.10.2.2 | ___ door openings to toilet rooms designated for individuals of size have Min. clear width of 45.5” |  |  |
| 2.2-3 | PATIENT CARE & DIAGNOSTIC AREAS |  |  |
| 2.1-3.1.2 | ___ Provisions shall be made to address patient visual and speech privacy |  |  |
| 2.2-3.2.2 | EXAM ROOMS |  |  |
| 2.2-3.2.2.2 | (may serve as both examination & treatment spaces) |  |  |
| 2.1-3.2.2.1(1)(b) | ___ Provisions to preserve patient privacy from observation from outside exam room |  |  |
| 2.1-3.2.2.2 | ___ Single-patient exam room ☐ check if not included in project |  |  |
|  | Space Requirements: |  |  |
| (2)(a) | ___ Min. clear floor area of 80 sf |  |  |
|  | ___ room size allows Min. clearance 2’-8” at each side & at foot of exam table or recliner | Ventilation: ___ Min. 2 air changes per hour | Table 8-2 |
|  | ___ room arrangement shown in plans for each exam room (Layout #1) | Power: ___ Each exam table is served by at least one duplex receptacle | 2.2-8.3.6.2 |
| (1)(b) | ___ room arranged with particular placement of exam table recliner or chair to accommodate type of patient being served ☐ check if not included in project |  |  |
|  | ___ room arrangement shown in plans (Layout #2) |  |  |
|  | ___ proposed room arrangement to accommodate type of patient being served is explained in Project Narrative |  |  |
| (3) | Exam Room Features: |  |  |
| (a) | ___ portable or fixed exam light |  |  |
| (b) | ___ storage for supplies |  |  |
| (c) | ___ accommodations for written or electronic documentation |  |  |
| (d) | ___ space for visitor’s chair |  |  |
| (e) | ___ handwashing station |  |  |
| 2.1-3.2.2.2 | ___ Single-patient exam/observation room ☐ check if not included in project |  |  |
| (1)(a) | ___ immediately accessible* to nurse or control station & toilet room |  |  |
|  | Space Requirements: |  |  |
| (2)(a) | ___ Min. clear floor area of 80 sf |  |  |
|  | ___ room size allows Min. clearance 2’-8” at each side & at foot of exam table or recliner | Ventilation: ___ Min. 2 air changes per hour | Table 8-2 |
|  | ___ room arrangement shown in plans for each exam room (Layout #1) | Power: ___ Each exam table is served by at least one duplex receptacle | 2.2-8.3.6.2 |
| (1)(b) | ___ particular placement of exam table recliner or chair ☐ check if not included in project |  |  |
|  | ___ room arrangement shown in plans (Layout #2) ___ proposed room arrangement to accommodate type of patient being served is explained in Project Narrative |  |  |
| (2)(b) | ___ single-patient exam/observation room with dual entry ☐ check if not included in project |  |  |
|  | ___ min. clear floor area of 100 sf |  |  |
|  | ___ room size accommodates min. clearance of 2’-8” at each side & at foot of exam table or recliner |  |  |
| (3) | Exam Room Features: |  |  |
| (a) | ___ portable or fixed exam light |  |  |
| (b) | ___ storage for supplies |  |  |
| (c) | ___ accommodations for written or electronic documentation |  |  |
| (d) | ___ space for visitor’s chair |  |  |
| (e) | ___ handwashing station |  |  |
| (2)(c) | ___ Single-patient exam room for specialty clinical services (ENT or Eye examinations) ☐ check if not included in project |  |  |
|  | Space Requirements: |  |  |
|  | ___ Min. clear floor area 100 sf |  |  |
|  | ___ Min. clearance 3’-6” at sides head or foot of exam table/chair as needed for staff expected work positions | Ventilation: ___ Min. 2 air changes per hour | Table 8-2 |
|  | ___ Min. clearance 1'-0" at sides head or foot of exam table or chair other than work positions | Power: ___ Each exam table is served by at least one duplex receptacle | 2.2-8.3.6.2 |
| (3) | Exam Room Features: |  |  |
| (a) | ___ portable or fixed exam light |  |  |
| (b) | ___ storage for supplies |  |  |
| (c) | ___ accommodations for written or electronic documentation |  |  |
| (d) | ___ space for visitor’s chair |  |  |
| (e) | ___ handwashing station |  |  |
| 2.1-3.2.2.3 | ___ Sexual assault forensic exam room ☐ check if not included in project |  |  |
| 2.2-3.2.1.2 | (may serve as both examination & treatment spaces) |  |  |
| 2.1-3.2.2.1(1)(b) | ___ Provisions to preserve patient privacy from observation from outside exam room |  |  |
| 2.1-3.2.2.3(1) | ___ each sexual assault forensic exam room contain pelvic exam bed/table |  |  |
| 2.1-3.2.2.3(2) | ___ private toilet room immediately accessible |  |  |
| (a) | ___ shower |  |  |
| (b) | ___ storage space for clothing, shoes linens & bathing products |  |  |
| 2.1-3.2.2.3(3) | ___ provisions for lockable storage for forensic collection kits, laboratory supplies & equipment |  |  |
| 2.1-3.2.2.3(4) | ___ room for consultation, family support services & law enforcement ___ readily accessible to sexual assault forensic exam room |  |  |
| 2.1-3.2.2.2 |  |  |  |
| (2)(a) | ___ Min. clear floor area of 80 sf |  |  |
|  | ___ room size allows Min. clearance 2’-8” at each side & at foot of exam table or recliner | Ventilation: ___ Min. 2 air changes per hour | Table 8-2 |
|  | ___ room arrangement shown in plans for each exam room (Layout #1) | Power: |  |
| (1)(b) | ___ room arranged with particular placement of exam table recliner or chair to accommodate type of patient being served ☐ check if not included in project | ___ Each exam table is served by at least one duplex receptacle | 2.2-8.3.6.2 |
|  | ___ room arrangement shown in plans (Layout #2) |  |  |
|  | ___ proposed room arrangement to accommodate type of patient being served is explained in Project Narrative |  |  |
| (3) | Exam Room Features: |  |  |
| (a) | ___ portable or fixed exam light |  |  |
| (b) | ___ storage for supplies |  |  |
| (c) | ___ accommodations for written or electronic documentation |  |  |
| (d) | ___ space for visitor’s chair |  |  |
| (e) | ___ handwashing station |  |  |
| 2.2-3.8 | SUPPORT AREAS FOR GENERAL & SPECIALTY MEDICAL SERVICES FACILITIES |  |  |
| 2.1-3.8.11.2 | ___ Clean workroom or clean work area |  |  |
| (1) | ___ work counter | Ventilation: |  |
| (2) | ___ handwashing station | ___ Min. 2 air changes per hour | Table 8-2 |
| (3) | ___ storage for clean & sterile supplies or | ___ Positive pressure |  |
| 2.1-3.8.11.3 | ___ Clean supply room or clean supply area ___ used only for storage & holding as part of system for distribution of clean & sterile materials | Ventilation: ___ Min. 2 air changes per hour ___ Positive pressure | Table 8-2 |
| 2.1-3.8.12.2 | ___ Soiled workroom |  |  |
| 2.1-3.8.12.1 | ___ does not have direct connection with clean workrooms or clean supply rooms | Ventilation: ___ Min. 6 air changes per hour | Table 8-2 |
| 140.204 | ___ handwashing station | ___ Exhaust |  |
| 140.204 | ___ clinical service sink | ___ Negative pressure |  |
| 2.1-3.8.12.2(1) (d) | ___ work counter | ___ No recirculating room units |  |
| 2.1-3.8.12.2 (1)(e) | ___ space for separate covered containers for waste & soiled linen |  |  |
| 2.1-3.8.12.2(2) | ___ fluid waste management system ☐ check if not included in project |  |  |
| (a) | ___ electrical & plumbing connections that meet manufacturer requirements |  |  |
| (b) | ___ space for docking station |  |  |
|  | or |  |  |
| 2.1-3.8.12.3 | ___ Soiled holding room |  |  |
| 2.1-3.8.12.1 | ___ does not have direct connection with clean workrooms or clean supply rooms | Ventilation: ___ Min. 6 air changes per hour | Table 8-2 |
| 140.204 | ___ handwashing station | ___ Exhaust |  |
| 2.1-3.8.12.3(2) | ___ space for separate covered containers for waste & soiled linen | ___ Negative pressure ___ No recirculating room units |  |
| 2.2-3.8.13 | ___ Equipment & supply storage |  |  |
| 2.2-4.2 | ___ Medication safety zones ☐ check if not included in project (only if pharmacy is provided) |  |  |
| 2.1-3.8.8.1(2) | Design Promoting Safe Medication Use: |  |  |
| (a) | ___ medication safety zones located out of circulation paths |  |  |
| (e) | ___ sharps containers placed at height that allows users to see top of container |  |  |
| 2.1-3.8.8.2 |  |  |  |
| (1) | ___ medication preparation room | Ventilation: |  |
| (a) | ___ work counter | ___ Min. 2 air changes per hour | Table 8-2 |
|  | ___ handwashing station ___ lockable refrigerator ☐ check if not included in project (only if no medications requiring refrigeration are stored) |  |  |
|  | ___ locked storage for controlled drugs |  |  |
|  | ___ sharps containers ☐ check if not included in project |  |  |
| (b) | ___ self-contained medication dispensing units ☐ check if not included in project | Lighting: ___ Task lighting | 2.1-2.8.8.1(2)(d) |
|  | or |  |  |
| (2) | ___ automated medication-dispensing unit |  |  |
| (a) | ___ located at nurse station in clean workroom or in alcove | Lighting: ___ Task lighting | 2.1-3.8.8.1(2)(d) |
| (b) | ___ handwashing station or hand sanitation dispenser provided next to stationary med.-dispensing units |  |  |
| (c) | ___ countertop or cart provided adjacent to stationary med.-dispensing units |  |  |
| 2.2-3.10 | SUPPORT AREAS FOR PATIENTS |  |  |
| 2.2-3.10.2 2.2-3.10.2.2 | ___ Patient toilet room (may also serve waiting areas) |  |  |
| 2.2-3.10.2.1 | ___ readily accessible from exam rooms |  |  |
| 2.1-3.10.2.1 2.1-3.10.2.2 | ___ located to permit access from patient care areas without passing through publicly accessible areas ___ toilet & handwashing station | Ventilation: ___ Min. 4 air changes per hour ___ Exhaust ___ Negative pressure ___ No recirculating room units | Table 8-2 |
| 2.2-4.1 | LABORATORY SERVICES |  |  |
|  | ___ Laboratory services provided on-site ___ Compliance Checklist OP2 has been submitted or ___ Laboratory services provided off-site |  |  |
| 2.2-4.1.8 | SPECIMEN COLLECTION & STORAGE ☐ check if not included in project |  |  |
| 2.2-4.1.8.1 | Specimen Collection: |  |  |
| 2.2-4.1.8.1(1) | ___ dedicated specimen collection toilet room ___ accessible without reentering waiting room or leaving clinical services area | Ventilation: ___ Min. 4 air changes per hour ___ Exhaust | Table 8-2 |
| 2.1-4.1.8.2(1) | ___ handwashing station ___ staff-controlled access | ___ Negative pressure ___ No recirculating room units |  |
| 2.1-4.1.8.2(2) | ___ drug screening requiring Chain of Custody ☐ check if not included in project |  |  |
|  | ___ handwashing station meets requirements of “Department of Health & Human Services Mandatory Guidelines for Federal Workplace Drug Testing Programs” (including securing water supply) |  |  |
|  | or ___ patient toilet room used for specimen collection ___ accessible without reentering waiting room or leaving clinical services area |  |  |
| 2.1-4.1.8.2(1) | ___ handwashing station ___ staff-controlled access |  |  |
| 2.1-4.1.8.2(3) | ___ Dedicated blood collection facilities |  |  |
| (a) | ___ work counter |  |  |
| (b) | ___ seating space for patients |  |  |
| (c) | ___ handwashing station |  |  |
| (d) | ___ supply storage |  |  |
| 2.2-4.1.8.1(2) | or ___ Exam rooms used for blood collection |  |  |
| 2.2-4.1.8.2 | ___ Specimen storage |  |  |
| (1) | ___ accommodations for storage of blood urine & other specimens |  |  |
| (2) | ___ blood storage facilities meet requirements of CLIA standards for blood banks |  |  |
| §493.1103(c)(1) | ___ blood specimen stored in monitored refrigerator or ___ blood storage conditions prevent deterioration of blood specimens |  |  |
| 2.2-4.3 | STERILE PROCESSING ☐ check if not included in project (only if only disposable instruments & supplies are used) |  |  |
| 2.2-4.3.2 | ___ Facilities for on-site sterile processing are provided ___ Compliance Checklist OP4 has been submitted or |  |  |
| 2.2-4.3.3 | ___ Sterile processing is performed off-site |  |  |
|  | ___ Section 2.1-4.3.3 below is completed |  |  |
| 2.1-4.3.3 | ___ Support areas for outpatient facilities using off-site sterile processing ☐ check if not included in project (only if sterile processing services are provided on-site & Compliance Checklist OP4 has been submitted) |  |  |
| 2.1-4.3.3.1 |  |  |  |
| 2.1-4.3.2.4(2) | ___ clean/sterile medical/surgical supply receiving room or area |  |  |
| 2.1-4.3.3.2 |  |  |  |
| 2.1-4.3.2.4(1) | ___ instrument & supply storage |  |  |
| (a) | (may be separate room or portion of clean workroom) |  |  |
| (b) | ___ space for case cart storage ☐ check if not included in project (only if case carts are not used) |  |  |
| (c) | ___ storage for clean/sterile packs include provisions to maintain humidity & temperature levels specified by manufacturer(s) of materials being stored |  |  |
| 2.1-4.3.3.3 2.2-4.3.3.2(2) | ___ room with flush-type device for gross decontamination & holding of soiled instruments (may be combined with soiled workroom) |  |  |
| 2.1-3.8.12.1 | ___ does not have direct connection with clean workrooms or clean supply rooms |  |  |
| 2.1-3.8.12.2(1) |  |  |  |
| (a) | ___ handwashing station | Ventilation: |  |
| (b) | ___ flushing-rim clinical service sink or equivalent flushing-rim fixture | ___ Min. 6 air changes per hour ___ Exhaust | Table 8-2 |
| (c) | ___ work counter | ___ Negative pressure |  |
| (d) | ___ space for separate covered containers for waste & soiled linen | ___ No recirculating room units |  |
| 2.2-4.4 | LINEN SERVICES ☐ check if not included in project (only if no linens are used in facility) |  |  |
| 2.1-4.4.2 | ___ Dedicated on-site linen processing area |  |  |
| 2.1-4.4.2.1(1) | ___ area large enough for washer dryer & any plumbing equipment needed to meet temperature requirements |  |  |
| 2.1-4.4.2.1(2) | ___ area divided into distinct soiled area (sorting & washing) & clean area (drying & folding) |  |  |
| 2.1-4.4.2.2 | ___ storage for laundry supplies |  |  |
| 2.1-4.4.2.3 | ___ clean linen storage |  |  |
| 2.1-4.4.2.4 | ___ handwashing station |  |  |
|  | or |  |  |
| 2.1-4.4.3 | ___ Outpatient facility uses off-site laundry services |  |  |
| 2.1-4.4.3.1 | ___ soiled linen holding area or dedicated area for soiled laundry carts |  |  |
| 2.1-4.4.3.2 | ___ clean linen storage area or dedicated area for clean linen carts |  |  |
| 2.2-5.3 | ENVIRONMENTAL SERVICES |  |  |
| 2.1-5.3.1 | ___ Environmental services room |  |  |
| 2.1-5.3.1.1(3) 2.1-5.3.1.1(1) | (may serve more than one clinical service area on same floor) ___ Min. one ES room per floor | Ventilation: ___ Min. 6 air changes per hour ___ Exhaust | Table 8-2 |
| 2.1-5.3.1.2(1) | ___ service sink or floor-mounted mop sink |  |  |
| 2.1-5.3.1.2(2) | ___ provisions for storage of supplies & housekeeping equipment | ___ Negative pressure ___ No recirculating room units |  |
| 2.1-5.3.1.2(3) | ___ handwashing station or hand sanitation dispenser |  |  |
| 2.2-5.4 | ENGINEERING & MAINTENANCE SERVICES |  |  |
| 2.1-5.4.2.1 | ___ Equipment rooms for HVAC telecom & electrical equipment |  |  |
| 2.1-5.4.2.2 | ___ secured with controlled access |  |  |
| 2.1-5.4.3 | ___ Building maintenance supplies & equipment storage room (may be shared) |  |  |
| 2.2-6.2 | PUBLIC AREAS |  |  |
| 2.1-6.2.1 | ___ Vehicular drop-off & pedestrian entrance |  |  |
| 2.1-6.2.1.1 | ___ Min. of one building entrance reachable from grade level |  |  |
| 2.1-6.2.1.2 | ___ building entrances used to reach outpatient services are clearly marked |  |  |
| 2.1-6.2.1.3 | ___ building entrances used to reach outpatient services located so patients need not go through other activity areas (except for shared lobbies in multi-occupancy buildings) |  |  |
| 2.1-6.2.2 | ___ Reception |  |  |
|  | ___ reception & information counter desk or kiosk provided either at main entry or at each clinical service |  |  |
| 2.1-6.2.3 | ___ Waiting area |  |  |
| 2.1-6.2.3.2 | ___ visible from staff area either by camera or direct staff sight line |  |  |
| 2.1-6.2.4 | ___ Public toilet room |  |  |
| 2.1-6.2.4.2 | (may be located off public corridor in multi-tenant building) | Ventilation: ___ Min. 4 air changes per hour | Table 8-2 |
| 2.1-6.2.4.1 | ___ readily accessible from waiting area without passing through patient care or staff work areas | ___ Exhaust ___ Negative pressure ___ No recirculating room units |  |
| 2.1-6.2.5 | ___ Provisions for telephone access |  |  |
|  | ___ access to make local phone calls |  |  |
| 2.1-6.2.6 | ___ Provisions for drinking water |  |  |
| 2.1-6.2.7.1 | ___ Wheelchair storage ☐ check if not included in project |  |  |
|  | ___ located out of required corridor width ___ directly accessible to entrance ___ provided for at least one wheelchair |  |  |
| 2.1-6.2.7.2 | ___ Wheelchair parking space |  |  |
|  | ___ designated area for at least one patient-owned wheelchair in non-public area ___ located out of any required egress width or other required clearance |  |  |
| 2.2-6.3 | ADMINISTRATIVE AREAS |  |  |
| 2.1-6.3.2 (2) | ___ Interview space (used for patient communication/interviews related to social services, credit, etc.) ☐ check if not included in project (may be combined with consultation room) |  |  |
| (1) | ___ separate from public areas |  |  |
| 2.1-6.3.3 | ___ Office space for business administrative & professional staffs |  |  |
| 2.1-6.3.5 | ___ Medical records space |  |  |
|  | ___ provisions made for securing medical records of all media types used by facility |  |  |
| 2.1-6.3.5.1 | ___ location restricted to staff access to maintain confidentiality of record |  |  |
| 2.1-6.3.5.2 | Space Requirements: |  |  |
| (1) | ___ space provided for medical records management |  |  |
| (2) | ___ physical space for electronic storage of forms or documents |  |  |
| 2.1-6.3.6 | ___ Storage for office equipment & supplies |  |  |
| 2.2-6.4 | SUPPORT AREAS FOR STAFF |  |  |
| 2.1-6.4.1 | ___ Staff lounge ☐ check if not included in project |  |  |
|  | ___ handwashing station |  |  |
| 2.1-6.4.2 | ___ Storage for staff personal effects ___ locking drawers cabinets or lockers ___ readily accessible to individual work areas |  |  |

LOCATION TERMINOLOGY:

Directly accessible:  Connected to identified area or room through doorway pass-through or other opening without going through intervening room or public space

Adjacent:  Located next to but not necessarily connected to identified area or room

Immediately accessible:  Available either in or adjacent to identified area or room

Readily accessible:  Available on same floor or in same clinic as identified area or room

Architectural Details & MEP Requirements

| 2.1-7.2.2 | ARCHITECTURAL DETAILS |
| --- | --- |
|  | CORRIDOR WIDTH: |
| 2.1-7.2.2.1 IBC 1018.2 | ___ Min. 44” or ___ Detailed code review incorporated in Project Narrative |
| 421 CMR 6.00 | ___ Corridors include turning spaces for wheelchairs |
| 2.1-7.2.2.2 | CEILING HEIGHT: |
| (1) | ___ Min. ceiling height 7'-6"in corridors & in normally unoccupied spaces |
| (2) | ___ Min. height 7’-6” above floor of suspended tracks, rails & pipes located in traffic path |
|  | ___ Min. ceiling height 7’-10” in other areas |
| 2.1-7.2.2.3 (1) (a) (b) | DOORS & DOOR HARDWARE: Door Type: ___ doors between corridors rooms or spaces subject to occupancy swing type or sliding doors ___ sliding doors ☐ check if not included in project |
|  | ___ manual or automatic sliding doors comply with NFPA 101 ___ detailed code review incorporated in Project Narrative ___ no floor tracks |
| (2) (a) | Door Opening: ___ Min. 32” clear door width ___ Min. 83.5” clear door height |
| (3) | Door Swing: |
| (a) | ___ doors do not swing into corridors except doors to non-occupiable spaces (e.g. environmental services rooms & electrical closets) & doors with emergency breakaway hardware |
| (4) | ___ Lever hardware or push/pull latch hardware |
| (5) | Doors for Patient Toilet Facilities: |
| (a) | ___ door that swings outward or |
|  | ___ door equipped with emergency rescue hardware (permits quick access from outside room to prevent blockage of door) or |
|  | ___ sliding door (not pocket door) |
| (b) | ___ toilet room opens onto public area or corridor ☐ check if not included in project |
|  | ___ visual privacy is maintained |
| 2.1-7.2.2.8 | HANDWASHING STATIONS: |
| (3)(a) | ___ Handwashing station countertops made of porcelain stainless steel solid-surface materials or impervious plastic laminate assembly |
| (3)(b) | ___ Countertops substrate ☐ check if not included in project ___ marine-grade plywood (or equivalent material) with impervious seal |
| (4) | ___ Handwashing station casework ☐ check if not included in project ___ designed to prevent storage beneath sink |
| (5) | ___ Provisions for drying hands ☐ check if not included in project (only at hand scrub facilities) |
| (a) | ___ hand-drying device does not require hands to contact dispenser |
| (b) | ___ hand-drying device is enclosed to protect against dust or soil |
| (6) | ___ Liquid or foam soap dispensers |
| 2.1-7.2.2.9 | GRAB BARS: |
| (1) | ___ Grab bars anchored to sustain concentrated load 250 pounds |
| (3) | ___ Ends of grab bars constructed to prevent snagging clothes of patients staff & visitors |
| 2.1-7.2.3 | SURFACES |
| 2.1-7.2.3.1 | FLOORING & WALL BASES: |
| (1) | ___ Flooring surfaces cleanable & wear-resistant for location |
| (3) | ___ Smooth transitions provided between different flooring materials |
| (4) | ___ Flooring surfaces including those on stairways are stable firm & slip-resistant |
| (5) | ___ Floors & wall bases of all areas subject to frequent wet cleaning are constructed of materials that are not physically affected by germicidal or other types of cleaning solutions |
| (6)(a) | ___ Floors are monolithic & integral coved wall bases are at least 6” high & tightly sealed to wall in rooms listed below |
|  | - soiled workrooms & soiled holding rooms |
| 2.1-7.2.3.2 | WALLS & WALL PROTECTION: |
| (1)(a) | ___ Wall finishes are washable |
| (1)(b) | ___ Wall finishes near plumbing fixtures are smooth scrubbable & water-resistant |
| (2) | ___ Wall surfaces in areas routinely subjected to wet spray or splatter (e.g environmental services rooms) are monolithic or have sealed seams that are tight & smooth |
| (4) | ___ Wall protection devices & corner guards durable & scrubbable |
| 2.1-7.2.3.3 | CEILINGS: |
| (1) | ___ Ceilings provided in all areas except mechanical electrical & communications equipment rooms |
| (a) | ___ Ceilings cleanable with routine housekeeping equipment |
| (b) | ___ Acoustic & lay-in ceilings where used do not create ledges or crevices |
| 2.1-7.2.4.3 | ___ Privacy curtains in patient care areas are washable |
| 2.1-8.2 | HEATING VENTILATION & AIR-CONDITIONING (HVAC) SYSTEMS |

| 2.1-8.2.1.3 | ___ Ventilation rates meet requirements of Table 8-2 in Part 3 ASHRAE Standard 170 |
| --- | --- |
| 2.2-8.3 | ELECTRICAL SYSTEMS |
| 2.2-8.3.4 | EMERGENCY EGRESS LIGHTING |
|  | ___ Automatic emergency lighting or ___ Facility has total floor area of not more than 1,000 sf is located at grade level & has direct access to exits to grade |