COMPLIANCE CHECKLIST

OP17_Outpatient Rehabilitation Therapy Facilities

The following checklist is intended to be used in the plan review applications for health care facilities submitted to the Massachusetts Department of Public Health.  This checklist summarizes and references the applicable requirements from the Licensure Regulations and the 2022 Edition of the FGI Guidelines for Design and Construction of Outpatient Facilities.  Applicants must verify compliance of the plans submitted to the Department with all referenced requirements from the Licensure Regulations and FGI Guidelines when completing this Checklist.  A separate Checklist must be completed for each nursing unit, hospital or clinic department, or clinical suite.

Other jurisdictions, regulations and codes may have additional requirements which are not included in this checklist, such as:

- NFPA 101 Life Safety Code (2012) and applicable related standards contained in the appendices of the Code

- State Building Code (780 CMR)

- Accreditation requirements of The Joint Commission

- CDC Guidelines for Preventing the Transmission of Mycobacterium Tuberculosis in Health Care Facilities

- USP 797 & Regulations of the Massachusetts Board of Registration in Pharmacy

- Occupational Safety & Health Standards (OSHA)

- Accessibility Guidelines of the Americans with Disabilities Act (ADA)

- Architectural Access Board Regulations (521 CMR)

- Local Authorities having jurisdiction.

Instructions:

- All requirement lines must be completed according to the following instructions and included in the plan submissions for Self-Certification Process or Abbreviated Review Process.

- This checklist must be completed by the project architect or engineer based on the design actually reflected in the plans at the time of completion of the checklist.

- Each requirement line (___) of this Checklist must be completed exclusively with one of the following marks, unless otherwise directed in the checklist.  If a functional space is not affected by a renovation project, the mark “E” may be indicated on the requirement line (___) before the name of the functional space (associated requirements on indented lines below that name, or associated MEP requirements do not have to be completed in this case).  If more than one functional space serves a given required function (e.g. patient room or exam room), that clarification should be provided in the Project Narrative, and the requirement lines are understood to only address the functional spaces that are involved in the project.

| X = Requirement is met, for new space, for renovated space, or for existing direct support space for an expanded service. | = Check box under section titles or individual requirements lines for optional services or functions that are not included in the project area. |
| --- | --- |
| E = Requirement relative to an existing suite or area that has been licensed for its designated function, is not affected by the construction project and does not pertain to a required direct support space for the specific service affected by the project. “E” must not be used for an existing required support space associated with a new patient care room or area. | W = Waiver requested for specific section of the Regulations or FGI Guidelines, where hardship in meeting requirement can be demonstrated (a Physical Plant Waiver Form must be completed for each waiver request). An explicit floor plan or plan detail must be attached to each waiver request. |

- All room functions marked with "X" must be shown on the plans with the same name labels as in this checklist.

- Mechanical, electrical & plumbing requirements are only partially mentioned in this checklist.  The relevant section of the FGI Guidelines must be used for project compliance with all MEP requirements and for waiver references.

- Oxygen, vacuum, medical air, waste anesthesia gas disposal and instrument air outlets (if required) are identified respectively by the abbreviations "OX", "VAC", "MA", “WAGD” & “IA”.

- Requirements referenced with “FI” result from formal interpretations from the FGI Interpretations Task Group.

- The location requirements including asterisks (*) refer to the definitions of the Glossary in the beginning section of the FGI Guidelines and reproduced in this checklist.

| Facility Name: |  | DoN Project Number: (if applicable) |
| --- | --- | --- |
| Facility Address: |  |  |
| Satellite Name: (if applicable) |  | Building/Floor Location: |
| Satellite Address: (if applicable) |  | Submission Dates: |
| Project Description: |  | Initial Date: Revision Date: |

|  | Architectural Requirements | Building Systems Requirements |  |
| --- | --- | --- | --- |
| 2.12 | OUTPATIENT REHABILITATION THERAPY FACILITIES |  |  |
| 2.12-1.1 | Application: |  |  |
| 2.12-1.1.1 | ___ facilities where rehabilitation therapy & services are provided |  |  |
| 2.12-1.2.1 | Shared Services & Space: ☐ check if not included in project |  |  |
| 2.1-1.2.3 | ___ details of shared or purchased space and/or services are indicated in functional program contained in Project Narrative ___ waiver requests have been submitted for shared or purchased space (except as explicitly allowed below) |  |  |
| 2.12-1.2.1.1 | ___ outpatient rehabilitation facility located in facility housing other services has its own identifiable space |  |  |
| 2.12-1.2.1.2 | ___ dedicated support areas or ___ support areas are shared with adjacent facility |  |  |
| 2.12-2 | ACCOMMODATIONS FOR CARE OF INDIVIDUALS OF SIZE |  |  |
| 2.1-2.1.1.2 | ☐ check if not included in project (only if a Patient Handling & Movement Assessment that determines that the outpatient service does not have a need for expanded-capacity lifts & architectural details that support movement of individuals of size in patient areas is attached to the Project Narrative) |  |  |
| 2.1-2.1.2 | Location: |  |  |
|  | ___ spaces designated for care of or use by individuals of size are provided in locations to accommodate population expected to be served by facility |  |  |
| 2.1-2.5 | ___ Handwashing stations |  |  |
| 2.1-2.5.2 | ___ downward static force required for handwashing stations designated for individuals of size accommodates maximum patient weight of patient population |  |  |
| 2.1-2.6 | ___ Patient toilet room |  |  |
| 2.1-2.6.1.1 | ___ expanded-capacity toilet ___ mounted Min. 36” from finished wall to centerline of toilet on both sides (for caregiver assistance and/or use of floor-based lift) or | Ventilation: ___ Min. 4 air changes per hour ___ Exhaust ___ Negative pressure ___ No recirculating room units | Table 8.1 |
| 2.1-2.6.1.2 | ___ regular toilet ___ mounted Min. 44” from centerline of toilet on both sides to finished walls to allow for positioning of expanded-capacity commode over toilet |  |  |
| 2.1-2.6.1.3 | ___ rectangular clear floor area Min. 46” wide extends 72” from front of toilet |  |  |
| 2.1-2.6.2.1 | ___ grab bars in toilet rooms intended for use by individuals of size are anchored to sustain concentrated load of 800 pounds |  |  |
| 2.1-2.6.2.2 | ___ adjustable/foldable grab bar mounted on horizontally movable track is provided |  |  |
| 2.1-2.7 | ___ Single-patient therapy room |  |  |
| 2.1-2.7.1 | Space Requirements: |  |  |
| 2.1-2.7.1.1 |  |  |  |
| (1) | ___ min. 5'-0" clearance at foot of expanded-capacity exam table | Ventilation: ___ Min. 2 air changes per hour | Table 8-2 |
| (2) | ___ min. 3'-0" clearance on non-transfer side of expanded- capacity exam table |  |  |
| (3) |  |  |  |
| (a) | ___ min. 5’-0” on transfer side of expanded-capacity exam table with ceiling- or wall-mounted lift |  |  |
| (b) | or ___ min. 7’-0” on transfer side of expanded-capacity exam table in rooms without ceiling- or wall-mounted lift |  |  |
| 2.1-2.8 | ___ Equipment & supply storage |  |  |
| 2.1-2.9 | ___ Waiting areas |  |  |
| 2.1-2.9.1 | ___ seating for persons of size be provided in waiting areas in outpatient facilities |  |  |
| 2.1-2.9.2 | ___ waiting areas be sized to accommodate expanded-capacity furniture required for patients & visitors of size |  |  |
| 2.1-2.10.1 | ___ All plumbing fixtures, handrails, grab bars, patient lift, equipment, built-in furniture & other furnishings designed to accommodate maximum patient weight |  |  |
| 2.1-2.10.2 | Door Openings: |  |  |
| 2.1-2.10.2.1 | ___ all door openings used for path of travel to public areas & areas where care will be provided for individuals of size have min. clear width of 45.5” to provide access for expanded-capacity wheelchairs access |  |  |
| 2.1-2.10.2.2 | ___ door openings to toilet rooms designated for individuals of size have min. clear width of 45.5” |  |  |
| 2.12-3 | PATIENT CARE & DIAGNOSTIC AREAS |  |  |
| 2.12-3.2 | Physical & occupational therapy areas: |  |  |
| 2.12-3.2.2.1 (1) | ___ Individual therapy room ☐ check if not included in project (only if undressing is not necessary for patients to receive treatment) |  |  |
| (2) | Space Requirements: | Ventilation: |  |
| (a) | ___ min. clear floor area 80 sf | ___ Min. 3 air changes per hour | Table 8-2 |
| (b) | ___ min. clearance of 2’-8” on at least three sides of therapy furniture & equipment |  |  |
| (3) | ___ handwashing station |  |  |
| 2.12-3.8.13.2 | ___ designated storage for therapeutic equipment & safety devices |  |  |
| 2.12-3.2.2.2 | ___ Multiple-patient therapy or exercise area |  |  |
| (1) | ___ layout of multiple-patient therapy or exercise area includes staff work area located so staff can view activities taking place in exercise area |  |  |
| (2) | Space requirements: |  |  |
| (a) | ___ open, barrier-free space for rehab therapy is sized based on following: - Number of patients to be treated at same time - Number of staff members to be present at same time - Manufacturer’s clearance requirements for equipment used - Clearances to accommodate therapist or other caregiver |  |  |
|  | ___ above listed information is included in Project Narrative |  |  |
| (b) | ___ individual therapy spaces |  |  |
|  | ___ min. clear floor area 60 sf |  |  |
| (3) | ___ provisions for patient privacy |  |  |
| (4) | ___ handwashing station |  |  |
| 2.12-3.8.13.2 | ___ designated storage for therapeutic equipment & safety devices |  |  |
| 2.12-3.2.4 | ___ Therapeutic pool ☐ check if not included in project |  |  |
| 2.12-3.2.4.2 | ___ patient changing area |  |  |
| (1) | ___ single unisex rooms or ___ gender designated common locker rooms |  |  |
| (2) | ___ directly accessible to pool without entering public or exercise areas |  |  |
| (3) | ___ patient toilet room ___ directly accessible to changing area | Ventilation: ___ Min. 4 air changes per hour ___ Exhaust | Table 8-2 |
|  |  | ___ Negative pressure |  |
|  |  | ___ No recirculating room units |  |
| (4) | ___ shower |  |  |
| (a) | ___ at least one shower provided separate from toilet room |  |  |
| (b) | ___ directly accessible to toilet room |  |  |
| (5) | ___ securable lockers |  |  |
| 2.12-3.8.13.2 | ___ designated storage for therapeutic equipment & safety devices |  |  |
| 2.12-3.3.1 | ___ Prosthetics & orthotics area ☐ check if not included in project |  |  |
|  | Application: ___ evaluation & fitting of prosthetics & orthotics |  |  |
| 2.12-3.3.1.1 | ___ provision for privacy |  |  |
| 2.12-3.3.1.2 | ___ handwashing station |  |  |
| 2.12-3.3.1.3 | ___ clinical sink ☐ check if not included in project (only if running water is not needed in prosthetic & orthotic areas for materials preparation) |  |  |
| 2.12-3.8.13.2 | ___ designated storage for therapeutic equipment & safety devices |  |  |
| 2.12-3.3.1.4 | ___ eyewash station |  |  |
| 2.12-3.3.2 | ___ Speech & hearing therapy rooms ☐ check if not included in project |  |  |
| 2.12-3.3.2.2 | Space Requirements: ___ min. clear floor area 80 sf | Ventilation: ___ Min. 3 air changes per hour | Table 8-2 |
| 2.12-3.3.2.3 | ___ sound insulated gasketed door w/ sweep |  |  |
| 2.12-3.8.13.2 | ___ designated storage for therapeutic equipment & safety devices |  |  |
| 2.12-3.3.2.4 | Hand Hygiene: |  |  |
| 2.1-3.8.7 | ___ hands-on patient care is provided ___ handwashing station |  |  |
|  | or |  |  |
| 2.12-3.3.2.4(2) | ___ hands-on patient care is not provided ___ dedicated hand sanitation dispenser |  |  |
| 2.12-3.8 | Support Areas for Therapy & Other Patient Care Areas: |  |  |
| 2.12-3.8.3 | ___ Documentation area |  |  |
| 2.12-3.8.8 | ___ Medication safety zone ☐ check if not included in project |  |  |
| 2.1-3.8.8.1(2) | Design Promoting Safe Medication Use: |  |  |
| (a) | ___ medication safety zones located out of circulation paths |  |  |
| (b) | ___ work space designed so that staff can access information & perform required tasks | Lighting: ___ Task-specific lighting level min. 100 foot-candles | 2.1-3.8.8.1(2)(d) |
| (c) | ___ work counters provide space to perform required tasks |  |  |
| (e) | ___ sharps containers placed at height that allows users to see top of container |  |  |
| 2.1-3.8.8.2 |  |  |  |
| (1) | ___ medication preparation room | Ventilation: |  |
| (a) | ___ work counter | ___ Min. 4 air changes per hour | Table 8.1 |
|  | ___ handwashing station | Lighting: |  |
|  | ___ lockable refrigerator | ___ Task lighting | 2.1-3.8.8.1(2)(d) |
|  | ___ locked storage for controlled drugs |  |  |
|  | ___ sharps containers ☐ check if not included in project |  |  |
| (b) | ___ self-contained medication dispensing units ☐ check if not included in project |  |  |
|  | ___ room designed with space to prepare medications |  |  |
|  | or |  |  |
| (2) | ___ automated medication-dispensing unit |  |  |
| (a) | ___ located at nurse station, in clean workroom or in alcove | Lighting: ___ Task lighting | 2.1-3.8.8.1(2)(d) |
| (b) | ___ handwashing station or hand sanitation dispenser provided next to stationary medication-dispensing units |  |  |
| (c) | ___ countertop or cart provided adjacent to stationary medication-dispensing units |  |  |
| 2.12-3.8.9 | ___ Nourishment area or room ☐ check if not included in project |  |  |
| 2.1-3.8.9.1 | ___ handwashing station in or directly accessible to nourishment room or area |  |  |
| 2.1-3.8.9.2 | ___ work counter |  |  |
| 2.1-3.8.9.3 | ___ storage |  |  |
| 2.1-3.8.9.4 | ___ fixtures & appliances for beverages and/or nourishment provided in facility |  |  |
| 2.12-3.8.13.1(1) | ___ Clean linen storage for clean linen & towels provided in cabinets, closets, room or alcove for clean linen carts |  |  |
| 2.12-3.8.13.1(2) 140.204 | ___ Soiled linen holding room ___ handwashing station | Ventilation: ___ Min. 6 air changes per hour ___ Exhaust | Table 8-2 |
|  |  | ___ Negative pressure ___ No recirculating room units |  |
| 2.12-3.8.13.3 | ___ Wheelchair, lift & gurney storage space |  |  |
| 2.12-3.10 | Support Areas for Patients: |  |  |
| 2.12-3.10.1 2.12-3.10.1.2 | ___ Patient toilet room (may be shared by patients and staff) |  |  |
| 2.12-3.10.1.1 2.1-3.10.2.1 | ___ separate from public use toilet rooms & located to permit access from patient care areas without passing through publicly accessible areas | Ventilation: ___ Min. 4 air changes per hour ___ Exhaust | Table 8-2 |
| 2.1-3.10.2.2 | ___ equipped with toilet & handwashing station | ___ Negative pressure ___ No recirculating room units |  |
| 2.12-3.10.2 | ___ Provisions for drinking water |  |  |
| 2.12-5 | BUILDING SUPPORT FACILITIES |  |  |
| 2.12-5.3 | ___ Environmental services room |  |  |
| 2.1-5.3.1.1(3) | (may serve more than one clinical service area on same floor) |  |  |
| 2.1-5.3.1.1(1) 2.1-5.3.1.2(1) | ___ min. one environmental services room per floor ___ service sink or floor-mounted mop sink | Ventilation: ___ Min. 6 air changes per hour ___ Exhaust | Table 8-2 |
| 2.1-5.3.1.2(2) | ___ provisions for storage of supplies & housekeeping equipment | ___ Negative pressure ___ No recirculating room units |  |
| 2.1-5.3.1.2(3) | ___ handwashing station or hand sanitation dispenser |  |  |
| 2.12-6.2 | PUBLIC AREAS |  |  |
| 2.1-6.2.1 | ___ Vehicular drop-off & pedestrian entrance |  |  |
| 2.1-6.2.1.1 | ___ min. of one building entrance reachable from grade level |  |  |
| 2.1-6.2.1.2 | ___ building entrances used to reach outpatient services be clearly marked |  |  |
| 2.1-6.2.1.3 | ___ building entrances used to reach outpatient services located so patients need not go through other activity areas (except for shared lobbies in multi-occupancy buildings) |  |  |
| 2.1-6.2.2 | ___ Reception |  |  |
|  | ___ reception & information counter, desk or kiosk provided either at main entry or at each clinical service |  |  |
| 2.1-6.2.3 | ___ Waiting area |  |  |
| 2.1-6.2.3.2 | ___ visible from staff area either by camera or direct staff sight line |  |  |
| 2.1-6.2.4 | ___ Public toilet room |  |  |
| 2.1-6.2.4.2 | (may be located off public corridor in multi-tenant building) |  |  |
| 2.1-6.2.4.1 | ___ readily accessible from waiting area without passing through patient care or staff work areas | Ventilation: ___ Min. 4 air changes per hour ___ Exhaust ___ Negative pressure ___ No recirculating room units | Table 8.1 |
| 2.1-6.2.5 | ___ Provisions for telephone access |  |  |
|  | ___ access to make local phone calls |  |  |
| 2.1-6.2.6 | ___ Provisions for drinking water |  |  |
| 2.1-6.2.7.1 | ___ Wheelchair storage ☐ check if not included in project |  |  |
|  | ___ designated area located out of required corridor width ___ directly accessible to entrance ___ provided for at least one wheelchair |  |  |
| 2.1-6.2.7.2 | ___ Wheelchair parking space ☐ check if not included in project (only if facility provides services that do not require patients to transfer to facility chair, recliner, exam table or stretcher) |  |  |
|  | ___ designated area provided for parking at least one patient-owned wheelchair in non-public area ___ located out of any required egress width or other required clearance |  |  |
| 2.12-6.3 | ADMINISTRATIVE AREAS |  |  |
| 2.12-6.3.1 | ___ Office space |  |  |
| 2.12-6.3.1.1 | ___ staff office space & file storage |  |  |
| 2.12-6.3.1.2 | ___ office & clerical space (may be combined with reception area) |  |  |

LOCATION TERMINOLOGY:

Directly accessible:  Connected to the identified area or room through doorway, pass-through, or other opening without going through intervening room or public space

Adjacent:  Located next to but not necessarily connected to the identified area or room

Immediately accessible:  Available either in or adjacent to the identified area or room

Readily accessible:  Available on the same floor or in the same clinic as the identified area or room

Architectural Details & MEP Requirements

| 2.1-7.2.2 |  | ARCHITECTURAL DETAILS |  |
| --- | --- | --- | --- |
|  |  | CORRIDOR WIDTH: |  |
| 2.1-7.2.2.1 IBC 1018.2 |  | ___ Min. 44” or ___ Detailed code review incorporated in Project Narrative |  |
| 421 CMR 6.00 |  | ___ Corridors include turning spaces for wheelchairs |  |
| 2.1-7.2.2.2 |  | CEILING HEIGHT: |  |
| (1) |  | ___ Min. ceiling height 7'-6"in corridors & in normally unoccupied spaces |  |
| (2) |  | ___ Min. height 7’-6” above floor of suspended tracks, rails & pipes located in traffic path |  |
|  |  | ___ Min. ceiling height 7’-10” in other areas |  |
| 2.1-7.2.2.3 (1) (a) (b) |  | DOORS & DOOR HARDWARE: Door Type: ___ doors between corridors, rooms, or spaces subject to occupancy swing type or sliding doors ___ sliding doors ☐ check if not included in project |  |
|  |  | ___ manual or automatic sliding doors comply with NFPA 101 ___ detailed code review incorporated in Project Narrative ___ no floor tracks |  |
| (2) (a) |  | Door Opening: ___ min. 32” clear door width ___ min. 83.5” clear door height |  |
| (3) |  | Door Swing: |  |
| (a) |  | ___ doors do not swing into corridors except doors to non-occupiable spaces & doors with emergency breakaway hardware |  |
| (4) |  | ___ Lever hardware or push/pull latch hardware |  |
| (5) |  | Doors for Patient Toilet Facilities: |  |
| (a) |  | ___ door that swings outward or |  |
|  |  | ___ door equipped with emergency rescue hardware (permits quick access from outside the room to prevent blockage of the door) or |  |
|  |  | ___ sliding door other than pocket door |  |
| (b) |  | ___ toilet room opens onto public area or corridor ☐ check if not included in project |  |
|  |  | ___ visual privacy is maintained |  |
| 2.1-7.2.2.8 |  | HANDWASHING STATIONS: |  |
| (3)(a) |  | ___ Handwashing station countertops made of porcelain, stainless steel, solid-surface materials or impervious plastic laminate assembly |  |
| (3)(b) |  | ___ Countertops substrate ☐ check if not included in project ___ marine-grade plywood (or equivalent material) with impervious seal |  |
| (4) |  | ___ Handwashing station casework ☐ check if not included in project ___ designed to prevent storage beneath sink |  |
| (5) |  | ___ Provisions for drying hands ☐ check if not included in project (only at hand scrub facilities) |  |
| (a) |  | ___ hand-drying device does not require hands to contact dispenser |  |
| (b) |  | ___ hand-drying device is enclosed to protect against dust or soil |  |
| (6) |  | ___ Liquid or foam soap dispensers |  |
| 2.1-7.2.2.9 |  | GRAB BARS: |  |
| (1) |  | ___ Grab bars anchored to sustain concentrated load 250 pounds |  |
| (3) |  | ___ Ends of grab bars constructed to prevent snagging clothes of patients staff & visitors |  |
| 2.1-7.2.2.10 |  | HANDRAILS: ☐ check if not included in project |  |
| (2) |  | ___ Rail ends return to wall or floor |  |
| (3) |  | ___ Handrail gripping surfaces & fasteners are smooth (free of sharp or abrasive elements) with 1/8-inch min. radius |  |
| (4) |  | ___ Handrails have eased edges & corners |  |
| (5) |  | ___ Handrail finishes are cleanable |  |
| 2.1-7.2.2.14 |  | ___ Decorative water features ☐ check if not included in project |  |
| (1) |  | ___ no indoor unsealed (open) water features in confines of outpatient suite |  |
| (2) |  | ___ no covered fish tanks in other than public areas of outpatient suite |  |
| 2.12-7.2.3 |  | FURNISHINGS |  |
| 2.12-7.2.3.1 |  | ___ Windows in therapy areas have curtains or shades to provide patient privacy |  |
| 2.1-7.2.3 |  | SURFACES |  |
| 2.1-7.2.3.1 |  | FLOORING & WALL BASES: |  |
| (1) |  | ___ Flooring surfaces cleanable & wear-resistant for location |  |
| (3) |  | ___ Smooth transitions provided between different flooring materials |  |
| (4) |  | ___ Flooring surfaces including those on stairways are stable, firm & slip-resistant |  |
| (5) |  | ___ Floors & wall bases of all areas subject to frequent wet cleaning are constructed of materials that are not physically affected by germicidal or other types of cleaning solutions |  |
| 2.1-7.2.3.2 |  | WALLS & WALL PROTECTION: |  |
| (1)(a) |  | ___ Wall finishes are washable |  |
| (1)(b) |  | ___ Wall finishes near plumbing fixtures are smooth, scrubbable & water-resistant |  |
| (2) |  | ___ Wall surfaces in areas routinely subjected to wet spray or splatter (e.g. environmental services rooms) are monolithic or have sealed seams that are tight & smooth |  |
| (4) |  | ___ Wall protection devices & corner guards durable & scrubbable |  |
| 2.1-7.2.3.3 |  | CEILINGS: |  |
| (1) |  | ___ Ceilings provided in all areas except mechanical, electrical & communications equipment rooms |  |
| (a) |  | ___ Ceilings cleanable with routine housekeeping equipment |  |
| (b) |  | ___ Acoustic & lay-in ceilings where used do not create ledges or crevices |  |
| 2.1-7.2.4.3 |  | ___ Privacy curtains in patient care areas are washable |  |
| 2.1-8.2 |  | HEATING VENTILATION & AIR-CONDITIONING (HVAC) SYSTEMS |  |
| 2.1-8.2.1.3 |  | ___ Ventilation rates meet requirements of Table 8-2 in Part 3 ASHRAE Standard 170 |  |
| 2.1-8.3 |  | ELECTRICAL SYSTEMS |  |
| 2.1-8.3.2 |  | ELECTRICAL DISTRIBUTION & TRANSMISSION |  |
| 2.1-8.3.2.2 |  | Panelboards: |  |
| (1) |  | ___ all panelboards accessible to health care tenants they serve |  |
| (4) |  | ___ panelboards not located in exit enclosures or exit passageways |  |
| 2.1-8.3.6 |  | ELECTRICAL RECEPTACLES |  |
|  |  | ___ Receptacles in patient care areas are provided according to Table 2.1-1 |  |
| 2.1-8.4 |  | PLUMBING SYSTEMS |  |
| 2.1-8.4.2 |  | Plumbing & Other Piping Systems: |  |
| 2.1-8.4.2.1(3) |  | ___ no plumbing piping exposed overhead or on walls where possible accumulation of dust or soil may create cleaning problem |  |
| 2.1-8.4.2.5 |  | Heated Potable Water Distribution Systems: |  |
| (2) |  | ___ heated potable water distribution systems serving patient care areas are under constant recirculation ___ non-recirculated fixture branch piping length max. 25’-0” |  |
| (3)(a) (3)(c) |  | ___ no installation of dead-end piping (except for empty risers mains & branches for future use) |  |
| (3)(b) |  | ___ any existing dead-end piping is removed ☐ check if not included in project |  |
| (4)(a) |  | ___ water-heating system supplies water at following range of temperatures: 105–120oF |  |
| 2.1-8.4.2.6 |  | Drainage Systems: |  |
| (1)(a) |  | ___ drainage piping installed above ceiling of or exposed in electronic data processing rooms & electrical rooms have special provisions to protect space below from leakage & condensation ☐ check if not included in project |  |
| (1)(b) |  | ___ drip pan for drainage piping above ceiling of sensitive area ☐ check if not included in project ___ accessible ___ overflow drain with outlet located in normally occupied area |  |
| 2.1-8.4.3 |  | PLUMBING FIXTURES |  |
| 2.1-8.4.3.1(1) |  | ___ Materials used for plumbing fixtures are non-absorptive & acid-resistant |  |
| 2.1-8.4.3.2 |  | Handwashing Station Sinks: |  |
| (1) |  | ___ sinks are designed with basins & faucets that will reduce risk of splashing to areas where direct patient care is provided |  |
| (2) |  | ___ sink basins have nominal size of no less than 144 square inches ___ sink basins have min. dimension 9 inches in width or length |  |
| (3) |  | ___ sink basins are made of porcelain, stainless steel or solid-surface materials |  |
| (5) |  | ___ water discharge point of faucets is at least 10” above bottom of basin |  |
| (7) |  | ___ anchored so that allowable stresses are not exceeded where vertical or horizontal force of 250 lbs. is applied |  |
| (8) |  | ___ sinks used by staff, patients, & public have fittings that can be operated without using hands (may be single-lever or wrist blade devices) |  |
| (a) |  | ___ blade handles ☐ check if not included in project ___ at least 4 inches in length |  |
|  |  | ___ provide clearance required for operation |  |
| (b) |  | ___ sensor-regulated water fixtures ☐ check if not included in project |  |
|  |  | ___ meet user need for temperature & length of time water flows |  |
|  |  | ___ designed to function at all times & during loss of normal power |  |
| 2.1-8.4.3.4 |  | Ice-Making Equipment: ☐ check if not included in project ___ copper tubing provided for supply connections to ice-making equipment |  |
| 2.1-8.4.3.9 |  | Hydrotherapy Facilities: ☐ check if not included in project |  |
| (1) |  | ___ dedicated drain |  |
| (2) |  | ___ handwashing sinks not used as drains for hydrotherapy units |  |
| 2.1-8.7 |  | ELEVATORS ☐ check if not included in project |  |
| 2.1-8.7.4 |  | ___ Elevators are equipped with two-way automatic level-maintaining device with accuracy of ± 1/4 inch |  |
| 2.1-8.7.5 |  | Elevator Controls: |  |
| 2.1-8.7.5.1 |  | ___ elevator call buttons & controls not activated by heat or smoke |  |
| 2.1-8.7.5.2 |  | ___ light beams if used for operating door reopening devices without touch are used in combination with door-edge safety devices & are interconnected with system of smoke detectors |  |
| 2.1-8.7.5.3 |  | ___ elevator controls, alarm buttons & telephones are accessible to wheelchair occupants & usable by the blind |  |