[image: image13.jpg]




Background/Introduction
At the request of Mr. Thomas Bates, Director of Facilities for the Dexter Park School (DPS), the Massachusetts Department of Public Health (MDPH), Bureau of Environmental Health (BEH) conducted an indoor air quality (IAQ) assessment at the DPS located at 3 Dexter Street, Orange, Massachusetts.  This request was prompted by water damage and visible mold growth in one classroom (Room 12) following a roof leak due to sustained heavy rainfall in the late summer of 2011.  On October 21, 2011, Michael Feeney, Director of BEH’s IAQ Program made a visit to DPS to conduct an IAQ assessment accompanied by Kathleen Gilmore, Environmental Analyst/Regional Inspector in the BEH IAQ program.  Mr. Bates accompanied Mr. Feeney and Ms. Gilmore. 
The DPS is a single-story, flat-roofed building constructed in 1952.  Two additions were made to the building including a wing in 1970 and modular buildings in 1994.  The school consists of classrooms, a gymnasium, kitchen, auditorium, library and offices.  A crawl space runs below the 1952 and 1970 buildings.  Windows throughout the school are openable. 

Methods

Air tests for carbon monoxide, carbon dioxide, temperature and relative humidity were conducted with the TSI, Q-Trak, IAQ Monitor, Model 7565.  Air tests for airborne particle matter with a diameter less than 2.5 micrometers were taken with the TSI, DUSTTRAK™ Aerosol Monitor Model 8520.  BEH staff also performed visual inspection of building materials for water damage and/or microbial growth.  
Results

The DPS houses approximately 220 students and has a staff of 45.  Tests were taken during normal operations although some classrooms were sparsely occupied due to lunch hour.  Results appear in Table 1.  
Discussion

Ventilation

It can be seen from Table 1 that carbon dioxide levels were below 800 parts per million (ppm) in all areas surveyed indicating adequate air exchange in the building at the time of testing.  It is important to note that several rooms had windows open or were sparsely populated, as mentioned above, which can reduce carbon dioxide levels.  Carbon dioxide levels would be expected to increase with higher occupancy, windows closed and ventilation equipment deactivated. 
Fresh air to classrooms is supplied by unit ventilator (univent) systems made by several different manufacturers.  A univent draws air from the outdoors through a fresh air intake located on the exterior wall of the building.  Return air from the classroom is drawn through an air intake located at the base of the unit (Figure 1).  Fresh and return air are mixed, filtered, heated and provided to classrooms through an air diffuser located in the top of the unit.  Numerous univents were found deactivated at the time of assessment.  In addition, several univents were obstructed by items on top of air diffusers and/or in front of or above return vents along the bottom of the units (Pictures 1-2).  In order for univents to provide fresh air as designed, they must remain “on” and operating while rooms are occupied.  Furthermore, units must remain free of obstructions.  
The building has a series of mechanical exhaust vents.  Some of the classrooms had floor exhaust vents which were obstructed by furniture and items.  Exhaust vents must be clear of blockages in order to function properly.
To maximize air exchange, the MDPH recommends that both supply and exhaust ventilation operate continuously during periods of occupancy.  In order to have proper ventilation with a mechanical supply and exhaust system, the systems must be balanced to provide an adequate amount of fresh air to the interior of a room while removing stale air from the room.  It is recommended that HVAC systems be re-balanced every five years to ensure adequate air systems function (SMACNA, 1994).  The date of the last balancing of these systems was not available at the time of this assessment.
The Massachusetts Building Code requires that each room have a minimum ventilation rate of 15 cubic feet per minute (cfm) per occupant of fresh outside air or openable windows (SBBRS, 1997; BOCA, 1993).  The ventilation must be on at all times that the room is occupied.  Providing adequate fresh air ventilation with open windows and maintaining the temperature in the comfort range during the cold weather season is impractical.  Mechanical ventilation is usually required to provide adequate fresh air ventilation.
Carbon dioxide is not a problem in and of itself.  It is used as an indicator of the adequacy of the fresh air ventilation.  As carbon dioxide levels rise, it indicates that the ventilating system is malfunctioning or the design occupancy of the room is being exceeded.  When this happens, a buildup of common indoor air pollutants can occur, leading to discomfort or health complaints.  The Occupational Safety and Health Administration (OSHA) standard for carbon dioxide is 5,000 parts per million parts of air (ppm).  Workers may be exposed to this level for 40 hours/week, based on a time-weighted average (OSHA, 1997).

The MDPH uses a guideline of 800 ppm for publicly occupied buildings.  A guideline of 600 ppm or less is preferred in schools due to the fact that the majority of occupants are young and considered to be a more sensitive population in the evaluation of environmental health status.  Inadequate ventilation and/or elevated temperatures are major causes of complaints such as respiratory, eye, nose and throat irritation, lethargy and headaches.  For more information concerning carbon dioxide, consult Appendix A.
Indoor temperatures ranged from 70º F to 74º F, which were within the MDPH recommended comfort range (Table 1).  The MDPH recommends that indoor air temperatures be maintained in a range of 70o F to 78o F in order to provide for the comfort of building occupants.  In many cases concerning indoor air quality, fluctuations of temperature in occupied spaces are typically experienced, even in a building with an adequate fresh air supply.

The relative humidity measured in the building ranged from 37 to 53 percent at the time of the assessment, which was within or close to the lower end of the MDPH recommended comfort level (Table 1).  The MDPH recommends a comfort range of 40 to 60 percent for indoor air relative humidity.  The sensation of dryness and irritation is common in a low relative humidity environment.  For buildings in New England, periods of low relative humidity during the winter are often unavoidable.  Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low.  

Microbial/Moisture Concerns

As mentioned, water damage and mold growth concerns, specifically in the ceiling of classroom 12, prompted the assessment.  In order for buildings to support mold growth, a source of moisture exposure is necessary.  Identification and elimination of the source of water moistening the building materials is necessary to control mold growth.  Mr. Bates reported that excessive rainfall in late summer of 2011 resulted in a roof leak above classroom 12 leading to water-damaged ceiling tiles and visible mold growth (Picture 3).  The affected tiles were removed and the area was cleaned and disinfected.  At the time of the assessment, the ceiling tiles had not been replaced and the classroom has remained unoccupied.  
A crawlspace exists beneath the 1970 wing that provides a pipe chase for univent heating pipes. The interiors of several univents were examined.  Spaces and holes in walls and floors around pipes and within the air handling cabinets were observed (Picture 4).  These breaches can serve as pathways to draw air, odors and particulates from the crawlspace into classrooms.  Crawlspaces frequently are wet and contain mold spores and associated odors.

Mr. Bates also reported that the carpet in classroom 12 was also water-damaged due to the roof leak.  The carpet was reportedly dried out, cleaned and remains in place.  The Institute of Inspection, Cleaning and Restoration Certification (IICRC), recommends that carpeting be cleaned annually (or semi-annually in soiled high traffic areas) (IICRC, 2005).  Since the average service time of carpeting in a school environment is approximately eleven years (Bishop, 2002), consideration should be given to planning for the installation of new flooring as funds become available.  Until the carpeting is replaced, BEH staff recommends regular vacuuming with a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner, which filters out 99.97% of fine particles 0.3 micrometers (µm) in diameter that can exacerbate asthma and allergy symptoms (US EPA, 2001). 

The US Environmental Protection Agency (US EPA) and the American Conference of Governmental Industrial Hygienists (ACGIH) recommend that porous materials be dried with fans and heating within 24 to 48 hours of becoming wet (US EPA, 2001; ACGIH, 1989).  If not dried within this time frame, mold growth may occur.  Once mold has colonized porous materials, they are difficult to clean and should be removed and discarded.
Plants were noted in several classrooms.  Plants can be a source of pollen and mold which can be respiratory irritants to some individuals.  Plants should be properly maintained and equipped with drip pans and should be located away from univents to prevent the aerosolization of dirt, pollen and mold.
BEH staff conducted a perimeter inspection of the building’s exterior to identify potential sources of water penetration.  Cracks and crevices exist in the building envelope which can undermine the integrity of the exterior walls and provide a means of water entry by capillary action into the building through the exterior wall system (Picture 5).  Efflorescence was also identified in bricks along the side of the building (Picture 6).  Efflorescence is a characteristic sign of water damage to brick and mortar, but it is not mold growth.  As moisture penetrates and works its way through mortar, brick or plaster, water-soluble compounds dissolve, creating a solution.  As the solution moves to the surface of the material, the water evaporates, leaving behind white, powdery mineral deposits. 
Shrubbery and grassy areas were noted to be growing in close proximity to foundation walls (Picture 7).  The growth of roots against exterior walls can bring moisture in contact with brick, eventually leading to cracks and/or fissures in the foundation below ground level.  Over time, this process can undermine the integrity of the building envelope and provide a means of water entry into the building through capillary action through foundation concrete and/or masonry (Lstiburek & Brennan, 2001).

Other IAQ Evaluations
Indoor air quality can be negatively influenced by the presence of respiratory irritants, such as products of combustion.  The process of combustion produces a number of pollutants.  Common combustion emissions include carbon monoxide, carbon dioxide, water vapor, and smoke (fine airborne particle material).  Of these materials, exposure to carbon monoxide and particulate matter with a diameter of 2.5 micrometers (μm) or less (PM2.5) can produce immediate, acute health effects upon exposure.  To determine whether combustion products were present in the building environment, BEH staff obtained measurements for carbon monoxide and PM2.5.  

Carbon Monoxide

Carbon monoxide is a by-product of incomplete combustion of organic matter (e.g., gasoline, wood and tobacco).  Exposure to carbon monoxide can produce immediate and acute health effects.  Several air quality standards have been established to address carbon monoxide and prevent symptoms from exposure to these substances.  The MDPH established a corrective action level concerning carbon monoxide in ice skating rinks that use fossil-fueled ice resurfacing equipment.  If an operator of an indoor ice rink measures a carbon monoxide level over 30 ppm, taken 20 minutes after resurfacing within a rink, that operator must take actions to reduce carbon monoxide levels (MDPH, 1997).

The American Society of Heating Refrigeration and Air-Conditioning Engineers (ASHRAE) has adopted the National Ambient Air Quality Standards (NAAQS) as one set of criteria for assessing indoor air quality and monitoring of fresh air introduced by HVAC systems (ASHRAE, 1989).  The NAAQS are standards established by the US EPA to protect the public health from six criteria pollutants, including carbon monoxide and particulate matter (US EPA, 2006).  As recommended by ASHRAE, pollutant levels of fresh air introduced to a building should not exceed the NAAQS levels (ASHRAE, 1989).  The NAAQS were adopted by reference in the Building Officials & Code Administrators (BOCA) National Mechanical Code of 1993 (BOCA, 1993), which is now an HVAC standard included in the Massachusetts State Building Code (SBBRS, 1997).  According to the NAAQS, carbon monoxide levels in outdoor air should not exceed 9 ppm in an eight-hour average (US EPA, 2006).
Carbon monoxide should not be present in a typical, indoor environment.  If it is present, indoor carbon monoxide levels should be less than or equal to outdoor levels.  Outdoor carbon monoxide concentrations were non-detect (ND) at the time of the assessment (Table 1).  No measureable levels of carbon monoxide were detected inside the building during the assessment (Table 1).  
Particulate Matter

The US EPA has established NAAQS limits for exposure to particulate matter.  Particulate matter is airborne solids that can be irritating to the eyes, nose and throat.  The NAAQS originally established exposure limits to particulate matter with a diameter of 10 μm or less (PM10).  According to the NAAQS, PM10 levels should not exceed 150 micrograms per cubic meter (μg/m3) in a 24-hour average (US EPA, 2006).  These standards were adopted by both ASHRAE and BOCA.  Since the issuance of the ASHRAE standard and BOCA Code, US EPA established a more protective standard for fine airborne particles.  This more stringent PM2.5 standard requires outdoor air particle levels be maintained below 35 μg/m3 over a 24-hour average (US EPA, 2006).  Although both the ASHRAE standard and BOCA Code adopted the PM10 standard for evaluating air quality, MDPH uses the more protective PM2.5 standard for evaluating airborne particulate matter concentrations in the indoor environment.
Outdoor PM2.5 concentrations the day of the assessment were measured at 7 μg/m3.  PM2.5 levels measured inside the building ranged from 2 to 9 μg/m3 (Table 1).  Both indoor and outdoor PM 2.5 levels were below the NAAQS PM2.5 level of 35 μg/m3.  Frequently, indoor air levels of particulates (including PM2.5) can be at higher levels than those measured outdoors.  A number of activities that occur indoors and/or mechanical devices can generate particulate during normal operations.  Sources of indoor airborne particulates may include but are not limited to particles generated during the operation of fan belts in the HVAC system, use of stoves and/or microwave ovens in kitchen areas; use of photocopiers, fax machines and computer printing devices; operation of an ordinary vacuum cleaner and heavy foot traffic indoors.

Volatile Organic Compounds

Indoor air concentrations can be greatly impacted by the use of products containing volatile organic compounds (VOCs).  VOCs are carbon-containing substances that have the ability to evaporate at room temperature.  Frequently, exposure to low levels of total VOCs (TVOCs) may produce eye, nose, throat and/or respiratory irritation in some sensitive individuals.  For example, chemicals evaporating from a paint can stored at room temperature would most likely contain VOCs.  In an effort to identify materials that can potentially increase VOC concentrations, BEH staff examined classrooms for products that may contain these respiratory irritants.

Cleaning products were observed in several classrooms (Picture 8).  These items contain chemicals that can be irritating to the eyes, nose and throat and should be kept out of reach of students.  Additionally, a Material Safety Data Sheet (MSDS) should be available at a central location for each product in the event of an emergency.  
Photocopiers and lamination machines were located in hallways and administrative areas of the building.  Lamination machines melt plastic and give off odors and VOCs.  VOCs and ozone can be produced by photocopiers, particularly if the equipment is older and in frequent use.  Ozone is a respiratory irritant (Schmidt Etkin, 1992).

Several classrooms contained dry erase boards and related materials (Picture 9).  Materials such as dry erase markers and dry erase board cleaners may contain VOCs, such as methyl isobutyl ketone, n-butyl acetate and butyl-cellusolve (Sanford, 1999), which can be irritating to the eyes, nose and throat.  

Other Conditions
Other conditions that can affect indoor air quality were observed during the assessment.  In several classrooms, items were observed on the floor, windowsills, tabletops, counters, bookcases and desks (Pictures 1, 2 and 9).  The large number of items stored in classrooms provides a source for dusts to accumulate.  These items (e.g., papers, folders, boxes, books) make it difficult for custodial staff to clean.  Items should be relocated and/or be cleaned periodically to avoid excessive dust build up.  In addition, these materials can accumulate on flat surfaces (e.g., desktops, shelving and carpets) in occupied areas and subsequently be re-aerosolized causing further irritation.  
A number of univents, exhaust vents, and personal fans were observed to have accumulated dust/debris (Pictures 10, 11).  These diffusers, vents and fans should be cleaned in order to prevent dust/debris from being aerosolized and redistributed throughout the room. 
Several classrooms had open food containers and food preparation areas (Picture 12).  Stored food is attractive to insects and rodents, as is food waste such as crumbs or food in trash cans.  Rodent infestation can result in indoor air quality related symptoms due to materials in their wastes.  Mouse urine contains a protein that is a known sensitizer (US EPA, 1992).  A sensitizer is a material that can produce allergic symptoms (e.g., running nose or skin rashes) in sensitive individuals following repeated exposures.  
Conclusions/Recommendations

In view of the findings at the time of the visit, the following recommendations are made:
1. Examine roofs and repair/patch portions of the roofs to prevent/reduce leaks.  Continue to monitor classroom 12 and other areas of the building for roof leaks; change ceiling tiles as necessary.  Consider replacing the carpet in this room.
2. Seal all penetrations (e.g., holes and open conduit) in univent cabinets with an appropriate fire-rated expandable foam. 
3. Examine flashing around the building exterior and repair to prevent further water penetration.

4. Operate all ventilation systems throughout the building continuously during occupied periods.  
5. Use openable windows in conjunction with mechanical ventilation to facilitate air exchange.  
6. Remove all blockages from univents and exhaust vents to ensure adequate airflow.  
7. Consider adopting a balancing schedule of every 5 years for all mechanical ventilation systems, as recommended by ventilation industrial standards (SMACNA, 1994).

8. For buildings in New England, periods of low relative humidity during the winter are often unavoidable.  Therefore, scrupulous cleaning practices should be adopted to minimize common indoor air contaminants whose irritant effects can be enhanced when the relative humidity is low.  To control for dusts, a high efficiency particulate arrestance (HEPA) filter equipped vacuum cleaner in conjunction with wet wiping of all surfaces is recommended.  Avoid the use of feather dusters.  Drinking water during the day can help ease some symptoms associated with a dry environment (throat and sinus irritation).

9. Remove plants from univent air diffusers.  Ensure plants have drip pans and avoid over-watering.  Examine drip pans periodically for mold growth.  Disinfect with an appropriate antimicrobial where necessary.  

10. Store cleaning products properly and out of reach of students.  Ensure spray bottles are properly labeled.  Consider providing school issued cleaning products to staff.

11. Relocate or consider reducing the amount of materials stored in classrooms to allow for more thorough cleaning of classrooms.  Clean items regularly with a wet cloth or sponge to prevent excessive dust build-up.

12. Clean personal fans, univent air diffusers, return vents and exhaust vents periodically of accumulated dust.

13. Consider adopting the US EPA (2000) document, “Tools for Schools”, as an instrument for maintaining a good indoor air quality environment in the building.  This document is available at: http://www.epa.gov/iaq/schools/index.html.
14. Refer to resource manual and other related indoor air quality documents located on the MDPH’s website for further building-wide evaluations and advice on maintaining public buildings.  These documents are available at: http://mass.gov/dph/iaq. 
References

ACGIH.  1989.  Guidelines for the Assessment of Bioaerosols in the Indoor Environment.  American Conference of Governmental Industrial Hygienists, Cincinnati, OH. 

ASHRAE.  1989.  Ventilation for Acceptable Indoor Air Quality.  American Society of Heating, Refrigeration and Air Conditioning Engineers.  ANSI/ASHRAE 62-1989

BOCA.  1993.  The BOCA National Mechanical Code/1993.  8th ed.  Building Officials and Code Administrators International, Inc., Country Club Hill, IL.

Bishop, J. & Institute of Inspection, Cleaning and Restoration Certification.  2002.  A Life Cycle Cost Analysis for Floor Coverings in School Facilities.

IICRC.  2005.  Carpet Cleaning FAQ 4 Institute of Inspection, Cleaning and Restoration Certification.  Institute of Inspection Cleaning and Restoration, Vancouver, WA.

Lstiburek, J. & Brennan, T.  2001.  Read This Before You Design, Build or Renovate.  Building Science Corporation, Westford, MA.  U.S. Department of Housing and Urban Development, Region I, Boston, MA.

MDPH.  1997.  Requirements to Maintain Air Quality in Indoor Skating Rinks (State Sanitary Code, Chapter XI).  105 CMR 675.000.  Massachusetts Department of Public Health, Boston, MA.

OSHA.  1997.  Limits for Air Contaminants.  Occupational Safety and Health Administration.  Code of Federal Regulations.  29 C.F.R 1910.1000 Table Z-1-A.

Sanford.  1999.  Material Safety Data Sheet (MSDS No: 198-17).  Expo( Dry Erase Markers Bullet, Chisel, and Ultra Fine Tip.  Sanford Corporation, Bellwood, IL.

SBBRS.  1997.  Mechanical Ventilation.  State Board of Building Regulations and Standards.  Code of Massachusetts Regulations.  780 CMR 1209.0
Schmidt Etkin, D.  1992.  Office Furnishings/Equipment & IAQ Health Impacts, Prevention & Mitigation.  Cutter Information Corporation, Indoor Air Quality Update, Arlington, MA.

SMACNA.  1994.  HVAC Systems Commissioning Manual.  1st ed.  Sheet Metal and Air Conditioning Contractors’ National Association, Inc., Chantilly, VA.

US EPA.  1992.  Indoor Biological Pollutants.  US Environmental Protection Agency, Environmental Criteria and Assessment Office, Office of Health and Environmental Assessment, research Triangle Park, NC.  EPA 600/8-91/202.  January 1992.

US EPA.  2000.  Tools for Schools.  Office of Air and Radiation, Office of Radiation and Indoor Air, Indoor Environments Division (6609J). EPA 402-K-95-001, Second Edition.  http://www.epa.gov/iaq/schools/tools4s2.html.

US EPA.  2001.  “Mold Remediation in Schools and Commercial Buildings”.  Office of Air and Radiation, Indoor Environments Division, Washington, DC.  EPA 402-K-01-001.  March 2001.  Available at: http://www.epa.gov/iaq/molds/mold_remediation.html
US EPA.  2006.  National Ambient Air Quality Standards (NAAQS).  US Environmental Protection Agency, Office of Air Quality Planning and Standards, Washington, DC.  http://www.epa.gov/air/criteria.html.
Picture 1

[image: image1.jpg]



Univent Obstructed with Books

Picture 2

[image: image2.jpg]



Univent Obstructed with Books (arrow)

Picture 3

[image: image3.jpg]



Water-damaged Ceiling in Room 12

Picture 4

[image: image4.jpg]



Univent Opening to Crawlspace, Note Corroded Metal (Arrow) Indicating Likely Water Vapor Exposure to Crawlspace Air

Picture 5

[image: image5.jpg]



Cracked Bricks in Building Exterior 

Picture 6
[image: image6.png]



Efflorescence on Building Exterior

Picture 7

[image: image7.jpg]



Grassy Area along Building Exterior

Picture 8

[image: image8.png]



Cleaning Products in Classroom

Picture 9

[image: image9.jpg]



Cluttered Items in Classroom 

Picture 10

[image: image10.jpg]



Personal Fan with Dusty Blades

Picture 11

[image: image11.png]



Univent with Dust and Debris

Picture 12

[image: image12.png]



Open Food Containers

	Location/ Room
	Occupants

in Room
	Temp

(°F)
	Relative

Humidity

(%)
	Carbon

Dioxide

(ppm)
	Carbon Monoxide

(ppm)
	PM2.5

(µg/m3)
	Windows

Openable
	Ventilation
	Remarks

	
	
	
	
	
	
	
	
	Supply
	Exhaust
	

	Background
	
	70
	38
	453
	ND
	7
	
	
	
	

	Principal’s Office
	0
	73
	42
	634
	ND
	6
	Y


	Y
	Y
	Windows open, DO,  6 WDCTs replaced

	Administration Office
	2
	72
	43
	622
	ND
	7
	Y


	Y
	Y
	Windows open, DO, PF, Plants

	Gym
	0
	72
	42
	515
	ND
	7
	Y
	Y
	Y
	DO

	Kitchen
	3
	73
	49
	406
	ND
	7
	Y
	Y
	Y
	DO

	Library
	0
	73
	41
	598
	ND
	5
	Y
	Y


	Y
	Supply vent off,

GW with vinyl wallpaper, PF

	Room 1
	0
	73
	39
	335
	ND
	4
	Y


	Y
	Y
	Windows open, GW with vinyl wall paper,

DO, CP

	Room 2
	3
	72
	39
	415
	ND
	6
	Y


	Y


	Y
	GW with vinyl wallpaper, clutter, UV blocked with items, FC, PC

	Room 3

Computer Room
	0
	74
	37
	449
	ND
	5
	Y
	Y
	Y
	Windows open,  GW with vinyl wallpaper, DO, MT

	Room 4

Community/

Supply room


	1
	73
	45
	498
	ND
	2
	Y


	Y
	Y
	Windows open, DO, 5 WDCTs, Clutter, Plants, DEM, CP

	Room 5
	13
	73
	42
	649
	ND
	3
	Y


	Y
	Y


	Windows open, GW with vinyl wallpaper, DEM, FC, CP

	Room 6
	2
	74
	40
	746
	ND
	4
	Y


	Y


	Y
	UV blocked, DO, GW with vinyl wallpaper, CP, FC

	Room 8
	9
	73
	44
	598
	ND
	9
	Y
	Y


	Y
	Windows open,  GW with vinyl wall paper, FC, DEM, Plants

	Room 11
	3
	73
	42
	712
	ND
	9
	Y
	Y
	Y
	Items on UV, PF, CP, Clutter

	Room 12
	0
	73
	44
	327
	ND
	6
	Y
	Y
	Y
	WD CT removed,



	Room 13
	1
	70
	42
	436
	ND
	5
	Y


	Y
	Y


	Exhaust vent blocked, Items on UV, CP, DEM, FC, Clutter

	Room 14
	1
	73
	53
	760
	ND
	5
	Y
	Y
	Y


	Exhaust vent blocked, 8 WD CTs, CP, Clutter, FC

	Room 15
	6
	74
	41
	436
	ND
	5
	Y


	Y


	Y


	Windows open, Exhaust vent blocked, Items on UV, CP, Clutter

	Room 17
	0
	74
	42
	600
	ND
	7
	Y


	Y


	Y


	Windows open, DO, UV blocked/off, DEM, FC, DEM, Clutter

	Room 19
	15
	70
	45
	481
	ND
	7
	Y


	Y
	Y


	Windows open, UV blocked, PF, FC

	Room 20
	25
	70
	42
	698
	ND
	9
	Y
	Y


	Y


	UV off/blocked, Items on UV, DO, DEM 

	Room 21
	12
	73
	46
	794
	ND
	5
	Y
	Y


	Y
	UV off/blocked, FC, Clutter, PF, FC, CP

	1994 Modular  Classrooms Addition
	
	
	
	
	
	
	
	
	
	

	Room 1
	8
	72
	38
	383
	ND
	3
	Y
	Y


	Y
	5 Damaged/missing CTs, PF, FC

	Room 2
	3
	74
	45
	383
	ND
	3
	Y


	Y
	Y
	Windows open, FC, PF, CP, Clutter

	Room 3
	7
	74
	39
	632
	ND
	5
	Y
	Y
	Y
	FC, PF, CP, Clutter

	Room 4
	9
	74
	39
	646
	ND
	5
	Y
	Y
	Y
	FC, Plants, CP

	Room 5
	8
	73
	40
	406
	ND
	6
	Y
	Y
	Y
	FC, CP, PF








INDOOR AIR QUALITY ASSESSMENT





Orange Dexter Park School


3 Dexter Street


Orange, Massachusetts




















�




















Prepared by:


Massachusetts Department of Public Health


Bureau of Environmental Health


Indoor Air Quality Program


January 2012











PAGE  
2

