Issue/Title: Pilgrim Nuclear Power Station (PNPS): Tritium in Groundwater Monitoring Wells

Topic: PNPS Updates as of January 2, 2013

Previous Plans: Results from groundwater monitoring well samples collected during the weeks of November 12, 2012 and November 26, 2012 were reported by Entergy.  Split sample results for the weeks of November 12, 2012 and November 26, 2012 were also reported by MERL.

Current Status:

Table 1:  Week of November 12th 	                 	      Table 2:  Week of November 26th

| Location | Date | MERL pCi/L | GEL pCi/L |  | Location | Date | MERL pCi/L | GEL pCi/L |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MW 201 | 11/12/2012 | 500 | 551 |  | MW 201 | 11/26/2012 | 457 | NDA(371)* |
| MW 202 | 11/12/2012 | 1,489 | 1,160 |  | MW 202 | 11/26/2012 | - | - |
| MW 202 I | 11/12/2012 | 449 | NDA(365)* |  | MW 202 I | 11/26/2012 | - | - |
| MW 203 | 11/12/2012 | NDA(300)* | NDA(363)* |  | MW 203 | 11/26/2012 | - | - |
| MW 204 | 11/12/2012 | 428 | NDA(370)* |  | MW 204 | 11/26/2012 | - | - |
| MW 205 | 11/12/2012 | 1,411 | 1,210 |  | MW 205 | 11/26/2012 | 4,235 | 3,680 |
| MW 206 | 11/12/2012 | 1,767 | 1,510 |  | MW 206 | 11/26/2012 | 2,060 | 1,970 |
| MW 207 | 11/12/2012 | 407 | NDA(389)* |  | MW 207 | 11/26/2012 | - | - |
| MW 208-S | 11/12/2012 | 369 | NDA(387)* |  | MW 208-S | 11/26/2012 | - | - |
| MW 208-I | 11/12/2012 | 325 | NDA(387)* |  | MW 208-I | 11/26/2012 | - | - |
| MW 209 | 11/12/2012 | 931 | 714 |  | MW 209 | 11/26/2012 | 980 | 810 |
| MW 210 | 11/12/2012 | 1,147 | 844 |  | MW 210 | 11/26/2012 | - | - |
| MW 211 | 11/12/2012 | 1,097 | 1,070 |  | MW 211 | 11/26/2012 | 1,087 | 986 |
| MW 212 | 11/12/2012 | *** | *** |  | MW 212 | 11/26/2012 | - | - |
| MW 213 | 11/12/2012 | NDA(300)* | NDA(363)* |  | MW 213 | 11/26/2012 | - | - |
| MW 214 | 11/12/2012 | NDA(300)* | NDA(381)* |  | MW 214 | 11/26/2012 | - | - |
| MW 215 | 11/12/2012 | 1,310 | 1,010 |  | MW 215 | 11/26/2012 | 1,173 | 1,010 |
| MW 216 new | 11/12/2012 | 3,148 | 2,460 |  | MW 216 new | 11/26/2012 | 4,668 | 3,960 |
| MW 217 | 11/12/2012 | 640 | NDA(372)* |  | MW 217 | 11/26/2012 | 469 | NDA(372)* |
| MW 3 | 11/12/2012 | 342 | NDA(388)* |  | MW 3 | 11/26/2012 | - | - |
| MW 4 | 11/12/2012 | 645 | 696 |  | MW 4 | 11/26/2012 | - | - |
| SW-boat ramp | 11/12/2012 | NDA(300)* | NDA(391)* |  | SW-boat ramp | 11/26/2012 | - | - |
| SW-intake | 11/12/2012 | NDA(300)* | NDA(377)* |  | SW-intake | 11/26/2012 | NDA(300)* | NDA(371)* |
| * NDA = not detected at less than activity value listed |  |  |  |  |  |  |  |  |
| ** results pending *** well inaccessible - not analyzed this week |  |  |  |  |  |  |  |  |

The groundwater monitoring results reported by Entergy show MW205 decreased to a level of 1,210 pCi/L of tritium detected during the week of November 12th  and increased to a level of 3,680 pCi/L of tritium detected during the week of November 26th (the previous result during the week of October 29th was 3,520 pCi/L).  Entergy results show that MW206 decreased to a level of 1,510 pCi/L of tritium detected during the week of November 12th and increased to a level of 1,970 pCi/L of tritium detected during the week of November 26th (the previous result during the week of October 29th was 4,300 pCi/L).   Results for the other wells sampled during the weeks of November 12th and November 26th were within typical ranges detected since the groundwater monitoring for tritium began.  The week of November 12th was also a comprehensive round.  It should be noted MW212 was not accessible due to ongoing site activities in that area.  Split sample results from MERL for the weeks of November 12th and November 26th were generally consistent with Entergy results (see tables above).

Weekly sampling of MW216 continued.  Entergy results for MW216 to date indicate fluctuations between 2,250 to 7,620 pCi/L of tritium detected for the weeks of September 17th through December 3rd.  The most recent result for MW216 was 3,740 pCi/L of tritium detected the week of December 3rd.  MERL split sample results for MW216 for the September 17th through November 26th period were generally consistent with Entergy’s results.  MERL is currently awaiting receipt of the December 3rd split sample from Entergy.   Weekly sampling is continuing.  The sampling schedule for MW216 will be re-evaluated once all results for 2012 weekly sampling have been reviewed.

Entergy surface water sampling results for the intake canal downstream of MW205 for the weeks of November 12th and November 26th indicated no detectable tritium.  The week of November 12th was also a comprehensive round, and a second surface water sample from the intake canal was collected, which also indicated no detectable tritium.  MERL split sample results for surface water also indicated no detectable tritium for samples collected during the weeks of November 12th and November 26th.

At the request of MDPH, Entergy is currently preparing a detailed summary of potential sources that have been investigated during the past 2.5 years (including a spill of contaminated water in 1988 in the area of MW206 and MW216) and their likely relationship to detections of tritium in groundwater at PNPS.

Looking Forward:

MDPH will continue to closely follow all investigational activities that are currently underway at PNPS.

PNPS screening level for tritium in groundwater monitoring wells is 3,000 pCi/L, which is 1/10th of the NRC-approved Pilgrim Offsite Dose Calculation Manual standard for tritium in non-drinking water sources. The EPA drinking water standard is 20,000 pCi/L. The nearest drinking water wells are approximately 2.5 miles from the plant.